## Table 1
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
This checklist is to compliment the structural concrete ITP – ITP007a.
Pour Date: |  |  |  |  | / / | [6 empty] | Vic Civil Engineer |  |  |  |  | Ben Thomas | [8 empty] | Checklist |  |  |  |  | of
Pour Description: |  |  |  |  | Pouring of architectural / structural concrete columns for the Ballarat Road Bridge at the New Footscray Hospital
ITP Ref # | ITP Activity |  |  |  | Acceptance Criteria | [11 empty] | Check Box |  |  |  |  | Verification Record | [6 empty] | Vic Civil |  |  | Multiplex
[29 empty] | Sign/Date* |  |  | Sign/Date*
4.0 CONSTRUCTION ACTIVITIES – PREPOUR
4.1 | Incoming Inspection of Materials |  |  |  | All materials conform to IFC drawings and specs- ferrules, galvanised dowels, drainage conduits etc. | [11 empty] | Yes No N/A |  |  |  |  | Delivery Dockets Compliance Certificates | [9 empty] | Project Engineer (HP):
4.6 | Reinforcement |  |  |  | Type, size, position, chairs, cover all as specified & within tolerance; laps and splices as specified; tack welds not undercut | [11 empty] | Yes No |  |  |  |  | Reinforcement Schedule | [9 empty] | Project Engineer (HP):
[5 empty] | Ensure starter bars match precast stitch bars (if applicable) | [11 empty] | Yes No N/A |  |  |  |  | Survey Report
[5 empty] | Placement, size and configuration as per drawings ± 5mm position. | [11 empty] | Yes No
[5 empty] | Cover (including tire wire) specified in drawings 0mm, + 5mm. Cover checked to FSL. | [11 empty] | Yes No
[5 empty] | Surface condition free from thick rust, grease, mud etc | [11 empty] | Yes No
[5 empty] | Min lap lengths N12 – 300mm N24 – 1000mm N16 – 500mm N28 – 1250mm N20 – 750mm N32 – 1500mm | [11 empty] | Yes No
[5 empty] | Tack Welding not within 50mm of bends | [11 empty] | Yes No N/A
[5 empty] | Mechanical splices (couplers or similar) fully engaged and installed as per manufacturers recommendations. | [11 empty] | Yes No N/A |  |  |  |  | Coupler Delivery Docket Compliance Certificates
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
ITP Ref # | ITP Activity |  |  |  | Acceptance Criteria | [11 empty] | Check Box |  |  |  |  | Verification Record | [6 empty] | Vic Civil |  |  | Multiplex
[29 empty] | Sign/Date* |  |  | Sign/Date*
4.7 | Formwork/ falsework setup, alignment and integrity |  |  |  | Installed as per temp design; design confirmed by survey; forms clean & release agent/oil applied. | [11 empty] | Yes No N/A
[5 empty] | Falsework/formwork over 1m high has a temporary design | [11 empty] | Yes No N/A |  |  |  |  | Temp Works Design | [9 empty] | Project Engineer (HP):
4.8 | Construction Joints |  |  |  | Concrete cast against concrete to be clean & free of laitance. Roughened and coarse aggregate exposed to depth of 3mm | [11 empty] | Yes No N/A
4.11 | Cast-in items, void formers, block-outs and hold down bolts |  |  |  | Type, quantity and location as per design. Checked with survey and relevant stakeholder | [11 empty] | Yes No N/A |  |  |  |  | Delivery Dockets
4.12 | Installation of thermocouples |  |  |  | Thermocouples installed as per VR610.22 | [11 empty] | Yes No N/A |  |  |  |  | Install Photos
HOLD POINT Concrete pre-pour checks completed in accordance with the applicable ITP, drawings, specifications and approved changes
PROJECT ENGINEER NAME (Vic Civil) | [17 empty] | SIGN | [10 empty] | DATE
PROJECT ENGINEER NAME (Multiplex) | [17 empty] | SIGN | [10 empty] | DATE
4.0 CONSTRUCTION ACTIVITIES – CONCRETE PLACEMENT
4.13 |  |  |  |  | Concrete Mix on Docket Checked. Ensure delivery dockets. Tester onsite. Visual assessment of quality. | [11 empty] | Yes |  |  |  | No | Concrete Delivery Dockets Field Test Docket Concrete Pour Record (Refer pg 7)
[5 empty] | 1 slump test per strength test | [16 empty] | Concrete Pour Record (Refer pg 7)
| Concrete Supply & |  |  |  | If mix contains superplasticiser, all batches shall be tested. If 5 consecutives batches comply, superintendent may reduce frequency to 1 per strength testing
| Concrete Testing – Slump Test |  |  |  | Test within 45 mins of adding cement to aggregates, or immediately prior to discharge when actual haul time is >45mins, or after addition of water. All other slumps to be estimated visually. VR Tolerances: | [11 empty] | Yes |  |  |  | No
[5 empty] | Specified slump, mm | [8 empty] | Tolerance, mm
[5 empty] | <60 | [8 empty] | ± 10mm
[5 empty] | ≥60mm to ≤80mm | [8 empty] | ± 15mm
[5 empty] | >80mm to ≤110mm | [8 empty] | ± 20mm
[5 empty] | >110mm to ≤150mm | [8 empty] | ± 30mm
[5 empty] | >150mm | [8 empty] | ± 40m
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
ITP Ref # | ITP Activity |  |  |  | Acceptance Criteria | [11 empty] | Check Box |  |  |  |  | Verification Record | [6 empty] | Vic Civil |  |  | Multiplex
[29 empty] | Sign/Date* |  |  | Sign/Date*
4.14 4.15 | Discharge & Placement of Concrete |  |  |  | Each load placed within 60mins of batching, unless approved otherwise | [11 empty] | Yes No |  |  |  |  | Concrete Pour Record (Refer pg 7)
[5 empty] | No water added once discharge commenced | [11 empty] | Yes No
[5 empty] | Max and min temps: | [11 empty] | Yes No
[10 empty] | MIN (ºC) |  |  |  | MAX (ºC)
[6 empty] | AMBIENT |  |  |  | 5 |  |  |  | 35
[6 empty] | CONCRETE |  |  |  | 10 |  |  |  | 32
[5 empty] | Max. lag between trucks is <=25 mins. If > 25min aliphatic alcohol to be used. Interval between final discharge and start of discharge of next truck is <45 mins for a continuous pour. | [11 empty] | Yes No
[5 empty] | Vertical drop not exceeding 2.0m Placed in not more than 350mm layers. | [11 empty] | Yes No
4.16 | Concrete Testing – Compressive Strength |  |  |  | Compressive Strength Testing => 28 days post-pour Refer VR 610 3 cylinders (1 x 7day, 2 x 28 Day) taken for each sample, minimum no. of samples: | [11 empty] | Yes No NA |  |  |  |  | Concrete Pour Record (Refer pg 7)
[5 empty] | Quantity, m3 |  |  |  |  | # Samples
[5 empty] | 0-10 |  |  |  |  | 1
[5 empty] | 10 to 25 |  |  |  |  | 2
[5 empty] | 25 to 50 |  |  |  |  | 3
[5 empty] | 50 to 100 |  |  |  |  | 4
[5 empty] | >100 |  |  |  |  | 1 sample for each 50m3 >100
4.19 | Visual check on formwork |  |  |  | Any significant deformation observed? | [11 empty] | Yes No
4.2 | Surface Finish |  |  |  | Surfaces finished to the class specified in the drawings. | [11 empty] | Yes No
4.22 | Curing of exposed surfaces |  |  |  | Curing in accordance with BCRC report recommendations | [11 empty] | Yes No N/A |  |  |  |  | Curing Methodology or Compound: BCRC Report (attached)
4.23 | Removal of falsework and stripping of formwork |  |  |  | Falsework and formwork removed as per VR Table 610.251 (See Pg 5) If early removal or loading is required, relevant approvals and test results to be reviewed by design engineer Days since pour | [11 empty] | Yes No N/A |  |  |  |  | RFI Reference #: Maturity Report | [9 empty] | Project Engineer (HP):
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
ITP Ref # | ITP Activity |  |  |  | Acceptance Criteria | [11 empty] | Check Box |  |  |  |  | Verification Record | [6 empty] | Vic Civil |  |  | Multiplex
[29 empty] | Sign/Date* |  |  | Sign/Date*
| Inspection of stripped surface |  |  |  | Stripped surface finish has been achieve in accordance with specifications (VR610.31) and design drawings? | [11 empty] | Yes No |  |  |  |  | Surface Finish Class:
4.25 | Patch Repair (where applicable) |  |  |  | Inactive crack and/or Patch repairs conducted as per approved procedure, where required | [11 empty] | Yes No N/A |  |  |  |  | Repair method approval- RFI- Repair Product TDS
4.26 | Crack Repair & Monitoring (where applicable) |  |  |  | Cracks greater than acceptable widths as per VR Table 610.241 are mapped and repaired in accordance with VR 687 and approved methodology specific to location. Cracks requiring repairs monitored. | [11 empty] | Yes No N/A |  |  |  |  | Repair method approval- RFI- Repair Product TDS | [9 empty] | Project Engineer (HP):
5.0 TESTING AND COMMISSIONING REQUIREMENTS – POST POUR CHECK & TESTING
5.1 | As Built survey complete |  |  |  | As-built survey is within tolerance when compared to Design & Specifications | [11 empty] |  Yes No |  |  |  |  | As-Built Record – conformance report | [6 empty] | Site Engineer (R): |  |  | Site Engineer (R):
5.2 | Maturity Testing |  |  |  | Concrete has achieved minimum strength prior to the removal of falsework/ formwork | [11 empty] | Yes No N/A |  |  |  |  | Strength Achieved: Maturity Report | [6 empty] | Site Engineer (R): |  |  | Site Engineer (R):
5.3 | Concrete Cover |  |  |  | For every 25m2 of exterior surface area a 3m2 ‘Test Area’ will be selected. Within this ‘Test Area’ 10 concrete cover checks will be conducted. | [11 empty] | Yes No |  |  |  |  | Cover Checks Record (Refer pg 6) | [6 empty] | Site Engineer (R): |  |  | Site Engineer (R):
5.4 | Temperature Monitoring (VR610.22) |  |  |  | Ensure temperature differential across the concrete member being constructed is < 20°C during the period of curing, and internal concrete temperature doesn’t exceed 75°C | [11 empty] | Yes No N/A |  |  |  |  | Temperature Monitoring Report | [6 empty] | Site Engineer (R): |  |  | Site Engineer (R):
5.5 | Compressive strength and slump results |  |  |  | 7 and 28 day strength results achieve min requirements as per VR table 610.051. Slump tests with tolerances. | [11 empty] |  Yes No |  |  |  |  | NATA Test Results | [6 empty] | Site Engineer (R): |  |  | Site Engineer (R):
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
ITP Ref # | ITP Activity |  |  |  | Acceptance Criteria | [11 empty] | Check Box |  |  |  |  | Verification Record | [6 empty] | Multiplex
Sign/Date*
6.0 SUB-LOT – COMPLETION REQUIREMENTS
6.1 | Works Completion Inspection |  |  |  | Ensure works completed in accordance with IFC Dwg & Specifications Inspection completed & recorded prior to releasing activity | [11 empty] | Yes No N/A | [11 empty] | Project Engineer (HP):
Punch List Items
6.2 | Close out NCR(s) |  |  |  | NCR(s) raised & closed formally All out of tolerances notified via Site NCR reporting system | [11 empty] | Yes No N/A | [11 empty] | Project Engineer (HP): Quality Representative (HP):
NCR/s related to lot:
6.3 | RFI(s) |  |  |  | All RFIs have been closed-out prior to work lot submission | [11 empty] | Yes No N/A | [11 empty] | Project Engineer (HP):
RFI & DCN Register relevant to sub-lot only
6.4 | Red Line Mark Ups |  |  |  | Confirm redline drawings are being progressively marked up | [11 empty] | Yes No N/A | [11 empty] | Project Engineer (HP):
Redline Drawings
Summary of Material Quantities
Check List Close Out
PROJECT ENGINEER NAME (Vic Civil) | [17 empty] | SIGN | [10 empty] | DATE
PROJECT ENGINEER NAME (Multiplex) | [17 empty] | SIGN | [10 empty] | DATE
ITP REF |  |  | ITP007a-VC235- | [7 empty] | CHECKLIST TITLE | [5 empty] | Structural Concrete Checklist
Cover Checks For every 25m2 of exterior surface area a 3m2 ‘Test Area’ will be selected. Within this ‘Test Area’ 10 concrete cover checks will be conducted.
COVER CHECKS | [6 empty] | RESULTS
Cover Check Date | [16 empty] | Cover Check Element
COVER CHECKS | [6 empty] | RESULTS
Test Area No: | [6 empty] | 1 |  | 2 |  |  |  |  | 3 |  | 4 |  |  | 5 |  |  | 6 |  |  | 7 |  |  | 8 |  | 9 |  |  | 10
Test Area 1: 0-25m2
Test Area 2: 25-50m2
Test Area 3: 50-75m2
Test Area 4: 75-100m2
Structural Concrete Checklist
[5 empty] | ITP REF |  |  |  |  | ITP007a-VC235- | [6 empty] | CHECKLIST TITLE | [6 empty] | Structural Concrete Checklist
STRUCTURAL CONCRETE POUR RECORD
Pour Date: |  | / / |  |  |  |  | ITP No. | [7 empty] | Work Location: | [16 empty] | Concrete Mix |  |  |  |  | Pour Record: |  | of
Structure |  |  |  | TRUCK ID No. |  |  |  | DOCKET No. |  |  |  |  | QUANTITY (m3) | [6 empty] | BATCH TIME |  |  | Truck Delivery Arrival Time |  | Water Added on Site (Ltr) |  | Measured SLUMP (mm) |  |  | Concrete Sample Taken? (Y/N) |  |  | Concrete Pouring |  |  | Truck Departure Time |  | Placement Time (Pour Finish - Batch Time) |  | Truck Interval on site (max 25 min). *
[13 empty] | TRUCK |  | CUMULATIVE | [17 empty] | START | FINISH
Comments:
* Truck Interval on site = Pour finish - Pour start of next load. Aliphatic alcohol to be used if truck interval exceeds 25 min. | [29 empty] | Approved aliphatic alcohol used? | [6 empty] | Yes |  |  | No
All concrete pouring completed in accordance with applicable procedures, drawings, specifications and approved design changes (if applicable)
Vic Civil Engineer Name: | [18 empty] | Signed: | [15 empty] | Date: |  | / /
Multiplex Engineer Name: | [18 empty] | Signed: | [15 empty] | Date: |  | / /