## Checklist Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix
ea080f51-cec9-5c5d-b21d-26fdf97c141d | checklist | As-Built Drawings |  | As-Built Drawings
634660bc-3569-518d-92ee-49a5ce864e21 | section | As-Built Drawings - attach scanned documents
f20dabd6-3341-47c6-b31f-f9204d894be1 | checkpoint-no-value | As-Built Drawings - attach scanned documents
97c91d10-8a66-5e83-90c0-ef3afede49b8 | textbox | Drawing no.
e2043f2c-aaca-40d7-a11c-99cd6a075a00 | checklist | Cable Test Record |  | Cable Test Record
56b6b7e0-eebb-5754-9e92-822956f50a78 | checkpoint | Upload completed ITR scans
f63572f8-d299-540d-ac09-7e0ff4d9073f | checklist | Certificate of compliance (COC) |  | Certificate of compliance (COC)
243fd733-6bab-56a2-8d1e-76a3fcfcfa73 | checkpoint | Please upload Certificate of Compliance here when complete (COC)
068047d9-77cb-5167-b268-27c3f921fe95 | checklist | Earth Pegs |  | Earth Pegs
e09c6e50-b1da-5e01-bb4c-531f323d7d49 | checkpoint | Mold type identified
8d2a1b0a-b8f1-5a0b-92f8-c0daec33c794 | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
d384c165-bb4d-51f8-81fe-b5c3be9bcff6 | checkpoint | Cadweld Visual test
9ae17236-0bd9-5bc0-96c6-72e9587a7dfe | note | Please attach photo
d5e0224c-c769-5195-9893-dc42f0bfa967 | checkpoint | Cadweld Ductor test
642b96df-9734-5ef4-9531-417d49c3a50a | textbox | Result:
ed808718-9484-59f7-add4-506485bf45ae | note | Please attach photo
cc634f25-a1cd-56b6-a299-6eea07238588 | checkpoint | Continuity test [Peg to Earth Bar]
401dacd4-633d-5769-9b12-62217ab63f5d | textbox | Result:
2c999201-76ad-5aec-8637-77d246062826 | checkpoint | 3 Wire Earth test
b9baa9b0-974d-593f-aa66-43f8886f0563 | textbox | Result:
803b2e55-3d8f-55f2-a311-076921ef9cd6 | note | Pass if <1 ohm
558a40db-769f-5169-86dc-c96239caf2f6 | checklist | Entec Daily Report |  | Entec Daily Report
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
da5f9580-4940-576b-8192-1c0607d69a45 | checkpoint | Daily Report
56c74d02-2feb-5793-b9b6-1d52c994a8f6 | date | Date:
857a0e69-b296-5371-b5fb-4fa741ad2ea6 | textbox | Site:
658fedb9-dfce-5a7f-97b3-e07cfd381bea | textbox | Work completed:
b275ad11-385a-5887-957c-c661c3c5901e | textbox | Issues:
19fbd79d-4e0d-57e8-ad1d-75d6c069af21 | textbox | Weather:
d7a1c016-ea44-5de1-96dc-5603c9a96894 | textbox | Labour:
70900bee-f8a7-56e8-8315-77529c7db7df | textbox | Plant & Equipment used:
2ec8f9c2-4c85-5ed5-892a-88c437f42fb6 | signoff | Signed/Approved:
a1b909fe-58a8-5ec9-be06-af072c4e7dd0 | checklist | ITP-I05B ENTEC - Instrument Loop Check |  | ITP-I05B ENTEC - Instrument Loop Check
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1f4e7cad-b83c-577a-8c4e-e1ae282277d9 | checkpoint | Please upload ITP here when complete
a1bed83c-9ef7-5454-bc46-42f38feeaa34 | checklist | ITR-CL-1-100 General Electrical Equipment |  | ITR-CL-1-100 General Electrical Equipment
40bc9c93-e593-5dbb-adf2-ebf0063e648f | checkpoint | General Electrical Equipment
cb2b4f97-7bb6-5cdf-b568-f35972d86f61 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
60cf451e-2147-50f0-878e-d1d58401ec15 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
ff7f4f22-5a01-5101-8163-c5d80786d1b0 | button | Installation is clean and tidy | Yes,N/A
2a27440d-8e2b-56e8-981f-798dd378e5f3 | button | Mounting arrangement correct | Yes,N/A
39d43819-935f-5663-bd11-12aa8755583f | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
e1c8e2c4-6fdd-52ac-b0b3-1dcd9dc10b14 | button | External cabling is correctly installed and labelled. | Yes,N/A
3f4f40a8-a7c7-52ba-88eb-0ed6855575f0 | button | Check that Equipment is correctly earthed. | Yes,N/A
af3cd66c-f354-5542-9f6d-342aeecff850 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
1659b601-6c2b-50b6-9175-44f9de00b359 | button | All spare entries blanked off with correct plugs. | Yes,N/A
aaf24b8e-ed4c-50b7-a7e2-48d43fa4947d | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
37da6b30-7a6e-5253-b41a-d9a2a5a1b4a8 | button | Conforms to Specifications and Drawings. | Yes,N/A
af731ba5-7686-5fc4-a623-04a38d5c3ff6 | button | As-builts complete. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
a9832c0e-7740-56da-a183-cf3080831d45 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
3be74dfc-63f0-548a-a987-235a08b0da5a | checklist | ITR-CL-1-101A Conduit/Ducting Below Ground |  | ITR-CL-1-101A Conduit/Ducting Below Ground
f9955031-6d35-5a70-b1c8-18bd7eb6cb70 | checkpoint | Conduit/Ducting Installation Below Ground
408a7d94-31bc-56a4-9a3f-c4846c80162c | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
d7f3657d-5f2f-55ea-bd1d-49025ee6f55a | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
83053eed-e03e-57a3-b4dd-37d0d23f1a27 | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
e7d1e47f-c7b6-54a2-8cce-b288322b4e14 | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
b64c2bff-cd7c-5ad4-b6b3-c1a3961ed5cb | button | Check all fixings are tight and secure. | Yes,N/A
14356867-98fd-55f9-8a02-dbaf14dd2fa7 | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
4824a953-d3aa-536e-8688-a9b24f1e2f0a | checklist | ITR-CL-1-101B Cable Supports Above Ground |  | ITR-CL-1-101B Cable Supports Above Ground
07ed07f0-b23b-57fa-8751-a99f24f5ee9c | checkpoint | Cable Supports Above Ground
545ba4b9-3ca9-53bf-a8c1-33531ac2922f | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
08f6bbce-68f2-5214-8e82-3c09cc89da33 | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
9de24e4f-cfa4-5a4b-8afd-73762a459057 | button | All covers fitted if applicable. | Yes,N/A
ee6eb51c-4cb0-5ff4-9fa1-fd6a361665c8 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
49004d30-ee0f-51e2-a510-d838e09c10af | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
2c5500c2-0096-57dc-a19a-400a00138f91 | button | Splice plates, barriers, earthing system secure. | Yes,N/A
d9b9bf78-2d3f-5724-9afc-22cf8925fff5 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
9e40b1d4-5f40-562f-9287-d94c46168b0f | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
63a588ab-dc2c-5420-985d-41d2e43f6907 | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
18d95617-e1a5-5897-8fc6-86d92bd4e5cb | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
94fbde4f-136d-5a56-bfde-952c6a4e7848 | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
2f2f2852-6611-5582-bbe2-bd5b29ac5e2a | button | Tray bonded to structure at correct locations. | Yes,N/A
cda96ee6-f7a6-59c5-b81f-8011bd5bec87 | button | Earth bonding continuity tested – record result: | Yes,N/A
2c57a430-fca0-5f27-95f5-d02cc773e721 | checklist | ITR-CL-1-101C Cable Transits |  | ITR-CL-1-101C Cable Transits
fdf8946e-d2a2-5a47-8940-7ce1e4e369a5 | checkpoint | Cable Transits
51b8c413-f37a-5297-b0b4-21d5691f4593 | button | Transit frame installed as per drawings. | Yes,N/A
96467c01-a9ec-5277-bc40-fd9e3023e7a6 | button | Transit frame identification marked correctly and visible. | Yes,N/A
21c75966-42d8-5280-a54d-21e841a37bbb | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
2f69ee43-4b4f-592f-a137-d72a6e2e14f5 | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
8a5cd616-5189-5ed3-aed7-bdeae1ecace4 | button | Rated insulation installed to transit (where required.) | Yes,N/A
f7647de3-9241-5a92-b7f5-717e39d07ab8 | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
48ddf984-809a-5360-8ed9-1ba660247247 | button | Cables pass through frames without strain on blocks. | Yes,N/A
4b79551f-3b55-583c-9900-01559e09ee55 | button | All cables identified on both sides of transit and visible. | Yes,N/A
502e00ee-104b-509c-aa19-461cf72e7e90 | checklist | ITR-CL-1-102 Entec - Distribution Board Installation |  | ITR-CL-1-102 Entec - Distribution Board Installation
ae4d5efd-a489-5f74-916f-77b38658b02d | checkpoint | Distribution Board Installation (Mandatory Photo)
dd10045f-7c02-5b32-ba7d-bb204fc01509 | button | Inspect for mechanical damage from freight and handling | Yes,N/A
36b5b6df-dbf1-54ba-8e0b-10de26e2b947 | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
60623dbb-82b8-5d8e-a013-e2c297e0caed | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
e41011e6-c5d0-5d9d-bb0f-5df48dc6e223 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
0fdd7ef1-fea1-566e-b9f8-11dc9089b254 | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
be177262-355d-5f6f-a945-678a725568c9 | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
d46d2cc9-6446-596d-8fa6-c45c72ec9df2 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
274fc4ae-0c46-5b8c-ad55-393f1c953843 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
5fad4a36-6295-5402-89f8-c583977a29e9 | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
232f2992-9a08-58cc-9ab7-49d9bbb97d1b | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
2845f34a-33d7-5508-8ec2-13c4edd2f9e1 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
35dd8359-22f7-53ce-a056-50f64edb0e79 | textbox | Earth Continuity |  |  |  | Ohms
3fa14140-bdf5-566b-904a-595c31dfe6d2 | textbox | Earth Bond |  |  |  | Ohms
5d57d622-bdb7-59eb-bd68-fd952363ad21 | textbox | Fault Loop Impedance, PSSC.
dc872782-c03d-5f2f-ab18-f61d35777b0e | textbox | RCD Test results (1/2x I, 1x I, 5x I)
e7372391-e24a-5c79-a513-67117cff418c | textbox | Voltage and Phase Rotation
fe76bdb6-0d0e-5673-9e56-ceeb7a05a647 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
af126e36-13ed-57ce-9666-a41aef3e5793 | checklist | ITR-CL-1-103 Schedule of Test Results DB |  | ITR-CL-1-103 Schedule of Test Results DB
56b6b7e0-eebb-5754-9e92-822956f50a78 | checkpoint | Upload completed ITR scans
b157e1bd-4e02-5ec1-8b09-a5ec0ef2b0a7 | checklist | ITR-CL-1-104 - Low Voltage Cable |  | ITR-CL-1-104 - Low Voltage Cable
5a674726-f510-523e-9da0-6baa8408aada | checkpoint | Low Voltage Cable
af28edc1-96a0-5a5f-bd7d-81afda15fcbf | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
e46a9aa7-5f6d-5842-bc61-cfb5182e4911 | button | Check dressing / cleating, cable undamaged | Yes,N/A
5c2861ad-6315-5bc7-bae4-059e0a0eaefa | button | Check cable cores correctly identified and labelled. | Yes,N/A
22f0c09d-6de4-5561-a994-c02bcf20db5f | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
77d6ecc1-fdb5-5479-8bb1-91e113d59070 | button | Check Armour / Screen correctly made off. | Yes,N/A
fb923de7-835f-5346-9267-0c1d13b74f2c | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
054e931d-90ae-5f38-bb32-dc7a88eacd10 | button | Glanding / Locknuts correctly installed. | Yes,N/A
352202bf-aae8-5e4e-9735-7d1feb3c873b | textbox | Gland type - from: |  |  | Haz. Area Rating
d7c958cc-8da0-56eb-844d-cc4554705410 | textbox | Haz. Area Cert Details.
40c0b575-5d7a-5779-9b72-185f2b33d28a | textbox | Gland type - to: |  |  | Haz. Area Rating
823ab698-3882-53fd-b7c4-a046de87be21 | textbox | Haz. Area Cert Details.
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
17074137-45f3-563a-9f62-a5192912d54d | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
1b3ad86a-fa35-5da0-bba4-564a2dceecad | checklist | ITR-CL-1-105 Control Panel |  | ITR-CL-1-105 Control Panel
b9c48017-8b15-5347-8a29-a890e4be9590 | checkpoint | Control Panel
b32d8822-1353-5faf-8885-16285f555a51 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
97775b31-6c59-5c38-97e7-faa0f79c54d3 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
c6564c61-370c-5dfd-af7b-ac634022aa9b | button | Check for mechanical damage. | Yes,N/A
5a0b37f2-3c66-512a-913f-25fdd58a12c6 | button | Check tightness of circuit connections. | Yes,N/A
2d9e2ffc-ce5f-5879-a79b-95b7019e6c0b | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
6e4c2e2c-19a6-54d0-a92a-78e0458a07de | button | Ammeter scale and current transformer correct. | Yes,N/A
4d78ad12-1e63-5aab-8cba-8f294bbe7547 | button | Check internals for cleanliness. | Yes,N/A
6672607f-dbe1-50f6-a535-09eebcfc9c58 | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
c3cac6f6-ff46-57cd-a687-2e0c862a7aea | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
28cd137b-01c6-5f66-8d4e-68584f0083ff | button | Heaters correctly installed. | Yes,N/A
ffd04a09-51f4-5631-8a62-72a2c8d36942 | button | Fuse rating correct. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
48527285-cf10-596b-b759-6eecee08cb68 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
79d7eee5-04e5-536b-9855-622b05b02767 | checklist | ITR-CL-1-106 - Junction Box |  | ITR-CL-1-106 - Junction Box
a8e8cecc-2cf8-5cda-9b8e-dd2f4097acf9 | checkpoint | Junction Box
245cf2c2-93e7-55f4-8b8f-084910184ab1 | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
e3722cc5-e37c-5219-9ad3-e6af0c0e3bdc | button | Check mechanical damage | Yes,N/A
8d4f6c79-ed60-5205-9480-609b73d9bea3 | button | Earthing installed correctly and as per drawing | Yes,N/A
8cfd38ca-9728-5203-8826-00aa47888d5f | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
216f195f-1635-5eb8-ae32-8039ae13c07a | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
1ee44d58-4ef0-524c-9c0b-6cf1d43db717 | button | Check all Cables & Cores are correctly identified | Yes,N/A
5319ace1-7c03-56db-a539-1b75be9081de | button | Check internals for cleanliness | Yes,N/A
68ff54a5-b7c5-5162-aa43-cc806b8cf101 | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
bee4f161-e6b7-54db-b47d-7cb9ac72ffbc | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
72788ef3-35a9-597e-aa86-40956951b878 | textbox | Record earth bar resistance to earth bond
e567f68d-b461-55a9-9f72-f2a034833fd7 | checklist | ITR-CL-1-107 Heat Tracing Circuit |  | ITR-CL-1-107 Heat Tracing Circuit
79223b5c-5afb-5d19-8fd5-66ebda5dcea9 | checkpoint | Heat Tracing Circuit
f0a55675-6e06-5319-931c-d84f849fe50b | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
1dd2bd0a-28f6-52e7-924d-4b8c31c44e5b | button | End caps and connection kits correctly installed. | Yes,N/A
f0254351-98f8-5421-9a2c-2bd73c9d2a20 | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
997c8955-f08b-575e-8fdd-2e7ca677b1bb | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
b9630306-2879-57d0-bbd6-d4fc782eee4c | button | All spare entries blanked off correctly. | Yes,N/A
7b96e0b9-f07a-5593-b29f-5ac940bbb33e | textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
f94780da-b851-5167-81f5-7b59c66cf3bf | button | Equipment certification meets the area classification requirements. | Yes,N/A
a0d2760e-0c76-5f68-89cf-85c50306a06c | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
e41c45b0-9059-5b1b-bd69-1336d6551631 | checkpoint | Electrical tests
4f89bd2a-fca3-515b-a040-451bbb38e09e | textbox | Insulation Resistance: Phase - Earth
5962cbe2-2039-58a0-a14c-ef598aba88c5 | textbox | Insulation Resistance: Phase - Neutral
9712c965-95e8-5464-94b5-5ca019e8db4d | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
5be6c9bd-3078-530e-b2ae-cdc50eaff832 | checklist | ITR-CL-1-108 Electrical Switch Rooms |  | ITR-CL-1-108 Electrical Switch Rooms
988275f7-8ab8-5361-9934-ba10043407d6 | checkpoint | Electrical Switchroom (Mandatory Photo)
c35c8c3b-6e5f-5852-8138-e12183b47e82 | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
9cb19cf9-3094-5dd8-b75f-c9e71c4da266 | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
6a9f984c-8d46-531e-ae34-602a384296e1 | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
38133667-8af5-5f22-9190-904b05cc6b48 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
1bb30d2e-808b-5e4f-b3d6-1a59666c3f13 | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
39b51e08-1787-5c74-8ef1-2f12f5dc619c | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
506a4e85-a11e-50cd-b2ae-3f34b9aaffe8 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
194f3185-12e2-5655-aa25-e24355f795e8 | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
513c5db0-c432-5a6b-8e94-d5956b35794f | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
987ea7a8-ff94-5ca8-b9b2-f4ceda30a358 | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
c2c4ff65-2e25-515c-98e2-46b89ca72d6a | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
8251fa54-2619-5f08-a5cc-8bc7e06dfb45 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
8782e416-2329-5221-98d9-08b14c73962c | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
cac4a24a-fec9-53cf-8a0d-394f91f9eda7 | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
d9a8e4db-3fc8-58f7-a3cd-6245104a996e | button | Check internals for cleanliness | Yes,N/A
95d95cd8-dd26-5176-8d7c-f8dd08d99591 | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
3ad5afe7-96ec-5205-9dad-f7e3848b1c62 | button | As-builts complete | Yes,N/A
f14d06f7-b040-535d-814f-36634c2f1b67 | checklist | ITR-CL-1-109 Electrical Equipment Package |  | ITR-CL-1-109 Electrical Equipment Package
b90d357e-c70a-5808-b2dc-3ccd86660fc8 | checkpoint | Electrical Equipment Package
de1a4929-51d8-5010-bb5a-8acbeaef7579 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
72770694-ba7a-53a3-8049-ada9f0bd30b5 | button | Check equipment is correctly rated for the area. | Yes,N/A
46e6b0ba-1237-5410-8e55-8782af342125 | button | Check if package is complete with all accessories. | Yes,N/A
0e7ade92-ffba-519f-99b4-c1ace5282e56 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
054459c2-a788-5880-b639-bad34d3ef7ab | button | All transportation supports, stops and fastenings removed. | Yes,N/A
91359383-e280-5b6e-92b6-97eb0e6046b6 | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
b6048e1f-0a8d-5bd7-a133-d4dede4e475e | button | Check package is installed on a level plane. | Yes,N/A
eb88b8e2-3dd1-5fee-a01f-8a04c9481d2d | button | External cabling (if required) correctly installed. | Yes,N/A
f0753463-a336-5ecd-b492-08f4dd0684ec | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
7c187dfb-945b-5f5d-b74c-ec1330baa79b | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
9fdec3f6-3e46-5769-9cad-68cd22178037 | button | Check that equipment is correctly earthed. | Yes,N/A
576774d6-4e9c-5045-b609-1f8c9697a62e | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  |  | Ohm
99e9c3d9-7457-5277-832e-03c87bbc4f49 | checklist | ITR-CL-1-110 Generator Package (LV) |  | ITR-CL-1-110 Generator Package (LV)
faeb6d32-f50c-5e49-950c-dac060a799c9 | checkpoint | Generator Package (LV)
e6fbe5d1-989b-5a7e-b072-80dc518b5d7e | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
e9c3bab9-6b0a-50d1-9266-6b9eff330218 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
ac81d7b6-fbb0-55a6-9705-74febf2117b2 | button | Check terminal boxes and glanding correct. | Yes,N/A
43aaa178-860c-5c80-9eb2-b1fedb98d454 | button | Instruments correctly installed. | Yes,N/A
3f2812c3-0080-5af8-b515-1c8bbb556654 | button | Heaters correctly installed. | Yes,N/A
c0e1f9e1-d4ae-5cc6-9d5e-1670fb4f81d7 | button | Check unit for cleanliness. | Yes,N/A
c04fb45e-b6a6-5b3f-be27-d7d74e800f98 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
8f2c4e75-2f9e-54ec-b5fc-f2eb0b40183e | button | External cabling correctly installed. | Yes,N/A
d349a7dc-022f-5b37-b638-395c086a5f48 | button | Protection of live parts adequate. | Yes,N/A
ab32df2f-ff8b-59a0-910c-73386532b64c | button | Main terminal box complete and terminations correct torque. | Yes,N/A
3302ba7c-ca89-506d-b543-2d6436452c85 | button | Ensure direction of rotation is clearly marked. | Yes,N/A
f809155e-fd49-55cd-b27d-40689fb303cc | button | Check gasket and seals are not damaged. | Yes,N/A
c7f299c2-ab94-5e6b-893a-f06d46279e6d | button | Unused cable entries are correctly sealed. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
1a8692e3-b3a0-55c9-8688-c459a400bd8b | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0b143cde-a7c2-5c3e-82b7-a93cb5550b3f | textbox | Heater circuit insulation resistance:
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
1927ac8a-b833-5bf3-90c1-47fdd4194cf4 | checklist | ITR-CL-1-111 Electrical earthing |  | ITR-CL-1-111 Electrical earthing
a5844d1c-d73b-5ed2-b3a4-ec9d9124535d | checkpoint | Electrical earthing system installation
ed5cbec0-bbd9-5717-afa2-bbabadab2ad8 | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
e9879619-f120-55be-8d65-9857f7539397 | button | Ensure that all metal work is earthed as required. | Yes,N/A
40b4f2a2-bc56-50bb-b7e4-4311ee8e416d | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
012de3bc-21f3-555d-94c1-169b7f7d57af | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
30fbe546-1267-58a8-8b54-ec3ee26c26f8 | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
2e0a11fa-cb2b-5e15-9e21-8f7d322eb8df | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
7795a8c6-9b99-560e-8c3e-4a1637f7e9bf | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
03714326-861f-5bc9-9980-6d59b15a4973 | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
eedc87cc-fe78-5415-af66-eb35afa8d051 | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
27a7a44b-94e5-5483-91c5-3d5da631d8aa | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
ac7a48ae-b931-5d99-80eb-aaf2424ab844 | button | Ensure that earth cable identification markings are in place. | Yes,N/A
673bd3b5-a328-596b-ba6e-9f804e3743d7 | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
8ae72d1d-24bb-55b5-b953-9000650101a0 | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
9fb6c93b-c93d-5301-8726-b7b7ba5927a7 | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
e0acc7d5-ee0d-557f-a05b-651fb56d3458 | textbox | 3-Wire earth test results (If applicable).
930891ae-e43d-5ca6-86d5-adf9a95d195c | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
a45de04b-c848-5952-8d2a-e31446744d3f | checklist | ITR-CL-1-112 Motors |  | ITR-CL-1-112 Motors
b379033e-6a86-54bb-887a-d19e9726729c | checkpoint | Motors installation
481f033e-46c8-5430-b530-6f504e55bdbb | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
88c4988e-d18e-5e59-8c4b-6484dfd5c17f | button | Space heater | Yes,N/A
47f7463d-fb36-563e-89c8-501bad7c1569 | textbox | Space heater specification (Power (Watts) and Voltage:)
92fda034-b723-508b-8166-4e1c11fdac37 | checkpoint | Nameplate details correct and in accordance with the data sheet (Mandatory Photo)
73a15ef7-a7ab-543b-88d7-1ca840163365 | note | Upload clear photo of nameplate
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
d173609e-3e03-5d51-965a-5b0e1db325ec | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
d78a2bae-0d71-5dd3-a29c-8bdd83d3cfed | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
6c5ab35a-a8bf-536c-8c9d-a833e064cd07 | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
55c44db7-a0fe-53b4-9b37-a0039b77be66 | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
92238dca-2d29-5bed-80f2-44e4db9408dc | button | Correct glanding for area classification. | Yes,N/A
75e0a3c4-6588-50e6-8a4b-918df7a2f881 | button | Holding down bolts fitted correctly. | Yes,N/A
7866c60e-e106-5a1e-aad5-30fb8248593a | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
890fb388-d930-5723-a4c5-a6ac805f468d | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
774fc876-b113-5771-bb52-817081b294bc | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
68654064-6090-5f89-affc-b6fa25f4374b | checkpoint | Motor Installation Testing
16f8af62-d6d0-51ab-b8a7-f880c9595eb9 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
87efb043-7852-5434-b74f-5895c1d22b39 | note | Insulation resistance U, V, W
c9db8775-ca52-5fec-a144-234e961e5c9c | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
a7ca9aef-9cb7-5178-bc50-97f58c58ecb6 | note | Insulation resistance U, V, W
e440f398-1b1f-595e-8d57-d7738c1f20d1 | textbox | Motor continuity between windings
c33dab3b-e5d0-5e71-a1e9-fcb65f2c5561 | note | Continuity U1-U2, V1-V2, W1-W2.
5692b944-3d62-5378-96d9-2d08640ed6ef | textbox | Space heater continuity & resistance check
832cb8eb-373f-53a3-8db7-0431fb43e82d | note | Continuity & Insulation resistance results:
696c7508-4ab7-535d-b554-cc4f03324fe1 | textbox | Thermostat or RTD wiring resistance check
3cbbd2db-5840-594a-81c1-779596aabf45 | note | Resistance:
c45f3e5a-11d5-5281-b95e-25a319732177 | textbox | Check motor is earthed correctly and record motor earth bond:
4a998987-8120-5498-b98d-bdc0f10f4da8 | checkpoint | Additional checks
9b10d71f-3358-507d-8a4a-20893d8d6f74 | tickbox | Winding temperature detector
1609bd00-806f-5fcc-849c-5d4e4e07be9e | tickbox | Air temp detectors
5474f5ca-d6b1-5888-a4bb-ad0f40e3eb48 | tickbox | Bearing temp indicators
76cb80fc-a5da-55c6-ba74-6904835b8bd0 | tickbox | Vibration Monitors
700fd2bc-8cce-59c0-b270-ba655c37ff4f | tickbox | Condensation detector
ad7a159c-e128-5124-b632-ab7f525a6695 | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
3080b9a2-d7b9-5fab-9678-883bf29f3898 | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
45e0c59b-ebdc-5bf7-83fd-6aa3efd96f3a | button | Installation conforms to specification and drawings | Yes,N/A
4c6f4151-1a21-5825-9277-5c1539c7db16 | button | As-Builts complete | Yes,N/A
19513ac1-0858-54b3-8f99-b38a549be2fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
b2400ed4-f494-5645-bdd2-a3a1c7d8143e | checklist | ITR-CL-1-113 Motor Control |  | ITR-CL-1-113 Motor Control
8b7f5c8f-9378-5c72-98a0-cff0c3ff4659 | checkpoint | General Motor Control
271889a3-0b99-5efa-8b30-3c840a309d4b | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
42dd4760-41a4-512b-a9ab-c89d144ec924 | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
3ec738bc-3381-576b-ab5d-b8dd559f3a94 | button | Check preservation and transit items are removed | Yes,N/A
7ae9798c-f24b-5c71-9791-d6fa6e08594d | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
2252f925-b80a-52dc-aa9a-30b89e0a442c | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
b37a4cd2-8560-56fa-ba6b-3ef8f07e645d | button | Check earthing bar and connections are correct and tight | Yes,N/A
423e5baa-bfdd-5581-bece-8cab5fee68f0 | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
97ad2b41-4cff-562c-897a-79017543f3f1 | button | Check phase identification on power cables is correct and visible | Yes,N/A
bc55e934-6184-5205-818f-f531f2da50d9 | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
7de845f5-1cc1-5751-98f9-953a1e450f1f | button | Check all other nuts and bolts are tight | Yes,N/A
c4b35821-b001-577e-981b-0ed6f1fb942a | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
dee4f953-7134-5cc7-b78d-d26f30a10744 | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
12787137-a0bd-5672-be3e-39544771225f | checkpoint | Variable Speed Drives (VSD)
41614d56-a8af-5092-9cb0-75a07864792f | note | Record VSD Details
3e1612e5-3dc5-5ffb-8b8c-a9c5a0994c9e | textbox | Volts (Input) |  |  |  | V
bbffba4a-45ee-5161-95ad-eb804bcc9014 | textbox | Amps (Input) |  |  |  | A
fdeeec23-31f5-5b22-8981-4c3cc478e235 | textbox | Amps (Output) |  |  |  | A
ad6bba94-8c05-5051-afb0-fdb46e1f73fe | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
3ba30a88-6699-5648-9dc6-3850dcbd81c3 | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
8edb13bc-60e2-5deb-b03d-0e1248cf12c7 | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
ee2d6df1-da80-53e7-9211-f7067bc8f4df | button | Check control signal cables use twisted pairs | Yes,N/A
a909a109-960c-5031-99e4-3d7bd42f0822 | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
62401cee-bc7c-5620-8e17-9c0b097e0f37 | button | Check analogue and digital signals are run in separate cables | Yes,N/A
100277f1-21fd-5165-beba-4958eacfcc37 | checkpoint | Voltage segregation
8ad4c2f8-6471-5e41-8427-26fdd46c4ac2 | button | Distance between input power and motor cable >300mm | Yes,N/A
8d4b68cd-8844-5208-b74e-25cb470a457d | button | Distance between input power and control signal cable >200mm | Yes,N/A
39727ef1-4ef6-56e4-bec7-abaaafa7ddec | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
e2516a13-edf5-528a-a49c-36ea963a218a | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
e0c0a718-f04e-522d-9bf2-3957e675e456 | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
c279141b-58af-5282-a021-59e7112de91f | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
d1321e44-ff12-59d4-aa8a-0df8e46c8a8d | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
dc639f77-ddbc-59a0-a1ff-43b2a1403aee | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
7746c8dd-c7ce-51cb-85e4-2ed0eeb2a50e | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
895b07e9-0177-56cf-a526-b503466d8675 | checklist | ITR-CL-1-114 UPS Installation |  | ITR-CL-1-114 UPS Installation
347ed6f2-edf9-53cd-afb5-7250c75c7497 | checkpoint | UPS Installation (Mandatory Photo)
655d03c8-7681-5332-9444-21a0283d5354 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
ed9c1d95-9a89-57cc-8d03-1f0d8b36ff8a | button | Check for mechanical damage. | Yes,N/A
aea841e9-31ab-539f-872a-1044ac154d25 | button | Panel IP rating is correct. | Yes,N/A
397fc40c-7a69-5ef2-b67d-09213ffe7cd1 | button | Holding down arrangement and seat alignment correct. | Yes,N/A
262740ab-cdd3-5090-9149-ba920db5d195 | button | Panels aligned correctly. | Yes,N/A
1c9ce2cf-65ed-5c1a-b678-dd6e6b26c32d | button | External bonding correct | Yes,N/A
b3e5c818-c5cc-5e49-8587-92d32e461ac7 | button | Phase identification correct. | Yes,N/A
e5ac5a6a-a284-5786-b72e-f99a363362e6 | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
227fdf0c-9120-58b7-a162-b64a01cabd0c | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
64594450-bd12-5ca3-b334-388aedfe47eb | button | Check Main Isolator and Bypass switch operation | Yes,N/A
de0d11ea-7945-52d1-a887-d18d09663978 | button | COM Interface & Mod Link. | Yes,N/A
e828b151-e799-55a6-8ca1-70b7061ef18c | button | Padlocking facilities correct. | Yes,N/A
3fdce359-213a-5841-8809-e3ad8cf1f943 | button | Check internals for cleanliness. | Yes,N/A
1c2b202d-3598-524f-8900-035008717f05 | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
4b09e7bb-403c-50e2-9f20-7893df9d86c5 | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
37d878a1-cbae-520f-8189-62138a287e44 | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
0bf69a78-986b-51cb-8425-f587f1c40d47 | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
6fc4bb8a-4347-5aaf-885b-15701c3db0fa | checkpoint | Test results
c7229fd8-3143-5995-ac3a-94e91ae24239 | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
5955295f-23db-5918-abcb-2b308456c01c | checklist | ITR-CL-1-115 Lightning Protection |  | ITR-CL-1-115 Lightning Protection
b51a0ab7-a35c-50cd-8d4c-319c10a51654 | checkpoint | Lightning Protection Earthing system (Mandatory Photo)
962dc00a-bf7b-5e05-acf2-d5645b2eb507 | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
3fd75246-24af-5c69-959d-532d34b705ac | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
0fb071fe-8243-5ed6-9685-eb139ed94ee5 | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
298085f4-2d0f-5af7-8443-080df6513427 | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
c6f282a1-b08f-519d-ba1d-89ebf825c0b3 | button | Check all installed components are firmly secured | Yes,N/A
61e068f0-3e1d-5b6a-a39c-5b705e475cec | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
67727910-4ffa-5a66-a264-005150daf9e9 | button | Check earth termination systems are interconnected | Yes,N/A
12880d6b-3ef4-5d2c-82ae-fd9fd56afbd6 | button | Check isolating and switching devices correctly located | Yes,N/A
ca1a8f84-153c-54c8-a30f-ae68fac9c2a5 | button | Check warning signs and diagrams are installed | Yes,N/A
665900b8-513e-5425-b6b9-1b80f47d7d52 | button | Check accessibility for operation and maintenance | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
157ca8be-2ef6-5e87-ba6f-f102e88400c7 | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  |  | Ohm
ddcc6e90-3827-5bad-a39e-b99ee4d7280f | textbox | Earth termination system resistance is correct and record value |  |  |  | Ohm
b1d32614-dcb6-5954-938b-7724481d8f46 | textbox | Record the insulation resistance of the electrical installation |  |  |  | MegaOhm
a5a93179-92e2-52e2-8be0-00cabc3894c7 | textbox | Continuity of the main and supplementary equipotential bonding: |  |  |  | Ohm
b57f4fd6-75d7-5a87-adfe-e2df08d34c15 | checklist | ITR-CL-1-116 Fire and Gas Detection Alarms |  | ITR-CL-1-116 Fire and Gas Detection Alarms
e9820304-02d0-5985-8faf-5cc6d712f981 | checkpoint | Fire and Gas detection alarms
91f7b1d3-927a-5fc1-9922-bc889c00505c | textbox | Make and Model
f74503eb-f8b8-5f8e-b15b-bc3a87d9ea8a | textbox | Type
5e850025-09cc-5119-915a-620b56b44ce0 | button | Location correct as per drawings | Yes,N/A
8b274b91-c78c-587a-b0e8-39b43622205c | button | Component & Type / Model correct per equipment schedule | Yes,N/A
d7a2ddc7-5046-5fa7-8d29-7be80745b4dd | button | Cable connection & termination correct | Yes,N/A
8db5056c-243d-5516-a00c-13058274d2c3 | button | Installation free of mechanical damage and clean | Yes,N/A
0ce5a0e7-0835-5d7d-997b-7463dc6ec51e | button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
ad343b60-f41d-54d7-a669-217ebad820be | button | E.O.L Installation | Yes,N/A
10a1d75d-7f45-549f-ae11-b119f9100343 | button | Test tubing installation | Yes,N/A
16a9ac87-3d01-5ae4-b987-e759bbbf1289 | button | Detection Path Clear | Yes,N/A
e7581576-5a10-5963-90b0-44587360e1f6 | checkpoint | Inspection
90a3b868-54d7-5ada-b1b3-d1cf777ceca2 | textbox | Tag No.
748cea45-9cca-57af-8ec8-1452e3e9e996 | textbox | RX Tag No:
bdc38525-5b3f-5bef-9b2a-6d376212e844 | button | Area Classification correct | Yes,N/A
96e54638-45c0-57d7-bc02-07452460aa8b | textbox | Hazardous Area Certificate:
d4d1741e-bff6-5186-b897-df18213d20a0 | textbox | Detector Type:
a8e6f72e-0e9d-5a3a-8251-8461ff0dadb2 | textbox | Gas Type:
dc36ed29-eb76-5be6-82d8-6065c51d4cc2 | textbox | Supply Voltage:
6489be0d-16ce-5477-b392-be1e7b98d1c2 | textbox | Output Signal:
f60ecb48-734f-5a72-b2ef-09bf19aa9dab | checkpoint | Functional Check
94fbb7c7-03dc-5b8c-b852-90e5415b1f35 | button | Self Test | Yes,N/A
103afaec-87cc-596d-b875-68318384ef65 | button | Alarm Operation | Yes,N/A
eefdd49b-785e-5e37-b0c0-50283fdb91f5 | button | Fault Relay Operation | Yes,N/A
18957424-83c6-5d83-9bbe-1169bdce9e22 | textbox | Measured output (clear path)
1b23ccee-71d3-56c0-9249-3592d9153ad6 | textbox | Measured output (blocked path)
0ad6eb12-6904-568e-b578-63d2ce00b169 | textbox | Measured output (filter in place)
f7366789-c1ce-5e77-a10e-7a5fc1d1b2da | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
fcddc6c3-9e70-5ee8-b21d-2cf24bff83d8 | checklist | ITR-CL-1-117 Instrument Tubing Installation |  | ITR-CL-1-117 Instrument Tubing Installation
22a4b0f7-8c08-5898-8def-9f2ce9f0fe16 | checkpoint | Checks Pre-Installation
2e7fc366-26f6-5021-8aeb-271a33e5282f | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
9ca1d4f5-95e2-5a47-8b4e-73e78d1f79e5 | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
843f4816-9c4b-55d5-9da9-9c719e8bcddf | button | Tube fitting size and type confirmed and available | Yes,N/A
a6d87294-9fa2-5060-a418-dbd33f374e00 | checkpoint | Checks During and Post-Installation
4968da8e-676b-5ef3-bdba-b430d7ad1d52 | button | Correct thread compatibility and engagement | Yes,N/A
84be2f7d-f244-5d87-a8ed-adff19279816 | button | Correct thread tape and sealant used on fittings | Yes,N/A
0cfcae7a-f9b5-57e1-8fc7-32ebcede9857 | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
49722970-578c-56ae-b877-09e9203c11e5 | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
70763579-d4d8-56c6-a6ec-bb4ba1a5c649 | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
c2e51bd9-35f8-50e0-9389-00c99de63ea7 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
52ca6a4f-fe50-5c4d-8cb9-16bdeacfc70c | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
66858c37-fbb2-578d-811b-66e29a58aff3 | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
e8c5a865-c141-5574-97df-4ce185ce3988 | button | Random check with No-Go gap gauge | Yes,N/A
6306f1ee-a88c-5e02-b5d3-513693e4dbfe | button | In service leak test performed and passed (ITR-CL-1-118) | Yes,N/A
b77b2185-19d4-575a-996e-f93077065e0d | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
8312427c-3f1e-5a34-a83f-13a43b12be7b | note | Refer to Swagelok book for tube/thread size pressure ratings
0ed21009-a791-5a6d-a31b-2bc2bbe6348f | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
2cde575a-c826-5aad-82b0-bfae9f329be1 | checklist | ITR-CL-1-118 Instrument Pressure/Leak Test |  | ITR-CL-1-118 Instrument Pressure/Leak Test
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
312025e1-3aa4-5c7d-aa52-585ee212bd62 | button | Tube identification correct | Yes,N/A
03343d53-ec9d-5c39-8c6b-fa6ca5dfaf29 | button | Mechanical damage visual check | Yes,N/A
c939ebae-325e-5129-8cc3-5fbc505398b6 | button | Flow direction and instrument orientation correct | Yes,N/A
6913b8c4-d27f-5fc4-8dd5-eb1b6002100f | button | Tubing size and installation correct | Yes,N/A
ea42bb29-f001-5a6e-8d35-77d90be2e691 | checkpoint | Testing
6ea556cb-8c60-580f-a306-65fdc03cf287 | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
9dde934f-af34-5214-b0a2-800a3990188a | textbox | Test fluid:
da7acc81-9ae5-5c3f-b054-5acf2799e4a1 | textbox | Test pressure:
a1bea254-af4e-50f2-ae2d-92369cf7ecf3 | textbox | Max design pressure:
f64592ff-f819-56bc-a234-d2a209e0f199 | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
d3fd68d6-32f5-5f43-8ac3-f077f5b1e763 | textbox | Duration: |  |  |  | Minutes
8e886e08-9f34-51e4-b3ce-a7a66cde1937 | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
09e66fd4-b7db-5f5e-a369-00651bd26e51 | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
f940703f-8ef3-52f1-adc2-1efb474c5b33 | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
cc603aa1-7bc7-5247-bb26-b44d6904a9f6 | button | Check hydraulic lines flushed to project specification. | Yes,N/A
36d17a09-847c-57d3-8c79-12c7b3566a54 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
5c63d0bc-60d3-5a41-b7d8-7d1318c83bd7 | checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) |  | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation)
56377b54-fde7-5406-837c-3890686afe74 | checkpoint | Equipment
c7902cfb-91a8-5221-ace4-52220adfc729 | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
71885bce-d253-55aa-aad6-1f6e8b3f00ae | button | Equipment checked for additional items as applicable | Yes,N/A
2c404141-581b-5dcf-b0bb-fb18186bd505 | checkpoint | Valve
973b94f3-475e-5c09-ac58-26f45d41ebe1 | textbox | Valve Size:
f20d9d4d-85b2-5a40-8dd0-eed2475e8bbc | textbox | Flange type:
46178969-5f15-5787-967e-863a89227d55 | button | Material certification correct | Yes,N/A
dfd1b5de-f2c2-5283-bcd2-dd64538b2fbf | button | Trim material correct | Yes,N/A
1456995c-c9c8-515f-8646-65968398415c | textbox | Rating:
d9937dd5-b397-5c5a-b005-517fdf84e468 | textbox | Service:
6d28f2af-9daf-56df-9677-24b936328a25 | button | Body material correct | Yes,N/A
5d3f0c67-e22a-5d31-94c0-5dcde54f30fb | textbox | Leakage class:
0610e54b-0dee-561d-8cbb-5ea26874b2fb | checkpoint | Actuator
ea7a4302-e31b-5d16-9163-9b69fbc71306 | textbox | Input range: |  |  |  | kPa
4b4228e1-3a1a-58d9-b97c-6fefb9148e4f | button | Failure action | Yes,N/A
ab7fed77-7f58-547c-a589-3dcc6d39745a | button | Hand wheel operation correct | Yes,N/A
a1a658d5-b431-5d40-b5b9-296b18cd0c83 | checkpoint | Positioner
9f9f468f-b7eb-5cb2-bee2-4a391dc38bba | textbox | Signal range
28a5795d-b6dc-5958-87ef-423101e4c7b3 | textbox | Output range
0c71f2ec-255a-5b0d-b0cf-ac779f8e58bd | checkpoint | I/P Converter
c28cfeb1-1625-5399-94a5-8b013f789ddd | textbox | Signal range
f6dda411-d9ab-5ecf-b26e-9962402b51f9 | textbox | Output range
d888314d-8e0b-5d10-aa66-e798050507bc | checkpoint | Filter/Regulator/On-Off Valve
d39e7391-c9dc-5e77-b9d2-4a7d9c6e01eb | textbox | Range |  |  |  | kPa
3b3b07a2-f274-5b91-ac1e-4326125d8d3c | textbox | Pressure setting |  |  |  | kPa
28d8afca-429e-5a36-ba0d-b32abd7deac8 | button | Stroke Time correct | Yes,N/A
7a3a8aa0-b4a0-5d29-acec-8e10a7739541 | textbox | Open |  |  |  | sec
eddc7056-f6b2-51ad-b7a6-b766b2ed6c50 | textbox | Close |  |  |  | sec
ffc3d9f6-1adc-59c1-af3b-bfa1ef97e584 | button | Open/Close times conform to commissioning specifications | Yes,N/A
12af7e2a-fcf5-563a-ada2-83262dee1165 | checkpoint | Fail Action
ec614ba9-235a-594e-a1c7-197827b5dc88 | dropdown | Electrical Fail Action | FO, FC, FL
1e269914-91f1-58b1-9190-82ba3aa37633 | dropdown | Motive Force | FO, FC, FL
2f5147e0-439d-5cf3-a34c-a68c79a610da | checkpoint | Valve Field Calibration and Hysteresis Check
ec856f7d-5948-5501-a248-63d28d70d62e | tickbox | Confirm test equipment is within calibration period prior to testing
4ecce144-7b92-5376-a8fe-9d25739a69ab | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
fc906e42-ff91-5aed-8b52-b7a39f44db3a | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
68e785a0-34a3-5d35-8fc4-1b0a402ae766 | checkpoint | Proximity Detectors
04cb349a-1c6f-5eea-ab26-85787735f476 | button | Open switch set, correct mode setting | Yes,N/A
8cc87a8e-f8b5-56dc-b10a-dfe5e65a97d8 | button | Closed switch set, correct mode setting | Yes,N/A
6b496ae2-8a2a-5e38-8e80-fa765b80c4f4 | button | Electrical connections and certification correct | Yes,N/A
ca31728d-089a-5a86-91f8-e6fa49290174 | checkpoint | Solenoid Valve
636044cd-24db-507f-a623-010ac1276448 | button | Operation correct | Yes,N/A
825a6f2e-3bfd-5f04-9627-c8e72439318d | button | Electrical connections correct | Yes,N/A
a5a070ca-4531-58e6-9b16-c2a979213aee | button | Electrical certification correct | Yes,N/A
8c15cfd9-ce6b-59f0-9944-7b5c80044bec | textbox | Voltage: |  |  |  | V
624b2e20-bee3-5885-bc05-3f03ebefc6ae | button | Pneumatic connections correct | Yes,N/A
c6f14b9f-450f-5187-af0b-1e63d1affbc1 | textbox | Pneumatic pressure |  |  |  | kPa
cf469d5d-719b-5c9f-939e-4b3f14281521 | checkpoint | Pilot Valve
3a1d4e7b-6274-5ca2-bf6a-cd2e64e24abd | button | Pneumatic connections correct | Yes,N/A
0ff1938e-c0ce-5503-ac50-7b00f7a334e6 | button | Operation correct | Yes,N/A
68617ca0-7a10-5bf7-9d34-ff60b33b6661 | button | Action/Lockup | Yes,N/A
d95c96d9-19e7-5920-8c36-be758c1c94e6 | checkpoint | Hydraulic Actuator
036099cb-3bb7-5f84-85a2-37263c265a39 | textbox | Working pressure
a8d86c7d-51e2-5730-a39f-eb731ad29d79 | textbox | Manifold pressure
2e2a6b4d-e0c9-5d86-999a-8d648dc9e31a | textbox | Fluid type
1f5173af-7b7f-5d87-8ed3-256ac6b591e2 | button | Hydraulic connections correct | Yes,N/A
f72452df-ab6f-5271-a347-de98a3718a92 | textbox | Regulator pressure setting
a62b06dc-d632-5faa-a886-7f19368bb4f7 | button | Pilot operation correct | Yes,N/A
3feee96c-5f87-541b-a1db-c34642a76ff9 | checkpoint | Accumulator
3bf6099a-5f6d-5d4e-bd7a-16979f529e99 | button | N2 Charge required | Yes,N/A
4c5449a4-0ec8-5004-87f1-08930390d5ef | textbox | N2 Pre-charge pressure
ff4e652b-ceca-516c-b404-3ed4ad5368c2 | textbox | Pressure switch setting
5567df27-7709-520a-ab43-37b13f72b8d8 | textbox | Working pressure
c0522002-1dae-5fed-a3f7-c043c09a2efe | textbox | Output range
196ad47c-8082-5bb5-9add-53d69ea5257a | button | Volume tank & check valve installed correctly | Yes,N/A
5bae141a-6bec-570a-8885-6c22a91756da | checkpoint | Electric Actuator
84e375bd-edcf-5a31-b959-00c66a045863 | textbox | Voltage:
2b8a5344-b4fc-58ce-8c3e-d5327a046dae | button | Electrical certification correct | Yes,N/A
3003da78-38ff-5327-93e1-7add060dee85 | button | Electrical connections correct | Yes,N/A
9fa4f9d0-7ae5-50e4-a995-52c4ab144116 | button | Remote operation correct | Yes,N/A
96f775c8-715b-5289-a875-4ac20e781985 | button | Local hand operation correct | Yes,N/A
1e2878e8-d699-5703-ac7e-4b52dd229efc | button | Torque switches and travel stops set | Yes,N/A
7d829060-f74f-56ec-b586-e00635137c82 | checkpoint | Miscellaneous Equipment
dd2193cf-450f-522e-9330-aaf0e6a2d7ff | textbox | Description
05d4c2dc-1e67-5653-986b-0445b024b51e | textbox | Manufacturer
a3940dc7-1266-583e-ac24-f1d0978f7aff | textbox | Model No:
334edf41-6e51-5019-999d-03dd0b9909d1 | textbox | Serial No:
e3ddc484-f2ad-5601-8d8a-4881522e51e1 | textbox | Range:
18003b78-0bf7-5e2f-9e09-b614d9233ece | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
b7eaa2f1-f3b6-5768-9905-32e5b3f1655f | checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) |  | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation)
56377b54-fde7-5406-837c-3890686afe74 | checkpoint | Equipment
517f5143-2410-513c-8d7d-2f49f3d447d4 | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
e22f1dcd-0f91-56a9-b6cb-a657c721443f | button | Equipment checked for additional items as applicable | Yes,N/A
2c404141-581b-5dcf-b0bb-fb18186bd505 | checkpoint | Valve
9c92b41f-7204-5212-aed6-3257e9f1b7cc | textbox | Valve Size:
7d24d3e9-9f5b-5d1c-a74f-957af5d4b1f3 | textbox | Flange type:
0a702e8c-08c2-5464-b2d8-fd941f8a3d01 | button | Material certification correct | Yes,N/A
92bb5ec1-ca60-5b8f-b9cc-d35f849c577a | button | Trim material correct | Yes,N/A
b7a66705-312c-5a37-9753-203ae866d715 | textbox | Rating:
5c677dbd-6c51-56ca-b12d-e43861762262 | textbox | Service:
e53a853d-d881-565d-b124-03e1435e4930 | button | Body material correct | Yes,N/A
4d94fca5-e1ce-5478-bf38-7f1643e91e5b | textbox | Leakage class:
0610e54b-0dee-561d-8cbb-5ea26874b2fb | checkpoint | Actuator
9b7a3aed-3141-5b36-9b2e-2f29c818b119 | textbox | Input range: |  |  |  | kPa
e668a569-7003-53d4-8b08-8e4c92694a20 | button | Failure action | Yes,N/A
2cc0eae6-ebc3-52de-9a88-26880a470426 | button | Hand wheel operation correct | Yes,N/A
a1a658d5-b431-5d40-b5b9-296b18cd0c83 | checkpoint | Positioner
b353380f-c770-5581-9f3c-7bc0f3062240 | textbox | Signal range
692a4b53-6dd2-5d34-b8ee-c78765cbf08d | textbox | Output range
0c71f2ec-255a-5b0d-b0cf-ac779f8e58bd | checkpoint | I/P Converter
23899687-e4b5-5875-ab6e-0b992899d669 | textbox | Signal range
d9e416c5-a93e-555c-bcef-34fe261bf1ab | textbox | Output range
5d274912-fff7-50ca-a3f4-56a014ce13c4 | checkpoint | Filter/Regulator
133eac93-481f-5f9c-a0fd-083ac3e95430 | textbox | Range |  |  |  | kPa
afb87505-cc8c-590d-a8ab-f4fbe6467c95 | textbox | Pressure setting |  |  |  | kPa
12af7e2a-fcf5-563a-ada2-83262dee1165 | checkpoint | Fail Action
ec04e265-647e-56b6-8b48-479e5b1f7d91 | dropdown | Electrical Fail Action | FO, FC, FL
1f215402-4968-5151-b202-9151944b4fa6 | dropdown | Motive Force | FO, FC, FL
68e785a0-34a3-5d35-8fc4-1b0a402ae766 | checkpoint | Proximity Detectors
a6571574-2216-51c5-87cc-f29592cd916a | button | Open switch set, correct mode setting | Yes,N/A
a5c32505-2c84-5fb2-883c-dc82759dd51e | button | Closed switch set, correct mode setting | Yes,N/A
66d0472f-bc64-5a28-bdb5-47499a2c6fa0 | button | Electrical connections and certification correct | Yes,N/A
ca31728d-089a-5a86-91f8-e6fa49290174 | checkpoint | Solenoid Valve
477ffd2c-7a55-5882-b145-66e2e665aa61 | button | Operation correct | Yes,N/A
5e5836a0-2ecc-5161-83ad-45659d110dd2 | button | Electrical connections correct | Yes,N/A
1ed1de9a-41c6-55d5-9c48-622ffc409103 | button | Electrical certification correct | Yes,N/A
3689c809-ad49-5bd0-99c2-7966adc57484 | textbox | Voltage: |  |  |  | V
a9b111b0-2063-56fc-b003-48e1eab4f337 | button | Pneumatic connections correct | Yes,N/A
a48a85ea-943d-5624-90ad-a23cfcdbae12 | textbox | Pneumatic pressure |  |  |  | kPa
cf469d5d-719b-5c9f-939e-4b3f14281521 | checkpoint | Pilot Valve
f7ba09ab-1e8a-52b3-ae21-6066c26d4698 | button | Pneumatic connections correct | Yes,N/A
9e3f4bdd-0d8a-54fe-a5bd-b25a21d04ff5 | button | Operation correct | Yes,N/A
e739200f-9bd6-5986-9259-34611ad5a919 | button | Action/Lockup | Yes,N/A
d95c96d9-19e7-5920-8c36-be758c1c94e6 | checkpoint | Hydraulic Actuator
3e3f1287-83ab-5697-a097-d3fb85193daf | textbox | Working pressure
ce6ad7ab-df42-5863-9dc3-92275dbbab72 | textbox | Manifold pressure
47db2c3b-2c8e-5791-92b3-a2f611270808 | textbox | Fluid type
00b85d2f-e7eb-54fe-8746-2b6cd1a8e3de | button | Hydraulic connections correct | Yes,N/A
cfea285c-20c6-5066-afe1-e5ea2b77b970 | textbox | Regulator pressure setting
81455763-1465-59ed-9c39-72ef5c753235 | button | Pilot operation correct | Yes,N/A
3feee96c-5f87-541b-a1db-c34642a76ff9 | checkpoint | Accumulator
5fe56fca-7110-5ccf-8f3a-2b4f73566419 | button | N2 Charge required | Yes,N/A
28b774b6-e360-5287-ae20-275ef49ca2fb | textbox | N2 Pre-charge pressure
60cc1dcc-44df-567a-b2ab-1eabd920de9a | textbox | Pressure switch setting
c4bb92f6-e099-50ca-b2b0-829d0328b7d4 | textbox | Working pressure
de143b9b-52d2-54e5-9891-144af16a37d1 | textbox | Output range
d81fa3fa-09ec-5bfa-8162-7b63a087e6fa | button | Volume tank & check valve installed correctly | Yes,N/A
5bae141a-6bec-570a-8885-6c22a91756da | checkpoint | Electric Actuator
d2e1d6f4-25f5-5405-80f3-5b2f510618d2 | textbox | Voltage:
56ea04ca-b789-5764-ae95-c2a9a5e23027 | button | Electrical certification correct | Yes,N/A
82255a42-1ddb-53fb-a6a3-d64f51011a20 | button | Electrical connections correct | Yes,N/A
babce00a-1db7-5a22-b91a-4a9c1e9df755 | button | Remote operation correct | Yes,N/A
65f0b7d2-9988-5b1c-926a-12f183b4121d | button | Local hand operation correct | Yes,N/A
a27675c1-7419-56b3-a584-16fe4381ca7e | button | Torque switches and travel stops set | Yes,N/A
7d829060-f74f-56ec-b586-e00635137c82 | checkpoint | Miscellaneous Equipment
b2608af8-33a2-5723-b44f-13b93084cf30 | textbox | Description
f037109f-9268-5948-bf2c-6432b6d71b72 | textbox | Manufacturer
f217159e-30b0-5085-b0f1-0d648c1f56cd | textbox | Model No:
7aa41820-86e2-5bde-a60c-fcbbe8f5f391 | textbox | Serial No:
2e603b63-0a65-5ca2-8ae9-d1d1e046e97f | textbox | Range:
18003b78-0bf7-5e2f-9e09-b614d9233ece | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
66b9bb91-851f-562e-a7b8-bfbc7a8b6142 | checklist | ITR-CL-1-121 Instrument Installation |  | ITR-CL-1-121 Instrument Installation
ed193010-c972-513a-b2cf-5f996216c7be | checkpoint | Instrument Installation (Mandatory Photo)
1012254a-4972-5fdc-8d71-df31d7dadfa9 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
0c741fc8-02f3-53e1-ab33-06f15918df18 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
54a6e2ff-164b-58bf-8867-c6cb5e7af121 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
8a3d1bdb-9159-5dbd-aea9-7619d3191e3a | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
60d133f8-3ef0-50a2-9179-acecbf0cbeb6 | button | Vent lines are directed into a safe area. | Yes,N/A
d050cc4f-30ba-5466-b4b8-df2714d53a47 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
7f312423-2e54-5722-97cc-15062feec468 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
daaa6797-cafb-5a0f-85ad-b402e355489f | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
d21240e8-c68e-5dae-bad1-45031304c583 | button | Instrument earthed in accordance with project specification. | Yes,N/A
2a3c1515-03df-5008-91cc-d1feedd102d0 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
ffebb209-372b-5459-8ce8-573575508c8e | checklist | ITR-CL-1-122 Instrument Calibration |  | ITR-CL-1-122 Instrument Calibration
d061d535-ea64-5fe6-81d5-c825708b16c6 | checkpoint-no-value | Required Data
41757319-167a-5cd8-aa07-c7199b9ba8d1 | textbox | Type and Size:
42e7d429-c339-5e32-90b0-dff5c5fa554d | textbox | Make and Model:
9525ed89-0474-5d44-8ff0-3f1f965963c5 | textbox | Serial No:
5f6e8c41-a08b-5394-94f3-dfaee7420291 | textbox | Instrument Type:
ef6e8d81-b952-543e-b989-618e5fc54fce | textbox | Instrument designation/equipment no
013ed506-2f7b-5333-b447-51c85cc51039 | textbox | Calibration interval
b514c3b3-3339-571b-bb05-9d42ed54d281 | textbox | Calibration method
92652948-f8e5-5c46-aac9-dc8673169287 | textbox | Calibrated at
a084b1a2-8688-51e4-824f-3472c8608254 | checkpoint | Instrument Power Supply
e3a84c82-da34-5d47-8dd7-17426f6e7f45 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
487fbee1-964d-5c75-8eaa-c3d60db995b2 | textbox | Supply value:
8d9f507d-31de-553a-8602-8f512697a4b5 | button | Calibration sheet completed and attached below | Yes,N/A
4c28aeec-b4cb-5c6b-b9e8-2300245cb34b | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
8bc3774e-d4dc-586c-a938-daea54489cc5 | checklist | ITR-CL-1-123 Instrument Pre-Commissioning |  | ITR-CL-1-123 Instrument Pre-Commissioning
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
897e9c39-89a6-5075-b9aa-fde697807612 | button | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface | Yes,N/A
47f1318b-307e-5a97-a5fe-c77d0c3a625d | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
a985c65a-ed7f-54f2-9666-2867917a834e | checkpoint | Analogue Input:
850f66cd-8570-4223-bca4-d6c8d4c8bd9e | checkpoint-no-value | Analogue Input:
378a8d55-eb5f-5b57-b324-9108a86e2635 | textbox | Input range & units:
62d06d33-8cad-5af8-ae02-814d936f92c9 | textbox | Indication range & units:
9e6d1123-a43a-5dcb-af67-05f749afcd30 | checkpoint-no-value | 0% Rising
6c3091b6-dc01-598f-a533-d3e2ab0b9468 | textbox | Input Signal:
ac589bf5-4f15-5503-aa6d-71bab343ea42 | textbox | Control Interface Indication:
fcfac1e9-ea11-5c67-948c-fe55efe6425c | checkpoint-no-value | 25% Rising
e8415b3f-3ac1-50f6-914c-a30b2c89be64 | textbox | Input Signal:
7af91f29-8b47-5538-877f-01c0ce9d0f7b | textbox | Control Interface Indication:
9ecae5c3-f2b8-50c2-9b5f-723437759c7f | checkpoint-no-value | 50% Rising
b3dfbaad-7d56-5932-8ccf-19733cf462cd | textbox | Input Signal:
235fb3ca-b4c1-571b-8dab-a2b4ef0dcafc | textbox | Control Interface Indication:
29c9954d-e249-5bc1-9560-fbb01a69bbec | checkpoint-no-value | 75% Rising
abc5d65e-8e20-5c2e-b704-d6bc0a5f2e67 | textbox | Input Signal:
a230595e-ee97-53ee-8ac5-45f9654d7297 | textbox | Control Interface Indication:
ac15c64f-eee2-5f7e-ab91-e63b2c5857de | checkpoint-no-value | 100% Peak
e961078d-a3f4-5808-bd61-5427a76bb78b | textbox | Input Signal:
6c5546a6-4215-59b3-a07e-f36021f29bcb | textbox | Control Interface Indication:
88444607-51fe-5cec-a192-b792e4061f64 | checkpoint-no-value | 75% Falling
b3deb643-40c6-5199-9484-e024b9980ae4 | textbox | Input Signal:
4863c711-1488-5deb-a5b3-2c60e9183372 | textbox | Control Interface Indication:
835f9c0a-db31-5f17-9338-7e6e972233c7 | checkpoint-no-value | 50% Falling
98a2b6df-5603-5b93-9a8a-48c41df189b2 | textbox | Input Signal:
fc09dfe3-c9a3-523c-89ac-a6e00319a87d | textbox | Control Interface Indication:
7d146d2d-713d-54cf-8b13-ec9f009430a6 | checkpoint-no-value | 25% Falling
014656fd-4bef-53ad-ade6-bf4f401a9cbf | textbox | Input Signal:
b65a9234-d2a4-5ce8-96bc-3cd215943c6a | textbox | Control Interface Indication:
0ac731dc-a181-58a4-861f-0bb6758b3d16 | checkpoint-no-value | 0% Falling
a99fedbf-ba52-53a7-b23b-51f8c31c2f5b | textbox | Input Signal:
9df90556-69b2-53bc-b89c-6537f4f59540 | textbox | Control Interface Indication:
1ed325df-44c7-55d1-9f72-c6a25205dbcf | checkpoint | Digital Input/Analogue Alarm Trip Points
42de2ed8-1938-53b2-b3db-e7a83f0bda82 | checkpoint-no-value | Alarm Lo:
962425e6-dcc3-5b54-9225-40b97d1fc357 | textbox | Alarm setting
08f42cc8-e309-5ef5-9e0f-82d963771251 | textbox | Measured Alarm Point
aebb232e-e92e-5ca4-b6ec-b9f513b43530 | textbox | Filter/Time Delay
52d9be6f-a683-52ed-a0ec-d858870ce05f | textbox | Result
60ad5ba8-5e46-5008-886d-8d142348550c | checkpoint-no-value | Alarm Lo-Lo:
a1abf795-19f3-5a51-8298-ac0238d21741 | textbox | Alarm setting
fd85b330-89f1-55eb-860d-701a06f98bd2 | textbox | Measured Alarm Point
a118d913-ab14-5f51-96db-e8d2833c9ee3 | textbox | Filter/Time Delay
1ab1dc99-d556-555b-b45b-e3abd75ff08f | textbox | Result
a1e8fb6c-7d43-5228-93d0-750be74f1f5a | checkpoint-no-value | Alarm Hi:
d85a7b2b-4c84-5a58-aeac-f60b7a795eae | textbox | Alarm setting
84a67f05-f22e-5bca-8d4d-91fb178fdc1d | textbox | Measured Alarm Point
60d46a44-257f-5dac-9985-54bb773aae1f | textbox | Filter/Time Delay
c9fd08ad-30c3-5610-8e1b-2cb691acee86 | textbox | Result
a83cc59e-3e67-551a-8cb8-e7450169cc26 | checkpoint-no-value | Alarm Hi-Hi:
8698d97d-6c93-53e2-a922-f98558c5c64b | textbox | Alarm setting
27d38d77-62a4-5bcd-a195-02d0467b1ce4 | textbox | Measured Alarm Point
20462948-5499-5de0-b84e-83595ed54bf2 | textbox | Filter/Time Delay
36f57217-6430-5d43-884a-41842a0a23e9 | textbox | Result
66aabf17-dff8-5b2d-9eec-dc7c136d5509 | checkpoint-no-value | Control loop set points correct:
2a301152-a39d-59d5-becf-713d8ab86590 | textbox | Set Point 1:
5602cd0c-76fd-54b1-8d63-7518b1e2cfa4 | textbox | Set Point 2:
82912c49-655e-5895-9ec0-1823330525b3 | textbox | Set Point 3:
936ef3ac-8cea-5e81-a069-e7683e2e71f0 | textbox | Set Point 4:
29cf032d-63bf-5627-8282-9da087e897bf | checkpoint | Startup, Shutdown and Override functions
140999e7-21db-5d8f-8c3e-64acb045e0a7 | button | Control system graphic display | Yes,N/A
f92b149f-fe16-55fc-8508-4cedcd34d717 | button | Control system point display | Yes,N/A
51d22c96-e685-5d6f-a000-240b788b14d0 | button | ESD graphic display | Yes,N/A
c2dccac6-6065-55ee-821e-cfe8f4cda715 | button | Alarm Recording and Text | Yes,N/A
4a998987-8120-5498-b98d-bdc0f10f4da8 | checkpoint | Additional checks
7b1d1578-812d-51d2-8657-7f08d153646e | button | Control system display and alarms are correct as per control functions | Yes,N/A
a813ba46-f34e-5288-80be-4b607bb1c24b | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
ec7ef43b-b63a-51cb-8c64-8940affd60dd | button | Switch action verified, including power loss | Yes,N/A
895842f3-ac96-5241-b3ef-bb893805d6df | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
19513ac1-0858-54b3-8f99-b38a549be2fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
c515ca60-95bf-54b5-82d4-84a2ff73a660 | checklist | ITR-CL-1-124 Commissioning Instruments |  | ITR-CL-1-124 Commissioning Instruments
d061d535-ea64-5fe6-81d5-c825708b16c6 | checkpoint | Required Data
7d782c52-bbaa-504f-a90d-8788404f7508 | textbox | Instrument range:
759396e7-a65e-5b5d-bfde-afdd21fdd322 | button | Installation complete | Yes,N/A
32fdef0f-346b-52b6-b9dd-bcc8b2ea83d9 | button | Point-to-point | Yes,N/A
1d10c968-6216-5936-8f24-5d70acc19c2b | button | Haz. Inspected | Yes,N/A
ddb0305c-1859-54dc-99f4-287a62ae8a8a | button | Tag correct | Yes,N/A
2b8bbdd7-9ffc-5fad-809f-29d35a4b5514 | button | Hook-up correct | Yes,N/A
722314e4-0baf-5c5e-89a3-942255c8940f | checkpoint | Alarms & Set points
7b922954-94ff-517c-bc1c-5b267e18a853 | checkpoint-no-value | Alarm Lo
39ed4655-2862-588c-a3b1-153d512e527e | textbox | Activated:
209e76cf-9d08-579d-bddd-4ac0865c8a8f | checkpoint-no-value | Alarm Lo-Lo
651f931f-b1a4-5b08-a49d-c2cb17ce66f5 | textbox | Activated:
0e4fcb7b-fece-565a-8d4c-cce4b8905bf6 | checkpoint-no-value | Alarm Hi
74d6c4a9-b6b2-5e02-b52c-839395a706c7 | textbox | Activated:
6bf74d78-37d3-5492-82ce-337fde21a23e | checkpoint-no-value | Alarm Hi-Hi
be9d0b2e-14c9-5375-8f6a-e84a29a6505d | textbox | Activated:
10bd4618-eefc-5c44-8115-50d1b98dae65 | checkpoint-no-value | Set Point 1
be81ac26-8dcc-5ac5-8b01-d8277febae29 | textbox | Activated:
332eaf77-70b6-59b3-ae63-8b9da1ab368a | checkpoint-no-value | Set Point 2
cd52fb7d-5e3b-5a43-b82c-5acecbdba150 | textbox | Activated:
c317bac7-22a2-55aa-a7ca-ec364f340b8f | checkpoint-no-value | Set Point 3
20dcee58-d50d-5e32-b540-749665832549 | textbox | Activated:
31056f22-f138-57d2-aa0f-0e4d2f9ef078 | checkpoint-no-value | Set Point 4
957a2329-e4e4-5280-b20f-203083a54a14 | textbox | Activated:
075b6472-07b1-5c7f-813d-cd6eb5eafea3 | checkpoint | Calibration settings
408edc55-83c2-5e4f-82e9-1175ffc54db0 | textbox | Zero
56d1d0ef-0eab-5bdf-bba7-5a3960989452 | textbox | Range
e0e4a04e-ff82-5a4a-a5bd-6b458db51718 | textbox | Other (Specify)
f29fef1b-2a7d-5f18-8a8d-81d046c28d9c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1242d43c-fa3d-5dce-b762-f7be1a1de523 | checklist | ITR-CL-1-125 Cone and Thread Tubing Installation |  | ITR-CL-1-125 Cone and Thread Tubing Installation
0959a2d8-a8b6-5a53-a6c5-1b35e12647be | checkpoint-no-value | General Data
7141cf95-5dea-5b0f-8d8c-81f196d5a59d | textbox | Location:
255cbc42-9802-516c-a136-c042f69c7857 | textbox | Duty:
6887b83d-bc70-53e8-b553-80544ea43fe2 | textbox | Reference Drawings/Hook-up drawing:
f71a1a13-44f7-556b-996b-2b1398f630d8 | textbox | Related instrument tag no:
3b8c7d90-5404-50c9-9cb5-ff74c7cc5ca7 | textbox | Tube diameter and wall thickness:
7904017c-f83b-5cbf-bbee-0b2b1547e5a9 | checkpoint | Cone and Thread installation - Stainless fittings
d43e5bc0-c8bb-5532-b2df-b69f7cceeaed | button | Correct thread compatibility and engagement | Yes,N/A
39be5582-98e9-5b64-bf35-b56df54e22ac | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
11c86109-300b-5d46-bd80-5b4e8b2204b7 | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
6b9ea312-508f-5804-ace3-ed7b548bba4b | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
920b9894-e0d8-5af6-80e5-a90c1b5d34f1 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
418c3109-140f-5b00-ba6d-c39a3593e4b4 | checkpoint | Cone machined face. No defects, lines, bumps etc. (MANDATORY PHOTO)
2f419ae7-c5f8-5b75-9102-aadd65f3b4ee | note | Attach photo of cone and thread.
c671b1f1-0075-575a-a232-168cde2fc86f | checkpoint | Thread cleanly cut, de-burred and cleaned. (MANDATORY PHOTO)
6b9e5d58-35a2-5767-8ee8-64320309ab65 | note | Attach photo of collar.
33b6b064-7fb6-5c17-a57d-ab015a8f638f | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
675acade-cf00-58b2-be9e-8c885504bf48 | button | Correct Tube nut used for the right sized tube | Yes,N/A
6390f66d-ee7b-532c-a0cc-ae3ab696094e | note | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
7bcc3afc-9160-54a2-9b81-be483b83d27a | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
f354ef76-4789-5085-ad39-925286a57219 | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
dfb2e174-954a-5a61-b637-6609eb938380 | button | In service leak test performed and passed | Yes,N/A
1126d282-7850-5605-aa0d-367ec4066b64 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
ce82cdf0-99c5-552a-9572-eb505115723c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
accaa90b-ea40-58ee-ab7f-1eb4fc813ead | checklist | ITR-CL-1-126 Cone and Thread Pressure Testing |  | ITR-CL-1-126 Cone and Thread Pressure Testing
0959a2d8-a8b6-5a53-a6c5-1b35e12647be | checkpoint-no-value | General Data
9bdca364-c6e4-5032-9956-643da41dda63 | textbox | Location:
96a72ebf-1e66-59ad-b053-72910f7c9442 | textbox | Duty:
cbf08a12-f724-5e20-8708-9376e9c32c97 | textbox | Reference Drawings:
3ffd6b5a-1297-55c2-a17b-d946fdedbca2 | textbox | Hook-up drawing:
41943411-c78c-5e38-929d-e23a499f8658 | textbox | Related instrument tag no:
b53090f0-055e-57a8-bd2f-8e79b7d37312 | textbox | Tube diameter and wall thickness:
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
4cddb07c-c76a-539b-baf0-14863ebb25b4 | button | Tubing orientation as per hook up drawing. | Yes,N/A
623dbe2f-d69c-5ccb-93e7-44635f6c4d19 | button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
fb1b199d-5938-5a8b-a26f-b0107005353d | button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
f23cd556-ae2c-55d3-abac-643c35a70465 | button | Tube as per specification and hook up drawings. | Yes,N/A
76a67493-fab4-57c4-9a27-a6abb7748fc3 | textbox | Max design pressure:
6cc939ae-1c2d-5e20-b4e3-1b666eb3cda5 | textbox | Test medium used:
1c71bf2f-6b10-5fb9-aa9b-c87225790e6f | textbox | Record Testing pressure:
3661e20b-d462-54c0-9f7e-9f01d240b545 | textbox | Test pressure duration: |  |  |  | Minutes
df8aaede-7e79-54e6-9f6e-53339dd0db91 | textbox | Test leak rate: |  |  |  | Litres/minute
b50cedcc-0f97-5536-b30e-e74667a73118 | button | Chart recorder used and attached (where applicable). | Yes,N/A
7ad8258c-4c5a-5f9f-b969-c11763f0a080 | button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
b4354c34-3058-51b6-bf55-9a43cc123035 | button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
2a69bb8b-cafe-5fb6-a250-a5c95445879f | button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
9ec7e675-e0a2-55ea-aa72-182664bc922d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
866c6d15-65d8-50c6-b60e-3a3783574536 | checklist | ITR-CL-1-127 Telecommunications Equipment Panel |  | ITR-CL-1-127 Telecommunications Equipment Panel
b734ea26-8173-5b2a-9ba2-f4a76d9c2596 | checkpoint | Telecommunications Equipment Panel
484f6359-9b8f-514e-ba92-38eb94aff49f | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
19e9f9b1-d7c3-5daf-b1f0-fb51ee88b1b4 | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
12f8ffc5-c8e6-55f5-9522-76a209bd3e60 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
936ffdf6-019d-527d-99ec-4e8a7ea64003 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
012a506c-b61a-55c4-8ea9-fa509bbb8ecf | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
849f4624-9b10-50af-b750-6f5365a1266e | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
27341d97-8db3-512a-8b5e-bfa4629b0fc5 | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
512848cc-59c8-57dd-9043-e46615bf02fa | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
8c99f84b-0bbb-5acc-bb39-35d6e62b3517 | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
ceb55166-fde4-5dbd-97cf-f2ddde176c60 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
27bd8155-5aaf-5348-b08b-d3d172ebdbcd | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
9e4c60d9-10b1-5af2-8aaf-48920f19ce54 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
def6d813-ea1c-5313-b111-fc49eecac804 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
815a165e-dbd6-5cc1-bfea-cc2299917df6 | checklist | ITR-CL-1-128 Temperature Instrument Installation |  | ITR-CL-1-128 Temperature Instrument Installation
5a8339ca-f486-54f5-95fb-e84dfef1da9c | checkpoint | Temperature Instrument Installation
40121701-d5a4-5d7b-8ca5-f5bcf7e868c1 | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
435b3ada-fb4a-5318-b7d8-e7f8b08d1b33 | button | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
1191fafb-f55a-5e82-a46c-1a722f57b6c7 | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
bf1a36c6-83ba-51b3-b211-e2e6b22ce900 | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
804640f3-5ffc-5ca7-b188-b5a50885a2e0 | button | Internal depth of thermowell checked and recorded | Yes,N/A
7763a5c3-ed16-5a59-85c6-62931a0298ae | textbox | Depth:
f4cf64b4-ecb3-598b-aa05-16a76c52e56e | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
94922c1b-4642-512e-bc43-8cbae749d22c | button | Thermowell CE marked | YES,NO
726fe10c-739c-5d4b-a353-c91634bbd281 | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
cd94768a-6a61-5a85-8c74-80e37f6052bf | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
aff5e9b0-f0bb-5825-bce5-8ff6cec3eb69 | checklist | ITR-CL-1-129 Flow Meter Installation |  | ITR-CL-1-129 Flow Meter Installation
455173c9-ff6a-5288-b65b-4c5fc763b7c9 | checkpoint | Flow Meter Installation
79d399e8-6bf1-5cf5-8726-622bba11e82f | button | Check instrument nameplate details are correct in accordance with the instrument index | Yes,N/A
cda7b0d1-4555-5c62-b89f-a442ee69f159 | button | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
ff13f8b1-514d-5390-8877-9a74428cc7b7 | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
6235fc3d-b0ef-5cc5-b169-4aef086a088a | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
6ac08eff-e464-5c4f-b8ad-bcbcac0b0234 | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
a3eb006e-3fed-5fd6-a7bd-7667a3be5301 | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
d1c16033-5856-5923-b04f-9286452fea9b | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
d9e10f5b-05b1-52b1-a51e-e01317f8a08b | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
cf3283ce-ca96-5de1-a013-6b55da6c109b | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
4a5d8526-d718-5e6d-a2ba-d4025509da1a | checklist | ITR-CL-1-130 Pressure Instrument Installation |  | ITR-CL-1-130 Pressure Instrument Installation
6543ef08-8703-5786-8c08-ea5e55da06ba | checkpoint | Pressure Instrument Installation
3551c246-6b6b-5e9e-b168-09e9da476d8c | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
9bac761e-4fd1-59f5-a25c-77efd674b87a | button | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
1a2f2ebd-21bf-59d5-93f8-de0becef9f63 | button | Instrument mounted as per hook-up drawings | Yes,N/A
0207d236-be36-57d4-a64d-492b83b4ce92 | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
ed2879d7-7bdc-55ba-88c1-b177386890a1 | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
6ce27fe2-de24-57b7-b477-4fd4ddbb6236 | button | Correct bolt size and material/grade used | Yes,N/A
87d4819e-9699-57b5-a505-c6ba0a9c6515 | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
95901383-a398-57fe-917c-498e0f9b050f | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
32276249-0f52-5741-863f-5d512f6e0457 | button | Isolation valve installed | Yes,N/A
1a781a60-bb87-565c-9929-787928f070a9 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
ee31de9e-4a23-50fa-9d7a-741ec55c02b8 | checklist | ITR-CL-1-131 Level Instrument Installation |  | ITR-CL-1-131 Level Instrument Installation
76879399-6f0a-53e6-a86a-76af925a85df | checkpoint | Level Instrument Installation
cb30df0e-b480-5026-8139-809f2feb861e | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
a3c4b616-52ed-524a-a54c-5a33cf1c7e6d | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
be629b31-5e80-55b1-8d2e-e063834710b6 | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
5e6da57c-3caf-50b2-9afd-49e3456a6a9a | button | Bolts and studs are to site specification | Yes,N/A
9af8105c-9d64-58c2-ae6f-c6aa3c928578 | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
0363c507-fc6b-5a10-9f56-544a45013556 | button | Ensure gasket and studs are used as per specifications | Yes,N/A
8b14497a-acf8-579b-b824-7b51bb902980 | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
a760aff2-422b-5236-81f7-a9621af1693e | button | Verify antenna/source are installed correctly | Yes,N/A
734d1561-7cff-5d9e-add6-f610b703003e | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
29b45421-dea1-525b-8648-a82b6ae57429 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1c54a465-cc50-55d1-a7ca-8a0b872e7469 | checklist | ITR-CL-1-132 - Instrument/Control Cables |  | ITR-CL-1-132 - Instrument/Control Cables
43c7b5f3-337f-5425-8176-89305ffc0c21 | checkpoint | Instrument Cable
75deae0c-8214-566e-a6cd-4514849c1069 | tickbox | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
14994549-f4a3-5430-93cb-89cc0e9db4db | tickbox | Check dressing / cleating, cable undamaged
ece2796f-aee9-5c81-ba47-8dd04b8bd289 | tickbox | Cable mechanically protected
439029a7-4320-5538-8d56-f06ab2239de9 | tickbox | Cable terminated with correct lugs and crimped with the correct die.
414385c1-2b44-5fe3-8774-9f8d725dd069 | tickbox | Screen correctly made off
12f1e79b-0574-50c7-8808-2c4f3849c703 | tickbox | Glanding / Locknuts correctly installed.
db41e706-3bee-5a39-b705-e8998c49fb8d | textbox | Gland type - from: |  |  | Haz. Area Rating
10aa8414-45c4-509b-8e17-031bd9e1679d | textbox | Haz. Area Cert Details.
265346b5-b21b-5492-ac2a-264dff32e381 | textbox | Gland type - to: |  |  | Haz. Area Rating
69e039ca-0eeb-59fa-b7af-dadd4efaf624 | textbox | Haz. Area Cert Details.
a8f71738-adf4-5f1c-8a9a-d0b3d1c6ec6f | tickbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
132e99c5-0646-5123-916a-d4bb9e2cc252 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0c5fb84d-f269-5543-8ae1-fd241e38c3be | checklist | JHA - Job Hazard Analysis |  | JHA - Job Hazard Analysis
1dd72c41-b476-54ec-8ebf-cab6567b715b | section | Job details
90129915-30b8-43d2-9129-df0debe8950a | checkpoint-no-value | Job details
9121b653-9465-5c94-8e98-616d3720b083 | date | Date:
2296b6cd-d4f1-5691-8da3-a529becb34bf | textbox | Permit No.
8c3c490d-c825-5522-bdbc-0b806270bda3 | textbox | Job No.
b79ea938-c5ce-52f8-af36-c62c2f65c8e3 | textbox | Site
e10cb77a-6c27-5a76-995b-93e170d648e0 | textbox | Activity Location
72676fca-63ab-5aef-bc4e-64505c74da15 | textbox | Asset:
2f2b1683-9a8b-5c8a-84d5-4dade0dd5aa0 | textbox | Work Details:
d0e2da1e-7bc7-5faf-bd9c-add02d8a5915 | section | Prompts for Hazards - Mark all that apply.
9c216722-725f-4ef3-902b-5c25d774b48c | checkpoint-no-value | Prompts for Hazards - Mark all that apply.
e2e74f39-287a-52bd-8eca-eb140dc9cf2a | tickbox | Sparks/Open flame
2acfc571-e5a6-505c-ac2b-eba8970a62d4 | tickbox | Disabled safety device(s)
65f6238a-90cd-56f6-ad6b-0554edd0bd36 | tickbox | Uneven surfaces
f9e713ed-53fd-5dc5-929f-d6ff97eeecf0 | tickbox | Fatigue, over-exertion
24e995ec-3dd7-569e-b330-0578c5373bae | tickbox | Crane movements
01452f54-e4bd-5c7e-8ec0-ffa875e8501a | tickbox | Moving/Rotating parts
1f7273b3-8cb8-5054-9bbf-90013ef12dfc | tickbox | Remote area, working alone
1e00237e-3a56-527c-95bd-1af4f5c47fa6 | tickbox | Conflicting work/SIMOPS
48550d8d-c109-5c4c-9a7d-ed410eba740f | tickbox | Electrical arc flash
d3c0a2b4-04b7-5bc6-aef3-4ca1c2480940 | tickbox | Sharp objects/materials
f9d836e2-dc1e-51ae-a045-3e021201afe1 | tickbox | Restricted/Difficult Entry/Exit
f0c52d3f-bfd4-53c0-92dd-c40489c22c79 | tickbox | Overhead obstacles
7c761f22-d173-52dc-8223-bd1285cc4716 | tickbox | Ignition sources (other)
3272747d-9450-5da3-a2ac-faa787d2363f | tickbox | Access/Egress
866f2e8c-c205-5d58-8086-23ecb0668fb0 | tickbox | Water body
d3e0555a-b9f4-5c0c-b061-e01105e6b7d3 | tickbox | Live equipment
24ac8cbf-ef66-53d5-a5ce-8bcbf39c061d | tickbox | Slippery surfaces
a3b30d7b-ec59-58ca-9313-26d2c562f387 | tickbox | Suspended loads
98b1bf54-a699-528e-821a-322c9c2430da | tickbox | Hazardous substances (chemicals)
22f019ba-6ada-5889-82f6-57f72a23a014 | tickbox | Use of non-intrinsically safe equipment
e3dc92c4-6d8c-5806-9d79-ba9d7375189c | tickbox | Weather extremes
317ef129-b4f2-5978-a01b-dd9b3f7ee83c | tickbox | Moving vehicles
789348a6-324b-5e45-98b9-5df2ad640f56 | tickbox | Task related noise
d4e3a79f-63f6-53ac-a71f-8f3f6f7034a1 | tickbox | Engulfment
f77e1ae9-20bd-5d76-b6fe-db40018c1738 | tickbox | General waste
bfa762a9-8535-532c-9647-bd72e4369d72 | tickbox | Hazardous waste
3f775ada-8d29-5732-8d34-4393bf241882 | tickbox | Hazardous/toxic substance, fumes, gas
6d0bf608-f379-595e-bf82-0b824ac63501 | tickbox | Flammable materials - Gas, liquids, solids
34bd77ea-7899-5601-b0fd-d9b499ba4ac3 | tickbox | Reduced visibility, lighting
fb4bb6db-ab81-5c66-b884-cb3f83b3f055 | tickbox | Electricity
3c73deb5-614d-59df-aa2a-6bc6c5952c80 | tickbox | Static electricity
337fec5f-a0d8-5f8b-bec4-6af9d689ac55 | tickbox | Work at height
317be1f2-c61e-5d51-9f28-b1926070f1fa | tickbox | Underground services
14ec678d-6ee2-5bda-a8e5-9a125d230adf | tickbox | O2 Deficiency/Excess
8303cc09-1e9a-5772-836c-820f27c974f5 | tickbox | Temperature extremes
82a98376-7688-5830-87bd-11ec437ec37c | tickbox | Heavy objects
39972442-f325-5a1d-93e7-200899637b63 | tickbox | Radiation
4f4b68b1-b454-55a0-a219-1a2333da1520 | tickbox | Potential energy - Tension/Compression
ff1407f6-56d7-5d5f-b604-0a466c33788b | tickbox | Flying particles/Dust/Objects
35a7f122-ad6a-5594-9946-aba2eb678cba | tickbox | Vehicle entry
5c89e163-bce5-5049-b6a2-5e1ebad30bfb | tickbox | Exposure to process temperatures.
bb7578a2-4875-54de-afed-194a7e08db79 | section | Prompts for Initial Consequences - Mark all that apply
75e38327-3706-4cf9-84cd-7bdab2981357 | checkpoint-no-value | Prompts for Initial Consequences - Mark all that apply
00f19fe5-1ad2-53fd-8229-8c082a6bd8bc | tickbox | Falling/Dropped objects
c7c51e4d-394e-5bb3-9043-2690d397d2d1 | tickbox | Fall from height
5fc58abf-df57-5cdf-b4fc-b936b095b1b1 | tickbox | Trip/Slip/Fall
963fbd82-7281-5cb7-b204-586311d1a02c | tickbox | Gas release
35caaac2-10b3-53bb-9464-4f613176c840 | tickbox | Pressure release
a8380d82-74a4-5f0f-8446-51917018e112 | tickbox | Struck by object
8b925c2b-16c6-5bff-a427-8a4f2cce1558 | tickbox | Exceeding tool limits
855f5e64-7af0-51fe-8436-0fda03120d74 | tickbox | Overloading people
51b43355-9c5f-57c3-8d84-1d991669a3d4 | tickbox | Unplanned shutdown
1c3f2082-961c-5c6d-b286-218a65f1a12d | tickbox | Exposure to O2 deficiency/excess
742ffc11-e2e1-556f-9da6-d85cdf6ab0c9 | tickbox | Exposure to hazardous substance
3c76c8a8-0ec2-58d3-b890-4b9f9c07f07c | tickbox | Entanglement
17cab252-ff5d-5afc-8c9f-0291ff00b395 | tickbox | Flying objects
545a0a83-f1ae-53ae-a51d-3559eee6d18e | tickbox | Loss of control
7c4c484c-cef0-50f7-9fdc-d2c237b59e35 | tickbox | Loss of containment
38e73858-15e2-530f-b6cb-687a3a5228b5 | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
a479994e-91eb-527b-8b30-780190b19085 | tickbox | Loss of structural integrity
07de0b49-6421-52ef-8c3e-90e955f5e47b | tickbox | Equipment failure
e42f97da-349e-5e21-a5f3-f9b5b4e59e24 | tickbox | Uncontrolled ignition source
3d7150c4-b075-5b3b-a8a5-2b2b91b8d6a9 | tickbox | Collision
b7287a6e-9b8a-5347-bfc7-686ff353c681 | tickbox | Ignition/Fire
c1e99fe1-fa68-5556-bb36-7462c665d8b8 | tickbox | Back strain/Injury
febb8172-fed9-5553-9762-1ed383864782 | tickbox | Burns
65f86853-2b43-501a-81fa-10802d729290 | tickbox | Heat exhaustion
7f2d7094-e12d-5779-8909-10e99c0c3200 | section | Initial controls - Mark all that apply.
64d5901f-79af-44b5-b2df-5ba274e0fd84 | checkpoint-no-value | Initial controls - Mark all that apply.
0531576a-0e0d-5e0a-9822-c90127d2c91f | note | People controls
cdb87cd9-aa83-552e-9f27-192ad19e29f1 | tickbox | Safety/Fire watch person
c7ce9b43-64e2-5a9c-8866-82a154afcba6 | tickbox | Barriers/Flagging
dcf6bb7e-a5f9-52f0-a099-4bfb78439724 | tickbox | Warning signs
bc6fc587-4cd7-57aa-8aac-b1885ff5d667 | note | Equipment controls
92675b30-30a9-58e0-af6a-1b04a7c62402 | tickbox | Master tags and locks
5ae218e2-4b86-5e4c-a9cc-6344228e94da | tickbox | Scaffolding for access
d3d8dc3e-2571-5fed-b558-c2a29d1d7824 | tickbox | Radio communication
56c8c170-dbe5-5304-a387-0e1d58901816 | note | Environmental controls
d74792dd-5e8d-54f1-8718-88bf002c7d28 | tickbox | Ventilation
08c2a88f-3143-553f-ba43-3884c222ed1c | tickbox | Lighting
15c09d2b-546f-5b76-a853-2b27f4dcf21a | tickbox | Gas Testing
24f619a7-6d34-5444-b150-524826812edb | note | High risk controls
17426f23-9ba6-535d-a26c-8d86191f6e73 | tickbox | WSCS Work permit
00147651-933a-5dad-83fd-9df182bf01de | tickbox | WSCS Certificates
b26db9bb-a7f2-55cd-9f17-ca969ff48d9b | tickbox | Critical lift/Fall protection plan
8d1fd861-b1cb-5271-acd4-f4cfd50bb495 | tickbox | Specialised PPE
2142844c-3e51-58fa-a1a1-06005b55fd4f | tickbox | Spill kit
35ee2540-5d3d-5bc6-abb6-1a93433e919f | tickbox | Fire extinguisher
0ea35b14-b47f-58c4-9129-58c1a83117dc | section | Signatures
66af9c5a-1f5f-4ddc-8e06-22ea9b5a07f8 | checkpoint-no-value | Signatures
08dd81cd-932b-58b2-9b84-2913f2f6f46a | signoff | Applicant signature
e9a3b389-05b5-5eee-9c5d-e3b61b2d14d1 | checklist | JHA - Job Step |  | JHA - Job Step
e62f412e-efbd-50c2-b348-57fee9e5a033 | section | Task Step - add task step for each individual task
00780faa-d665-40b2-87ab-6cadb24cd40f | checkpoint-no-value | Task Step - add task step for each individual task
26e2895e-46dc-55d8-91aa-d34462d3219f | date | Date:
edc2c497-a45f-5063-8c12-87586ccbfeb2 | textbox | Task step number (eg. Step 1, Step 2 etc):
a12b90eb-71dc-5936-b414-a3b4762a0526 | textbox | Task details:
90373697-09a2-52da-9093-db43db06e3e5 | textbox | Hazards:
f9753613-aa62-5d16-ba34-191186a9832b | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
578f357f-fae0-515e-99b1-60042e5723d9 | textbox | Potential consequence:
be7dc2f6-39bf-5087-a981-031a48ffe06d | textbox | Controls:
d61174a1-6a04-5f2c-90e9-2d589f32cacf | textbox | Recovery steps:
38bcca95-c251-5bb8-8ce5-ce18bef184a7 | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
d574a822-a52d-5be0-b1b6-4aa45276d0ad | checklist | MSDS |  | MSDS
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
18f906b0-6744-555a-b652-e3773583a9dd | checkpoint | Please Upload MSDS Sheets
a9f20cf0-1241-5cbf-948e-19817bd6c7c4 | checklist | Record of Inspection (ROI) |  | Record of Inspection (ROI)
f8eb7881-7f3c-5872-b944-b0fa1e752a6b | checkpoint | Please upload Record of Inspection here when complete (ROI)
f105264a-6276-59b2-8673-abc19267a423 | checklist | Safe/Unsafe Observation Card |  | Safe/Unsafe Observation Card
111a524e-9e5b-5bca-9cbd-3549c888851d | section | Basic Details
355b34ca-ad4c-4e82-9b35-f533322eb808 | checkpoint | Basic Details
d602e59a-1a81-5f60-a7d6-2f827da33a73 | button | Safe or Unsafe observation? | SAFE,UNSAFE
cb033385-3086-53a0-bbac-3c20e33d057c | date | Date:
f49370b9-a829-5df1-9111-809ae08fe247 | textbox | Observers Name
d28cfffc-ddd4-5179-bcd9-5f78155c4826 | textbox | Site
96f36722-055e-5270-ad2d-69c7d78c54b4 | textbox | Task Observed
6aefe625-b4b3-55d7-a581-1a7b03689331 | section | Hazard Observation (select all that apply)
f1cf4dde-cdf0-495f-86b7-68a64ab39d2c | checkpoint | Hazard Observation (select all that apply)
17092683-2b10-5c80-8089-05b8947b07a7 | button | Mobile Equipment | YES,NO
7b7871e6-df54-557f-b017-58f42a9916cc | button | Hoisting & Lifting | YES,NO
fbdfbd64-b065-50c3-b73a-51c15673e56a | button | Dropped Objects | YES,NO
ae96e44c-d7d4-53ac-80bd-478435f9a4ce | button | PPE & Process | YES,NO
293008da-b8f7-5abd-be58-679497580893 | button | Pressurised equipment | YES,NO
057c83c4-04b1-554d-94b6-2faa2f064aa5 | button | Machinery & Tools | YES,NO
a4de9a3f-f26c-5ecd-9ef2-a0656e7698d4 | button | Electrical equipment | YES,NO
9e38850d-3fe1-571d-8d97-1c621613565c | button | Housekeeping | YES,NO
080c4ecc-937a-56fb-a4e0-3520ca024a33 | button | Person fall risk | YES,NO
75d1356e-4970-503d-8356-7e0ec8c43b6a | button | Manual handling | YES,NO
0c091747-fc77-5b1c-82c2-7840e1a97f4a | button | Exposure to process temperatures. | YES,NO
c2d1aff2-59c0-586f-bb05-7b9b11611ec1 | button | Confined space | YES,NO
48b40157-a891-5948-b3eb-9475aa0b0d1d | textbox | What I saw
45961bcc-530a-5d8f-919f-4a526f17c0fa | textbox | What I did
69046fb6-7bd8-5821-98a7-34e0bee56b6d | button | Is further action required? | YES,NO
f6ee80f1-5dc3-5f59-90e9-dd1c0fc30272 | checkpoint | Observation reported?
9e09ffc8-baf0-5b76-bf83-57ad64ebda26 | textbox | Reported to:
0e65806f-84ca-5b46-af40-22bafee761af | textbox | Other comments
9190d35e-62ad-549b-b4b3-68404b96641e | checklist | Test Equipment Details: |  | Test Equipment Details:
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint-no-value | Details
4a866a34-da33-5783-8eda-0803536fed2f | textbox | Make
d22df50f-1070-5906-b3c0-7c4dc5fe5ce4 | textbox | Model
ba416c92-406b-57d4-b40f-fbb09fe6ac82 | textbox | Serial No
6aecfb6a-a654-5cc3-8de7-e0850f9c3fd4 | textbox | Calibration Expiry Date
1bbd320a-0d22-5276-bc0e-2234c714606c | checklist | Toolbox Meeting |  | Toolbox Meeting
4bff8cf5-2f9b-5ff6-b60a-449bd8fb0518 | section | Toolbox meeting
b6514b73-7c79-4b26-966a-21a3871636ff | checkpoint-no-value | Toolbox meeting
da98d349-009c-5dbb-aded-33660590f394 | date | Date:
b0c2f5f3-8c74-5db3-ae82-57d532528533 | textbox | Meeting location:
1571e769-db4c-5060-be7a-4bdfe3bdaa39 | textbox | Meeting conducted by:
f08798a0-bb3a-5f99-bcdb-0c1b059e3de6 | textbox | Meeting attendees:
10be6db0-65fb-5ac7-a41d-09e750c341e4 | textbox | Today's work scope/Hazards
620957ff-5c29-5c5b-89f5-3b1f659122ee | textbox | Hazard controls:
8a582c41-2e7e-533d-a344-42036f914b8f | signoff | PICWS Signoff