## Checklist Templates
Id | Type | Name | Values | Prompting Name | Prefix | Postfix
ea080f51-cec9-5c5d-b21d-26fdf97c141d | checklist | As-Built Drawings |  | As-Built Drawings
634660bc-3569-518d-92ee-49a5ce864e21 | section | As-Built Drawings - attach scanned documents
f20dabd6-3341-47c6-b31f-f9204d894be1 | checkpoint-no-value | As-Built Drawings - attach scanned documents
97c91d10-8a66-5e83-90c0-ef3afede49b8 | textbox | Drawing no.
b98a8467-c01c-4fd3-9b2e-928e1f72fab5 | checklist | Cable Support |  | Cable Support
53c2b56a-fa06-4f65-8ecc-173eb4045a1d | section | Details
ee79aa13-104f-4560-ab22-68915cdd168b | checkpoint | Cable Support
70a79e10-8cfc-56e6-9ceb-f7573fd7b8d7 | button | Cable ladder installed | Yes,N/A
2c58026d-c692-4e56-a8db-59008f4ea91e | checkpoint | Photo of cable ladder
74c164ba-388d-5867-98f8-7c7aff4555c9 | button | Vertical UT-3 Uni tray installed where required to allow cable access into cabinets | Yes,N/A
6bb54593-39c4-4094-be6e-e715f9e00528 | checkpoint | Photo of tray
22a245c0-bd79-5553-a81d-f9e549286237 | button | Fibre/comms duct insatlled | Yes,N/A
cfa71d67-ca65-4963-86ad-69428c34b26d | checkpoint | Photo of fibre/comms duct
55d78570-7c6a-56f9-80eb-d3c14dee6944 | button | Fire wall penetrations go through fire sleeves | Yes,N/A
1fd360c9-a1e0-4c36-a723-f7a10e892b3b | checkpoint | Photo of fire wall penetrations
2c2eaef1-5262-480b-a1a0-c6f3dc9baa64 | signoff | Cable Supports checked by:
b0e579ae-f8b5-42c9-af2e-fdc6762e76dc | checkpoint | Client Representative
076f35ff-0f51-40f6-a75b-2e7d5c0ba97c | signoff | Client Representative:
e2043f2c-aaca-40d7-a11c-99cd6a075a00 | checklist | Cable Test Record |  | Cable Test Record
56b6b7e0-eebb-5754-9e92-822956f50a78 | checkpoint | Upload completed ITR scans
f63572f8-d299-540d-ac09-7e0ff4d9073f | checklist | Certificate of compliance (COC) |  | Certificate of compliance (COC)
243fd733-6bab-56a2-8d1e-76a3fcfcfa73 | checkpoint | Please upload Certificate of Compliance here when complete (COC)
068047d9-77cb-5167-b268-27c3f921fe95 | checklist | Earth Pegs |  | Earth Pegs
e09c6e50-b1da-5e01-bb4c-531f323d7d49 | checkpoint | Mold type identified
8d2a1b0a-b8f1-5a0b-92f8-c0daec33c794 | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
d384c165-bb4d-51f8-81fe-b5c3be9bcff6 | checkpoint | Cadweld Visual test
9ae17236-0bd9-5bc0-96c6-72e9587a7dfe | note | Please attach photo
d5e0224c-c769-5195-9893-dc42f0bfa967 | checkpoint | Cadweld Ductor test
642b96df-9734-5ef4-9531-417d49c3a50a | textbox | Result:
ed808718-9484-59f7-add4-506485bf45ae | note | Please attach photo
cc634f25-a1cd-56b6-a299-6eea07238588 | checkpoint | Continuity test [Peg to Earth Bar]
401dacd4-633d-5769-9b12-62217ab63f5d | textbox | Result:
2c999201-76ad-5aec-8637-77d246062826 | checkpoint | 3 Wire Earth test
b9baa9b0-974d-593f-aa66-43f8886f0563 | textbox | Result:
803b2e55-3d8f-55f2-a311-076921ef9cd6 | note | Pass if <1 ohm
3f2813eb-c332-42a2-8717-500aca98f4ae | checklist | Earthing |  | Earthing
5338dfa2-32db-42e3-bd64-3d57edaeedb3 | section | Details
f4714f95-0730-4cc8-a7ca-231961d65274 | checkpoint | Earthing
9a527d7b-c8a1-595b-bfc3-924c18d54247 | button | 50mmx10mm copper earth bar installed on cable ladder as per design | Yes,N/A
d1689637-4e2f-4a66-bbe2-bab0058eba98 | checkpoint | Photo of copper bar
13134ea6-7da5-5ca2-93e7-5a64365204d3 | button | All cubicles connected to earth bar using 35mm2 Cu earth bond | Yes,N/A
1a799457-e493-4079-892c-022523b8bca8 | checkpoint | Photo of cubicles connected to earth bar
01e479f8-7b46-590f-b32e-366dd715ed91 | button | All doors have flat tinned copper braid earth straps fitted | Yes,N/A
d0804fb2-e38b-4cf3-b87b-1fcfd0e85f0e | checkpoint | Photo of doors with copper braid
558e12fd-6536-5b0f-a684-109ad22a37cf | button | Earth bar penetrates floor | Yes,N/A
7cae3ef1-8225-4ad8-991b-22d036d12a2b | checkpoint | Photo of earth bar
097b597e-73b2-5907-95db-408cc900b85f | button | As-Built drawings completed and signed off | Yes,N/A
51a1b86a-f076-4f3b-8f7d-44fcffb3297f | signoff | Earthing checked by:
374cb6a2-9614-4dd7-a818-a667cdc00c66 | checkpoint | Client Representative
0fba1206-a4d6-4475-8fce-03e229539019 | signoff | Client Representative:
558a40db-769f-5169-86dc-c96239caf2f6 | checklist | Entec Daily Report |  | Entec Daily Report
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
da5f9580-4940-576b-8192-1c0607d69a45 | checkpoint | Daily Report
56c74d02-2feb-5793-b9b6-1d52c994a8f6 | date | Date:
857a0e69-b296-5371-b5fb-4fa741ad2ea6 | textbox | Site:
658fedb9-dfce-5a7f-97b3-e07cfd381bea | textbox | Work completed:
b275ad11-385a-5887-957c-c661c3c5901e | textbox | Issues:
19fbd79d-4e0d-57e8-ad1d-75d6c069af21 | textbox | Weather:
d7a1c016-ea44-5de1-96dc-5603c9a96894 | textbox | Labour:
70900bee-f8a7-56e8-8315-77529c7db7df | textbox | Plant & Equipment used:
2ec8f9c2-4c85-5ed5-892a-88c437f42fb6 | signoff | Signed/Approved:
db7e5f84-2b48-4d7c-b02f-1aa110d70ca4 | checklist | Floor, Duct Penetrations and Vents |  | Floor, Duct Penetrations and Vents
9716e17c-20f7-4fa2-a6b9-b674bacef8bd | section | Details
4e7d8e9a-e205-40fe-835e-61fc3318331c | checkpoint | Floor, Duct Penetrations and Vents
cb490e98-488f-51d0-983b-623e772a8641 | button | Floor cable penetrations arrangement as per latest drawings | Yes,N/A
d50b6fb6-3693-4ebf-a4bf-665aa28eab12 | checkpoint | Photo of floor cable penetrations
02a6add1-9a2a-5ba5-9653-d25ea5a20bae | button | Battery Cabinet Ventilations as per drawings | Yes,N/A
b73e38e6-fa02-44b5-897d-04d7c22b0f12 | checkpoint | Photo of battery cabinet ventilation points
ed67968e-7a8b-5c38-98de-058f2179c999 | button | Fresh air intake installed for the control room as per drawings. | Yes,N/A
38ad21f8-0714-46eb-914a-9e4711988f3d | checkpoint | Photo of fresh air intake
2a51b967-43a1-575a-8f0c-de5b746aa01d | button | Ventilation point for the switchroom insatlledas per drawings | Yes,N/A
39cdee16-1ecd-47c1-9e10-cfd08b4fd360 | checkpoint | Photo of ventilation point
4b38a92b-e39d-5a26-9b8a-97308a44bf49 | button | Switch board arc vent installed and located as per drawings | Yes,N/A
93980a07-00b5-4b5b-9231-54ff70e3262f | checkpoint | Photo of switchboard arc
6496da54-c658-52e4-8371-a3d9c493c3f0 | button | Warning signs installed | Yes,N/A
782fd929-4093-467a-a651-bbf0b0f93046 | checkpoint | Photo of warning signs
1e4fcdd2-f99d-5c3d-9473-64fc271c0833 | textbox | Deflection Check - (+/-) 1mm tolerance in any 1 metre radius & a tolerance of (+/-) 3mm over the length of the switchroom. Record results:
3ee32ddb-4bf5-5d2c-b468-61eab16d0d1f | button | As-Built drawings completed and signed off | Yes,N/A
ac06a600-9f63-42b6-9ec8-80cdc4c4e1a0 | signoff | Floor, Duct Penetrations checked by:
782af336-81b7-4037-b23e-1762bb76af37 | checkpoint | Client Representative
bc3eb374-5a12-4f46-bd87-f8dd2a9db741 | signoff | Client Representative:
7d4221d8-1d4c-4c24-af72-62442176a790 | checklist | Frame Construction |  | Frame Construction
bdb95a8d-1e8a-40c4-a84d-ef55e65841c3 | section | Details
9982d98d-4825-4fc2-9563-c83190f8b013 | checkpoint | Frame Construction
470f4b31-e60f-5bd4-8997-fd05eaf7095f | button | Baseplate layout as per drawing specififcation | Yes,N/A
beadfa6b-3cf8-4752-b6ff-ec0051e9e3be | checkpoint | Photo of Baseplate
fe5015d1-5617-50ae-9069-bcb55913c318 | button | Removeable Padeyes in place | Yes,N/A
d0fd1597-b561-4bbb-84b7-588a97dc56c6 | checkpoint | Photo of removeable padeyes
8652dbf8-c024-510d-815b-cef2f8968fd4 | button | Floor/room layout as per drawing | Yes,N/A
3e58d612-125a-49bc-ae31-9dc010a1d59c | checkpoint | Photo of floor/room layout
39e860fc-59f9-5315-8a1e-32090daea25a | button | Compressed cement board used | Yes,N/A
dd20a180-5b96-4d85-8420-61dc6ea11e6d | checkpoint | Photo of floor board
f99f2b6b-62f3-569e-93bc-e6c623ec9faf | button | Frame construction adhering to all general steel work notes as per latest drawings | Yes,N/A
204d86c9-1310-51a0-9883-1c05ea36958e | button | Baseplate is free from damage and paintwork is intact | Yes,N/A
81861317-d724-43dc-9d42-9679bc7085ba | checkpoint | Add QA pack from blast and paint
0964dd60-3952-4d4b-b3d8-e3e3015a1022 | checkpoint | Add QA pack from fabricators
82eb162a-b86d-5c6c-b7aa-77ff58685277 | button | As-Built drawings completed and signed off | Yes,N/A
852922d4-34ac-4d97-a22e-8aa7d5853dfa | signoff | Frame Construction checked by:
652feca5-901e-4c67-95cd-8f60edbb28cb | checkpoint | Client Representative
413a17a2-543b-451f-8b57-5d98a0a71e86 | signoff | Client Representative:
a1b909fe-58a8-5ec9-be06-af072c4e7dd0 | checklist | ITP-I05B ENTEC - Instrument Loop Check |  | ITP-I05B ENTEC - Instrument Loop Check
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
1f4e7cad-b83c-577a-8c4e-e1ae282277d9 | checkpoint | Please upload ITP here when complete
a1bed83c-9ef7-5454-bc46-42f38feeaa34 | checklist | ITR-CL-1-100 General Electrical Equipment |  | ITR-CL-1-100 General Electrical Equipment
40bc9c93-e593-5dbb-adf2-ebf0063e648f | checkpoint | General Electrical Equipment
cb2b4f97-7bb6-5cdf-b568-f35972d86f61 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
60cf451e-2147-50f0-878e-d1d58401ec15 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
ff7f4f22-5a01-5101-8163-c5d80786d1b0 | button | Installation is clean and tidy | Yes,N/A
2a27440d-8e2b-56e8-981f-798dd378e5f3 | button | Mounting arrangement correct | Yes,N/A
39d43819-935f-5663-bd11-12aa8755583f | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
e1c8e2c4-6fdd-52ac-b0b3-1dcd9dc10b14 | button | External cabling is correctly installed and labelled. | Yes,N/A
3f4f40a8-a7c7-52ba-88eb-0ed6855575f0 | button | Check that Equipment is correctly earthed. | Yes,N/A
af3cd66c-f354-5542-9f6d-342aeecff850 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
1659b601-6c2b-50b6-9175-44f9de00b359 | button | All spare entries blanked off with correct plugs. | Yes,N/A
aaf24b8e-ed4c-50b7-a7e2-48d43fa4947d | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
37da6b30-7a6e-5253-b41a-d9a2a5a1b4a8 | button | Conforms to Specifications and Drawings. | Yes,N/A
af731ba5-7686-5fc4-a623-04a38d5c3ff6 | button | As-builts complete. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
a9832c0e-7740-56da-a183-cf3080831d45 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
3be74dfc-63f0-548a-a987-235a08b0da5a | checklist | ITR-CL-1-101A Conduit/Ducting Below Ground |  | ITR-CL-1-101A Conduit/Ducting Below Ground
f9955031-6d35-5a70-b1c8-18bd7eb6cb70 | checkpoint | Conduit/Ducting Installation Below Ground
408a7d94-31bc-56a4-9a3f-c4846c80162c | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
d7f3657d-5f2f-55ea-bd1d-49025ee6f55a | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
83053eed-e03e-57a3-b4dd-37d0d23f1a27 | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
e7d1e47f-c7b6-54a2-8cce-b288322b4e14 | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
b64c2bff-cd7c-5ad4-b6b3-c1a3961ed5cb | button | Check all fixings are tight and secure. | Yes,N/A
14356867-98fd-55f9-8a02-dbaf14dd2fa7 | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
4824a953-d3aa-536e-8688-a9b24f1e2f0a | checklist | ITR-CL-1-101B Cable Supports Above Ground |  | ITR-CL-1-101B Cable Supports Above Ground
07ed07f0-b23b-57fa-8751-a99f24f5ee9c | checkpoint | Cable Supports Above Ground
545ba4b9-3ca9-53bf-a8c1-33531ac2922f | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
08f6bbce-68f2-5214-8e82-3c09cc89da33 | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
9de24e4f-cfa4-5a4b-8afd-73762a459057 | button | All covers fitted if applicable. | Yes,N/A
ee6eb51c-4cb0-5ff4-9fa1-fd6a361665c8 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
49004d30-ee0f-51e2-a510-d838e09c10af | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
2c5500c2-0096-57dc-a19a-400a00138f91 | button | Splice plates, barriers, earthing system secure. | Yes,N/A
d9b9bf78-2d3f-5724-9afc-22cf8925fff5 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
9e40b1d4-5f40-562f-9287-d94c46168b0f | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
63a588ab-dc2c-5420-985d-41d2e43f6907 | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
18d95617-e1a5-5897-8fc6-86d92bd4e5cb | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
94fbde4f-136d-5a56-bfde-952c6a4e7848 | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
2f2f2852-6611-5582-bbe2-bd5b29ac5e2a | button | Tray bonded to structure at correct locations. | Yes,N/A
cda96ee6-f7a6-59c5-b81f-8011bd5bec87 | button | Earth bonding continuity tested – record result: | Yes,N/A
2c57a430-fca0-5f27-95f5-d02cc773e721 | checklist | ITR-CL-1-101C Cable Transits |  | ITR-CL-1-101C Cable Transits
fdf8946e-d2a2-5a47-8940-7ce1e4e369a5 | checkpoint | Cable Transits
51b8c413-f37a-5297-b0b4-21d5691f4593 | button | Transit frame installed as per drawings. | Yes,N/A
96467c01-a9ec-5277-bc40-fd9e3023e7a6 | button | Transit frame identification marked correctly and visible. | Yes,N/A
21c75966-42d8-5280-a54d-21e841a37bbb | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
2f69ee43-4b4f-592f-a137-d72a6e2e14f5 | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
8a5cd616-5189-5ed3-aed7-bdeae1ecace4 | button | Rated insulation installed to transit (where required.) | Yes,N/A
f7647de3-9241-5a92-b7f5-717e39d07ab8 | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
48ddf984-809a-5360-8ed9-1ba660247247 | button | Cables pass through frames without strain on blocks. | Yes,N/A
4b79551f-3b55-583c-9900-01559e09ee55 | button | All cables identified on both sides of transit and visible. | Yes,N/A
502e00ee-104b-509c-aa19-461cf72e7e90 | checklist | ITR-CL-1-102 Entec - Distribution Board Installation |  | ITR-CL-1-102 Entec - Distribution Board Installation
ae4d5efd-a489-5f74-916f-77b38658b02d | checkpoint | Distribution Board Installation (Mandatory Photo)
dd10045f-7c02-5b32-ba7d-bb204fc01509 | button | Inspect for mechanical damage from freight and handling | Yes,N/A
36b5b6df-dbf1-54ba-8e0b-10de26e2b947 | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
60623dbb-82b8-5d8e-a013-e2c297e0caed | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
e41011e6-c5d0-5d9d-bb0f-5df48dc6e223 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
0fdd7ef1-fea1-566e-b9f8-11dc9089b254 | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
be177262-355d-5f6f-a945-678a725568c9 | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
d46d2cc9-6446-596d-8fa6-c45c72ec9df2 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
274fc4ae-0c46-5b8c-ad55-393f1c953843 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
5fad4a36-6295-5402-89f8-c583977a29e9 | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
232f2992-9a08-58cc-9ab7-49d9bbb97d1b | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
2845f34a-33d7-5508-8ec2-13c4edd2f9e1 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
35dd8359-22f7-53ce-a056-50f64edb0e79 | textbox | Earth Continuity |  |  |  | Ohms
3fa14140-bdf5-566b-904a-595c31dfe6d2 | textbox | Earth Bond |  |  |  | Ohms
5d57d622-bdb7-59eb-bd68-fd952363ad21 | textbox | Fault Loop Impedance, PSSC.
dc872782-c03d-5f2f-ab18-f61d35777b0e | textbox | RCD Test results (1/2x I, 1x I, 5x I)
e7372391-e24a-5c79-a513-67117cff418c | textbox | Voltage and Phase Rotation
fe76bdb6-0d0e-5673-9e56-ceeb7a05a647 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
af126e36-13ed-57ce-9666-a41aef3e5793 | checklist | ITR-CL-1-103 Schedule of Test Results DB |  | ITR-CL-1-103 Schedule of Test Results DB
56b6b7e0-eebb-5754-9e92-822956f50a78 | checkpoint | Upload completed ITR scans
b157e1bd-4e02-5ec1-8b09-a5ec0ef2b0a7 | checklist | ITR-CL-1-104 - Low Voltage Cable |  | ITR-CL-1-104 - Low Voltage Cable
5a674726-f510-523e-9da0-6baa8408aada | checkpoint | Low Voltage Cable
af28edc1-96a0-5a5f-bd7d-81afda15fcbf | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
e46a9aa7-5f6d-5842-bc61-cfb5182e4911 | button | Check dressing / cleating, cable undamaged | Yes,N/A
5c2861ad-6315-5bc7-bae4-059e0a0eaefa | button | Check cable cores correctly identified and labelled. | Yes,N/A
22f0c09d-6de4-5561-a994-c02bcf20db5f | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
77d6ecc1-fdb5-5479-8bb1-91e113d59070 | button | Check Armour / Screen correctly made off. | Yes,N/A
fb923de7-835f-5346-9267-0c1d13b74f2c | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
054e931d-90ae-5f38-bb32-dc7a88eacd10 | button | Glanding / Locknuts correctly installed. | Yes,N/A
352202bf-aae8-5e4e-9735-7d1feb3c873b | textbox | Gland type - from: |  |  | Haz. Area Rating
d7c958cc-8da0-56eb-844d-cc4554705410 | textbox | Haz. Area Cert Details.
40c0b575-5d7a-5779-9b72-185f2b33d28a | textbox | Gland type - to: |  |  | Haz. Area Rating
823ab698-3882-53fd-b7c4-a046de87be21 | textbox | Haz. Area Cert Details.
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
17074137-45f3-563a-9f62-a5192912d54d | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
1b3ad86a-fa35-5da0-bba4-564a2dceecad | checklist | ITR-CL-1-105 Control Panel |  | ITR-CL-1-105 Control Panel
b9c48017-8b15-5347-8a29-a890e4be9590 | checkpoint | Control Panel
b32d8822-1353-5faf-8885-16285f555a51 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
97775b31-6c59-5c38-97e7-faa0f79c54d3 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
c6564c61-370c-5dfd-af7b-ac634022aa9b | button | Check for mechanical damage. | Yes,N/A
5a0b37f2-3c66-512a-913f-25fdd58a12c6 | button | Check tightness of circuit connections. | Yes,N/A
2d9e2ffc-ce5f-5879-a79b-95b7019e6c0b | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
6e4c2e2c-19a6-54d0-a92a-78e0458a07de | button | Ammeter scale and current transformer correct. | Yes,N/A
4d78ad12-1e63-5aab-8cba-8f294bbe7547 | button | Check internals for cleanliness. | Yes,N/A
6672607f-dbe1-50f6-a535-09eebcfc9c58 | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
c3cac6f6-ff46-57cd-a687-2e0c862a7aea | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
28cd137b-01c6-5f66-8d4e-68584f0083ff | button | Heaters correctly installed. | Yes,N/A
ffd04a09-51f4-5631-8a62-72a2c8d36942 | button | Fuse rating correct. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
48527285-cf10-596b-b759-6eecee08cb68 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
79d7eee5-04e5-536b-9855-622b05b02767 | checklist | ITR-CL-1-106 - Junction Box |  | ITR-CL-1-106 - Junction Box
a8e8cecc-2cf8-5cda-9b8e-dd2f4097acf9 | checkpoint | Junction Box
245cf2c2-93e7-55f4-8b8f-084910184ab1 | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
e3722cc5-e37c-5219-9ad3-e6af0c0e3bdc | button | Check mechanical damage | Yes,N/A
8d4f6c79-ed60-5205-9480-609b73d9bea3 | button | Earthing installed correctly and as per drawing | Yes,N/A
8cfd38ca-9728-5203-8826-00aa47888d5f | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
216f195f-1635-5eb8-ae32-8039ae13c07a | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
1ee44d58-4ef0-524c-9c0b-6cf1d43db717 | button | Check all Cables & Cores are correctly identified | Yes,N/A
5319ace1-7c03-56db-a539-1b75be9081de | button | Check internals for cleanliness | Yes,N/A
68ff54a5-b7c5-5162-aa43-cc806b8cf101 | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
bee4f161-e6b7-54db-b47d-7cb9ac72ffbc | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
72788ef3-35a9-597e-aa86-40956951b878 | textbox | Record earth bar resistance to earth bond
e567f68d-b461-55a9-9f72-f2a034833fd7 | checklist | ITR-CL-1-107 Heat Tracing Circuit |  | ITR-CL-1-107 Heat Tracing Circuit
79223b5c-5afb-5d19-8fd5-66ebda5dcea9 | checkpoint | Heat Tracing Circuit
f0a55675-6e06-5319-931c-d84f849fe50b | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
1dd2bd0a-28f6-52e7-924d-4b8c31c44e5b | button | End caps and connection kits correctly installed. | Yes,N/A
f0254351-98f8-5421-9a2c-2bd73c9d2a20 | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
997c8955-f08b-575e-8fdd-2e7ca677b1bb | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
b9630306-2879-57d0-bbd6-d4fc782eee4c | button | All spare entries blanked off correctly. | Yes,N/A
7b96e0b9-f07a-5593-b29f-5ac940bbb33e | textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
f94780da-b851-5167-81f5-7b59c66cf3bf | button | Equipment certification meets the area classification requirements. | Yes,N/A
a0d2760e-0c76-5f68-89cf-85c50306a06c | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
e41c45b0-9059-5b1b-bd69-1336d6551631 | checkpoint | Electrical tests
4f89bd2a-fca3-515b-a040-451bbb38e09e | textbox | Insulation Resistance: Phase - Earth
5962cbe2-2039-58a0-a14c-ef598aba88c5 | textbox | Insulation Resistance: Phase - Neutral
9712c965-95e8-5464-94b5-5ca019e8db4d | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
5be6c9bd-3078-530e-b2ae-cdc50eaff832 | checklist | ITR-CL-1-108 Electrical Switch Rooms |  | ITR-CL-1-108 Electrical Switch Rooms
988275f7-8ab8-5361-9934-ba10043407d6 | checkpoint | Electrical Switchroom (Mandatory Photo)
c35c8c3b-6e5f-5852-8138-e12183b47e82 | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
9cb19cf9-3094-5dd8-b75f-c9e71c4da266 | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
6a9f984c-8d46-531e-ae34-602a384296e1 | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
38133667-8af5-5f22-9190-904b05cc6b48 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
1bb30d2e-808b-5e4f-b3d6-1a59666c3f13 | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
39b51e08-1787-5c74-8ef1-2f12f5dc619c | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
506a4e85-a11e-50cd-b2ae-3f34b9aaffe8 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
194f3185-12e2-5655-aa25-e24355f795e8 | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
513c5db0-c432-5a6b-8e94-d5956b35794f | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
987ea7a8-ff94-5ca8-b9b2-f4ceda30a358 | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
c2c4ff65-2e25-515c-98e2-46b89ca72d6a | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
8251fa54-2619-5f08-a5cc-8bc7e06dfb45 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
8782e416-2329-5221-98d9-08b14c73962c | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
cac4a24a-fec9-53cf-8a0d-394f91f9eda7 | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
d9a8e4db-3fc8-58f7-a3cd-6245104a996e | button | Check internals for cleanliness | Yes,N/A
95d95cd8-dd26-5176-8d7c-f8dd08d99591 | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
3ad5afe7-96ec-5205-9dad-f7e3848b1c62 | button | As-builts complete | Yes,N/A
f14d06f7-b040-535d-814f-36634c2f1b67 | checklist | ITR-CL-1-109 Electrical Equipment Package |  | ITR-CL-1-109 Electrical Equipment Package
b90d357e-c70a-5808-b2dc-3ccd86660fc8 | checkpoint | Electrical Equipment Package
de1a4929-51d8-5010-bb5a-8acbeaef7579 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
72770694-ba7a-53a3-8049-ada9f0bd30b5 | button | Check equipment is correctly rated for the area. | Yes,N/A
46e6b0ba-1237-5410-8e55-8782af342125 | button | Check if package is complete with all accessories. | Yes,N/A
0e7ade92-ffba-519f-99b4-c1ace5282e56 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
054459c2-a788-5880-b639-bad34d3ef7ab | button | All transportation supports, stops and fastenings removed. | Yes,N/A
91359383-e280-5b6e-92b6-97eb0e6046b6 | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
b6048e1f-0a8d-5bd7-a133-d4dede4e475e | button | Check package is installed on a level plane. | Yes,N/A
eb88b8e2-3dd1-5fee-a01f-8a04c9481d2d | button | External cabling (if required) correctly installed. | Yes,N/A
f0753463-a336-5ecd-b492-08f4dd0684ec | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
7c187dfb-945b-5f5d-b74c-ec1330baa79b | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
9fdec3f6-3e46-5769-9cad-68cd22178037 | button | Check that equipment is correctly earthed. | Yes,N/A
576774d6-4e9c-5045-b609-1f8c9697a62e | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  |  | Ohm
99e9c3d9-7457-5277-832e-03c87bbc4f49 | checklist | ITR-CL-1-110 Generator Package (LV) |  | ITR-CL-1-110 Generator Package (LV)
faeb6d32-f50c-5e49-950c-dac060a799c9 | checkpoint | Generator Package (LV)
e6fbe5d1-989b-5a7e-b072-80dc518b5d7e | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
e9c3bab9-6b0a-50d1-9266-6b9eff330218 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
ac81d7b6-fbb0-55a6-9705-74febf2117b2 | button | Check terminal boxes and glanding correct. | Yes,N/A
43aaa178-860c-5c80-9eb2-b1fedb98d454 | button | Instruments correctly installed. | Yes,N/A
3f2812c3-0080-5af8-b515-1c8bbb556654 | button | Heaters correctly installed. | Yes,N/A
c0e1f9e1-d4ae-5cc6-9d5e-1670fb4f81d7 | button | Check unit for cleanliness. | Yes,N/A
c04fb45e-b6a6-5b3f-be27-d7d74e800f98 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
8f2c4e75-2f9e-54ec-b5fc-f2eb0b40183e | button | External cabling correctly installed. | Yes,N/A
d349a7dc-022f-5b37-b638-395c086a5f48 | button | Protection of live parts adequate. | Yes,N/A
ab32df2f-ff8b-59a0-910c-73386532b64c | button | Main terminal box complete and terminations correct torque. | Yes,N/A
3302ba7c-ca89-506d-b543-2d6436452c85 | button | Ensure direction of rotation is clearly marked. | Yes,N/A
f809155e-fd49-55cd-b27d-40689fb303cc | button | Check gasket and seals are not damaged. | Yes,N/A
c7f299c2-ab94-5e6b-893a-f06d46279e6d | button | Unused cable entries are correctly sealed. | Yes,N/A
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
1a8692e3-b3a0-55c9-8688-c459a400bd8b | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
0b143cde-a7c2-5c3e-82b7-a93cb5550b3f | textbox | Heater circuit insulation resistance:
0aef2d9b-f94a-5db9-8325-b38113a3a749 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
1927ac8a-b833-5bf3-90c1-47fdd4194cf4 | checklist | ITR-CL-1-111 Electrical earthing |  | ITR-CL-1-111 Electrical earthing
a5844d1c-d73b-5ed2-b3a4-ec9d9124535d | checkpoint | Electrical earthing system installation
ed5cbec0-bbd9-5717-afa2-bbabadab2ad8 | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
e9879619-f120-55be-8d65-9857f7539397 | button | Ensure that all metal work is earthed as required. | Yes,N/A
40b4f2a2-bc56-50bb-b7e4-4311ee8e416d | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
012de3bc-21f3-555d-94c1-169b7f7d57af | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
30fbe546-1267-58a8-8b54-ec3ee26c26f8 | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
2e0a11fa-cb2b-5e15-9e21-8f7d322eb8df | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
7795a8c6-9b99-560e-8c3e-4a1637f7e9bf | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
03714326-861f-5bc9-9980-6d59b15a4973 | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
eedc87cc-fe78-5415-af66-eb35afa8d051 | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
27a7a44b-94e5-5483-91c5-3d5da631d8aa | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
ac7a48ae-b931-5d99-80eb-aaf2424ab844 | button | Ensure that earth cable identification markings are in place. | Yes,N/A
673bd3b5-a328-596b-ba6e-9f804e3743d7 | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
8ae72d1d-24bb-55b5-b953-9000650101a0 | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
9fb6c93b-c93d-5301-8726-b7b7ba5927a7 | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
e0acc7d5-ee0d-557f-a05b-651fb56d3458 | textbox | 3-Wire earth test results (If applicable).
930891ae-e43d-5ca6-86d5-adf9a95d195c | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
a45de04b-c848-5952-8d2a-e31446744d3f | checklist | ITR-CL-1-112 Motors |  | ITR-CL-1-112 Motors
b379033e-6a86-54bb-887a-d19e9726729c | checkpoint | Motors installation
481f033e-46c8-5430-b530-6f504e55bdbb | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
88c4988e-d18e-5e59-8c4b-6484dfd5c17f | button | Space heater | Yes,N/A
47f7463d-fb36-563e-89c8-501bad7c1569 | textbox | Space heater specification (Power (Watts) and Voltage:)
92fda034-b723-508b-8166-4e1c11fdac37 | checkpoint | Nameplate details correct and in accordance with the data sheet (Mandatory Photo)
73a15ef7-a7ab-543b-88d7-1ca840163365 | note | Upload clear photo of nameplate
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
d173609e-3e03-5d51-965a-5b0e1db325ec | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
d78a2bae-0d71-5dd3-a29c-8bdd83d3cfed | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
6c5ab35a-a8bf-536c-8c9d-a833e064cd07 | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
55c44db7-a0fe-53b4-9b37-a0039b77be66 | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
92238dca-2d29-5bed-80f2-44e4db9408dc | button | Correct glanding for area classification. | Yes,N/A
75e0a3c4-6588-50e6-8a4b-918df7a2f881 | button | Holding down bolts fitted correctly. | Yes,N/A
7866c60e-e106-5a1e-aad5-30fb8248593a | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
890fb388-d930-5723-a4c5-a6ac805f468d | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
774fc876-b113-5771-bb52-817081b294bc | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
68654064-6090-5f89-affc-b6fa25f4374b | checkpoint | Motor Installation Testing
16f8af62-d6d0-51ab-b8a7-f880c9595eb9 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
87efb043-7852-5434-b74f-5895c1d22b39 | note | Insulation resistance U, V, W
c9db8775-ca52-5fec-a144-234e961e5c9c | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
a7ca9aef-9cb7-5178-bc50-97f58c58ecb6 | note | Insulation resistance U, V, W
e440f398-1b1f-595e-8d57-d7738c1f20d1 | textbox | Motor continuity between windings
c33dab3b-e5d0-5e71-a1e9-fcb65f2c5561 | note | Continuity U1-U2, V1-V2, W1-W2.
5692b944-3d62-5378-96d9-2d08640ed6ef | textbox | Space heater continuity & resistance check
832cb8eb-373f-53a3-8db7-0431fb43e82d | note | Continuity & Insulation resistance results:
696c7508-4ab7-535d-b554-cc4f03324fe1 | textbox | Thermostat or RTD wiring resistance check
3cbbd2db-5840-594a-81c1-779596aabf45 | note | Resistance:
c45f3e5a-11d5-5281-b95e-25a319732177 | textbox | Check motor is earthed correctly and record motor earth bond:
4a998987-8120-5498-b98d-bdc0f10f4da8 | checkpoint | Additional checks
9b10d71f-3358-507d-8a4a-20893d8d6f74 | tickbox | Winding temperature detector
1609bd00-806f-5fcc-849c-5d4e4e07be9e | tickbox | Air temp detectors
5474f5ca-d6b1-5888-a4bb-ad0f40e3eb48 | tickbox | Bearing temp indicators
76cb80fc-a5da-55c6-ba74-6904835b8bd0 | tickbox | Vibration Monitors
700fd2bc-8cce-59c0-b270-ba655c37ff4f | tickbox | Condensation detector
ad7a159c-e128-5124-b632-ab7f525a6695 | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
3080b9a2-d7b9-5fab-9678-883bf29f3898 | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
45e0c59b-ebdc-5bf7-83fd-6aa3efd96f3a | button | Installation conforms to specification and drawings | Yes,N/A
4c6f4151-1a21-5825-9277-5c1539c7db16 | button | As-Builts complete | Yes,N/A
19513ac1-0858-54b3-8f99-b38a549be2fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
b2400ed4-f494-5645-bdd2-a3a1c7d8143e | checklist | ITR-CL-1-113 Motor Control |  | ITR-CL-1-113 Motor Control
8b7f5c8f-9378-5c72-98a0-cff0c3ff4659 | checkpoint | General Motor Control
271889a3-0b99-5efa-8b30-3c840a309d4b | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
42dd4760-41a4-512b-a9ab-c89d144ec924 | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
3ec738bc-3381-576b-ab5d-b8dd559f3a94 | button | Check preservation and transit items are removed | Yes,N/A
7ae9798c-f24b-5c71-9791-d6fa6e08594d | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
2252f925-b80a-52dc-aa9a-30b89e0a442c | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
b37a4cd2-8560-56fa-ba6b-3ef8f07e645d | button | Check earthing bar and connections are correct and tight | Yes,N/A
423e5baa-bfdd-5581-bece-8cab5fee68f0 | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
97ad2b41-4cff-562c-897a-79017543f3f1 | button | Check phase identification on power cables is correct and visible | Yes,N/A
bc55e934-6184-5205-818f-f531f2da50d9 | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
7de845f5-1cc1-5751-98f9-953a1e450f1f | button | Check all other nuts and bolts are tight | Yes,N/A
c4b35821-b001-577e-981b-0ed6f1fb942a | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
dee4f953-7134-5cc7-b78d-d26f30a10744 | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
12787137-a0bd-5672-be3e-39544771225f | checkpoint | Variable Speed Drives (VSD)
41614d56-a8af-5092-9cb0-75a07864792f | note | Record VSD Details
3e1612e5-3dc5-5ffb-8b8c-a9c5a0994c9e | textbox | Volts (Input) |  |  |  | V
bbffba4a-45ee-5161-95ad-eb804bcc9014 | textbox | Amps (Input) |  |  |  | A
fdeeec23-31f5-5b22-8981-4c3cc478e235 | textbox | Amps (Output) |  |  |  | A
ad6bba94-8c05-5051-afb0-fdb46e1f73fe | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
3ba30a88-6699-5648-9dc6-3850dcbd81c3 | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
8edb13bc-60e2-5deb-b03d-0e1248cf12c7 | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
ee2d6df1-da80-53e7-9211-f7067bc8f4df | button | Check control signal cables use twisted pairs | Yes,N/A
a909a109-960c-5031-99e4-3d7bd42f0822 | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
62401cee-bc7c-5620-8e17-9c0b097e0f37 | button | Check analogue and digital signals are run in separate cables | Yes,N/A
100277f1-21fd-5165-beba-4958eacfcc37 | checkpoint | Voltage segregation
8ad4c2f8-6471-5e41-8427-26fdd46c4ac2 | button | Distance between input power and motor cable >300mm | Yes,N/A
8d4b68cd-8844-5208-b74e-25cb470a457d | button | Distance between input power and control signal cable >200mm | Yes,N/A
39727ef1-4ef6-56e4-bec7-abaaafa7ddec | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
e2516a13-edf5-528a-a49c-36ea963a218a | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
e0c0a718-f04e-522d-9bf2-3957e675e456 | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
c279141b-58af-5282-a021-59e7112de91f | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
d1321e44-ff12-59d4-aa8a-0df8e46c8a8d | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
dc639f77-ddbc-59a0-a1ff-43b2a1403aee | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
7746c8dd-c7ce-51cb-85e4-2ed0eeb2a50e | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
895b07e9-0177-56cf-a526-b503466d8675 | checklist | ITR-CL-1-114 UPS Installation |  | ITR-CL-1-114 UPS Installation
347ed6f2-edf9-53cd-afb5-7250c75c7497 | checkpoint | UPS Installation (Mandatory Photo)
655d03c8-7681-5332-9444-21a0283d5354 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
ed9c1d95-9a89-57cc-8d03-1f0d8b36ff8a | button | Check for mechanical damage. | Yes,N/A
aea841e9-31ab-539f-872a-1044ac154d25 | button | Panel IP rating is correct. | Yes,N/A
397fc40c-7a69-5ef2-b67d-09213ffe7cd1 | button | Holding down arrangement and seat alignment correct. | Yes,N/A
262740ab-cdd3-5090-9149-ba920db5d195 | button | Panels aligned correctly. | Yes,N/A
1c9ce2cf-65ed-5c1a-b678-dd6e6b26c32d | button | External bonding correct | Yes,N/A
b3e5c818-c5cc-5e49-8587-92d32e461ac7 | button | Phase identification correct. | Yes,N/A
e5ac5a6a-a284-5786-b72e-f99a363362e6 | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
227fdf0c-9120-58b7-a162-b64a01cabd0c | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
64594450-bd12-5ca3-b334-388aedfe47eb | button | Check Main Isolator and Bypass switch operation | Yes,N/A
de0d11ea-7945-52d1-a887-d18d09663978 | button | COM Interface & Mod Link. | Yes,N/A
e828b151-e799-55a6-8ca1-70b7061ef18c | button | Padlocking facilities correct. | Yes,N/A
3fdce359-213a-5841-8809-e3ad8cf1f943 | button | Check internals for cleanliness. | Yes,N/A
1c2b202d-3598-524f-8900-035008717f05 | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
4b09e7bb-403c-50e2-9f20-7893df9d86c5 | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
37d878a1-cbae-520f-8189-62138a287e44 | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
0bf69a78-986b-51cb-8425-f587f1c40d47 | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
6fc4bb8a-4347-5aaf-885b-15701c3db0fa | checkpoint | Test results
c7229fd8-3143-5995-ac3a-94e91ae24239 | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
5955295f-23db-5918-abcb-2b308456c01c | checklist | ITR-CL-1-115 Lightning Protection |  | ITR-CL-1-115 Lightning Protection
b51a0ab7-a35c-50cd-8d4c-319c10a51654 | checkpoint | Lightning Protection Earthing system (Mandatory Photo)
962dc00a-bf7b-5e05-acf2-d5645b2eb507 | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
3fd75246-24af-5c69-959d-532d34b705ac | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
0fb071fe-8243-5ed6-9685-eb139ed94ee5 | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
298085f4-2d0f-5af7-8443-080df6513427 | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
c6f282a1-b08f-519d-ba1d-89ebf825c0b3 | button | Check all installed components are firmly secured | Yes,N/A
61e068f0-3e1d-5b6a-a39c-5b705e475cec | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
67727910-4ffa-5a66-a264-005150daf9e9 | button | Check earth termination systems are interconnected | Yes,N/A
12880d6b-3ef4-5d2c-82ae-fd9fd56afbd6 | button | Check isolating and switching devices correctly located | Yes,N/A
ca1a8f84-153c-54c8-a30f-ae68fac9c2a5 | button | Check warning signs and diagrams are installed | Yes,N/A
665900b8-513e-5425-b6b9-1b80f47d7d52 | button | Check accessibility for operation and maintenance | Yes,N/A
e9642488-22e1-5802-9274-a07b19d2ef31 | checkpoint | Test Results
157ca8be-2ef6-5e87-ba6f-f102e88400c7 | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  |  | Ohm
ddcc6e90-3827-5bad-a39e-b99ee4d7280f | textbox | Earth termination system resistance is correct and record value |  |  |  | Ohm
b1d32614-dcb6-5954-938b-7724481d8f46 | textbox | Record the insulation resistance of the electrical installation |  |  |  | MegaOhm
a5a93179-92e2-52e2-8be0-00cabc3894c7 | textbox | Continuity of the main and supplementary equipotential bonding: |  |  |  | Ohm
b57f4fd6-75d7-5a87-adfe-e2df08d34c15 | checklist | ITR-CL-1-116 Fire and Gas Detection Alarms |  | ITR-CL-1-116 Fire and Gas Detection Alarms
e9820304-02d0-5985-8faf-5cc6d712f981 | checkpoint | Fire and Gas detection alarms
91f7b1d3-927a-5fc1-9922-bc889c00505c | textbox | Make and Model
f74503eb-f8b8-5f8e-b15b-bc3a87d9ea8a | textbox | Type
5e850025-09cc-5119-915a-620b56b44ce0 | button | Location correct as per drawings | Yes,N/A
8b274b91-c78c-587a-b0e8-39b43622205c | button | Component & Type / Model correct per equipment schedule | Yes,N/A
d7a2ddc7-5046-5fa7-8d29-7be80745b4dd | button | Cable connection & termination correct | Yes,N/A
8db5056c-243d-5516-a00c-13058274d2c3 | button | Installation free of mechanical damage and clean | Yes,N/A
0ce5a0e7-0835-5d7d-997b-7463dc6ec51e | button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
ad343b60-f41d-54d7-a669-217ebad820be | button | E.O.L Installation | Yes,N/A
10a1d75d-7f45-549f-ae11-b119f9100343 | button | Test tubing installation | Yes,N/A
16a9ac87-3d01-5ae4-b987-e759bbbf1289 | button | Detection Path Clear | Yes,N/A
e7581576-5a10-5963-90b0-44587360e1f6 | checkpoint | Inspection
90a3b868-54d7-5ada-b1b3-d1cf777ceca2 | textbox | Tag No.
748cea45-9cca-57af-8ec8-1452e3e9e996 | textbox | RX Tag No:
bdc38525-5b3f-5bef-9b2a-6d376212e844 | button | Area Classification correct | Yes,N/A
96e54638-45c0-57d7-bc02-07452460aa8b | textbox | Hazardous Area Certificate:
d4d1741e-bff6-5186-b897-df18213d20a0 | textbox | Detector Type:
a8e6f72e-0e9d-5a3a-8251-8461ff0dadb2 | textbox | Gas Type:
dc36ed29-eb76-5be6-82d8-6065c51d4cc2 | textbox | Supply Voltage:
6489be0d-16ce-5477-b392-be1e7b98d1c2 | textbox | Output Signal:
f60ecb48-734f-5a72-b2ef-09bf19aa9dab | checkpoint | Functional Check
94fbb7c7-03dc-5b8c-b852-90e5415b1f35 | button | Self Test | Yes,N/A
103afaec-87cc-596d-b875-68318384ef65 | button | Alarm Operation | Yes,N/A
eefdd49b-785e-5e37-b0c0-50283fdb91f5 | button | Fault Relay Operation | Yes,N/A
18957424-83c6-5d83-9bbe-1169bdce9e22 | textbox | Measured output (clear path)
1b23ccee-71d3-56c0-9249-3592d9153ad6 | textbox | Measured output (blocked path)
0ad6eb12-6904-568e-b578-63d2ce00b169 | textbox | Measured output (filter in place)
f7366789-c1ce-5e77-a10e-7a5fc1d1b2da | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
fcddc6c3-9e70-5ee8-b21d-2cf24bff83d8 | checklist | ITR-CL-1-117 Instrument Tubing Installation |  | ITR-CL-1-117 Instrument Tubing Installation
22a4b0f7-8c08-5898-8def-9f2ce9f0fe16 | checkpoint | Checks Pre-Installation
2e7fc366-26f6-5021-8aeb-271a33e5282f | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
9ca1d4f5-95e2-5a47-8b4e-73e78d1f79e5 | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
843f4816-9c4b-55d5-9da9-9c719e8bcddf | button | Tube fitting size and type confirmed and available | Yes,N/A
a6d87294-9fa2-5060-a418-dbd33f374e00 | checkpoint | Checks During and Post-Installation
4968da8e-676b-5ef3-bdba-b430d7ad1d52 | button | Correct thread compatibility and engagement | Yes,N/A
84be2f7d-f244-5d87-a8ed-adff19279816 | button | Correct thread tape and sealant used on fittings | Yes,N/A
0cfcae7a-f9b5-57e1-8fc7-32ebcede9857 | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
49722970-578c-56ae-b877-09e9203c11e5 | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
70763579-d4d8-56c6-a6ec-bb4ba1a5c649 | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
c2e51bd9-35f8-50e0-9389-00c99de63ea7 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
52ca6a4f-fe50-5c4d-8cb9-16bdeacfc70c | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
66858c37-fbb2-578d-811b-66e29a58aff3 | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
e8c5a865-c141-5574-97df-4ce185ce3988 | button | Random check with No-Go gap gauge | Yes,N/A
6306f1ee-a88c-5e02-b5d3-513693e4dbfe | button | In service leak test performed and passed (ITR-CL-1-118) | Yes,N/A
b77b2185-19d4-575a-996e-f93077065e0d | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
8312427c-3f1e-5a34-a83f-13a43b12be7b | note | Refer to Swagelok book for tube/thread size pressure ratings
0ed21009-a791-5a6d-a31b-2bc2bbe6348f | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
2cde575a-c826-5aad-82b0-bfae9f329be1 | checklist | ITR-CL-1-118 Instrument Pressure/Leak Test |  | ITR-CL-1-118 Instrument Pressure/Leak Test
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
312025e1-3aa4-5c7d-aa52-585ee212bd62 | button | Tube identification correct | Yes,N/A
03343d53-ec9d-5c39-8c6b-fa6ca5dfaf29 | button | Mechanical damage visual check | Yes,N/A
c939ebae-325e-5129-8cc3-5fbc505398b6 | button | Flow direction and instrument orientation correct | Yes,N/A
6913b8c4-d27f-5fc4-8dd5-eb1b6002100f | button | Tubing size and installation correct | Yes,N/A
ea42bb29-f001-5a6e-8d35-77d90be2e691 | checkpoint | Testing
6ea556cb-8c60-580f-a306-65fdc03cf287 | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
9dde934f-af34-5214-b0a2-800a3990188a | textbox | Test fluid:
da7acc81-9ae5-5c3f-b054-5acf2799e4a1 | textbox | Test pressure:
a1bea254-af4e-50f2-ae2d-92369cf7ecf3 | textbox | Max design pressure:
f64592ff-f819-56bc-a234-d2a209e0f199 | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
d3fd68d6-32f5-5f43-8ac3-f077f5b1e763 | textbox | Duration: |  |  |  | Minutes
8e886e08-9f34-51e4-b3ce-a7a66cde1937 | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
09e66fd4-b7db-5f5e-a369-00651bd26e51 | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
f940703f-8ef3-52f1-adc2-1efb474c5b33 | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
cc603aa1-7bc7-5247-bb26-b44d6904a9f6 | button | Check hydraulic lines flushed to project specification. | Yes,N/A
36d17a09-847c-57d3-8c79-12c7b3566a54 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
5c63d0bc-60d3-5a41-b7d8-7d1318c83bd7 | checklist | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation) |  | ITR-CL-1-119 Valve & Ancillaries (Pre-Installation)
56377b54-fde7-5406-837c-3890686afe74 | checkpoint | Equipment
c7902cfb-91a8-5221-ace4-52220adfc729 | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
71885bce-d253-55aa-aad6-1f6e8b3f00ae | button | Equipment checked for additional items as applicable | Yes,N/A
2c404141-581b-5dcf-b0bb-fb18186bd505 | checkpoint | Valve
973b94f3-475e-5c09-ac58-26f45d41ebe1 | textbox | Valve Size:
f20d9d4d-85b2-5a40-8dd0-eed2475e8bbc | textbox | Flange type:
46178969-5f15-5787-967e-863a89227d55 | button | Material certification correct | Yes,N/A
dfd1b5de-f2c2-5283-bcd2-dd64538b2fbf | button | Trim material correct | Yes,N/A
1456995c-c9c8-515f-8646-65968398415c | textbox | Rating:
d9937dd5-b397-5c5a-b005-517fdf84e468 | textbox | Service:
6d28f2af-9daf-56df-9677-24b936328a25 | button | Body material correct | Yes,N/A
5d3f0c67-e22a-5d31-94c0-5dcde54f30fb | textbox | Leakage class:
0610e54b-0dee-561d-8cbb-5ea26874b2fb | checkpoint | Actuator
ea7a4302-e31b-5d16-9163-9b69fbc71306 | textbox | Input range: |  |  |  | kPa
4b4228e1-3a1a-58d9-b97c-6fefb9148e4f | button | Failure action | Yes,N/A
ab7fed77-7f58-547c-a589-3dcc6d39745a | button | Hand wheel operation correct | Yes,N/A
a1a658d5-b431-5d40-b5b9-296b18cd0c83 | checkpoint | Positioner
9f9f468f-b7eb-5cb2-bee2-4a391dc38bba | textbox | Signal range
28a5795d-b6dc-5958-87ef-423101e4c7b3 | textbox | Output range
0c71f2ec-255a-5b0d-b0cf-ac779f8e58bd | checkpoint | I/P Converter
c28cfeb1-1625-5399-94a5-8b013f789ddd | textbox | Signal range
f6dda411-d9ab-5ecf-b26e-9962402b51f9 | textbox | Output range
d888314d-8e0b-5d10-aa66-e798050507bc | checkpoint | Filter/Regulator/On-Off Valve
d39e7391-c9dc-5e77-b9d2-4a7d9c6e01eb | textbox | Range |  |  |  | kPa
3b3b07a2-f274-5b91-ac1e-4326125d8d3c | textbox | Pressure setting |  |  |  | kPa
28d8afca-429e-5a36-ba0d-b32abd7deac8 | button | Stroke Time correct | Yes,N/A
7a3a8aa0-b4a0-5d29-acec-8e10a7739541 | textbox | Open |  |  |  | sec
eddc7056-f6b2-51ad-b7a6-b766b2ed6c50 | textbox | Close |  |  |  | sec
ffc3d9f6-1adc-59c1-af3b-bfa1ef97e584 | button | Open/Close times conform to commissioning specifications | Yes,N/A
12af7e2a-fcf5-563a-ada2-83262dee1165 | checkpoint | Fail Action
ec614ba9-235a-594e-a1c7-197827b5dc88 | dropdown | Electrical Fail Action | FO, FC, FL
1e269914-91f1-58b1-9190-82ba3aa37633 | dropdown | Motive Force | FO, FC, FL
2f5147e0-439d-5cf3-a34c-a68c79a610da | checkpoint | Valve Field Calibration and Hysteresis Check
ec856f7d-5948-5501-a248-63d28d70d62e | tickbox | Confirm test equipment is within calibration period prior to testing
4ecce144-7b92-5376-a8fe-9d25739a69ab | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
fc906e42-ff91-5aed-8b52-b7a39f44db3a | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
68e785a0-34a3-5d35-8fc4-1b0a402ae766 | checkpoint | Proximity Detectors
04cb349a-1c6f-5eea-ab26-85787735f476 | button | Open switch set, correct mode setting | Yes,N/A
8cc87a8e-f8b5-56dc-b10a-dfe5e65a97d8 | button | Closed switch set, correct mode setting | Yes,N/A
6b496ae2-8a2a-5e38-8e80-fa765b80c4f4 | button | Electrical connections and certification correct | Yes,N/A
ca31728d-089a-5a86-91f8-e6fa49290174 | checkpoint | Solenoid Valve
636044cd-24db-507f-a623-010ac1276448 | button | Operation correct | Yes,N/A
825a6f2e-3bfd-5f04-9627-c8e72439318d | button | Electrical connections correct | Yes,N/A
a5a070ca-4531-58e6-9b16-c2a979213aee | button | Electrical certification correct | Yes,N/A
8c15cfd9-ce6b-59f0-9944-7b5c80044bec | textbox | Voltage: |  |  |  | V
624b2e20-bee3-5885-bc05-3f03ebefc6ae | button | Pneumatic connections correct | Yes,N/A
c6f14b9f-450f-5187-af0b-1e63d1affbc1 | textbox | Pneumatic pressure |  |  |  | kPa
cf469d5d-719b-5c9f-939e-4b3f14281521 | checkpoint | Pilot Valve
3a1d4e7b-6274-5ca2-bf6a-cd2e64e24abd | button | Pneumatic connections correct | Yes,N/A
0ff1938e-c0ce-5503-ac50-7b00f7a334e6 | button | Operation correct | Yes,N/A
68617ca0-7a10-5bf7-9d34-ff60b33b6661 | button | Action/Lockup | Yes,N/A
d95c96d9-19e7-5920-8c36-be758c1c94e6 | checkpoint | Hydraulic Actuator
036099cb-3bb7-5f84-85a2-37263c265a39 | textbox | Working pressure
a8d86c7d-51e2-5730-a39f-eb731ad29d79 | textbox | Manifold pressure
2e2a6b4d-e0c9-5d86-999a-8d648dc9e31a | textbox | Fluid type
1f5173af-7b7f-5d87-8ed3-256ac6b591e2 | button | Hydraulic connections correct | Yes,N/A
f72452df-ab6f-5271-a347-de98a3718a92 | textbox | Regulator pressure setting
a62b06dc-d632-5faa-a886-7f19368bb4f7 | button | Pilot operation correct | Yes,N/A
3feee96c-5f87-541b-a1db-c34642a76ff9 | checkpoint | Accumulator
3bf6099a-5f6d-5d4e-bd7a-16979f529e99 | button | N2 Charge required | Yes,N/A
4c5449a4-0ec8-5004-87f1-08930390d5ef | textbox | N2 Pre-charge pressure
ff4e652b-ceca-516c-b404-3ed4ad5368c2 | textbox | Pressure switch setting
5567df27-7709-520a-ab43-37b13f72b8d8 | textbox | Working pressure
c0522002-1dae-5fed-a3f7-c043c09a2efe | textbox | Output range
196ad47c-8082-5bb5-9add-53d69ea5257a | button | Volume tank & check valve installed correctly | Yes,N/A
5bae141a-6bec-570a-8885-6c22a91756da | checkpoint | Electric Actuator
84e375bd-edcf-5a31-b959-00c66a045863 | textbox | Voltage:
2b8a5344-b4fc-58ce-8c3e-d5327a046dae | button | Electrical certification correct | Yes,N/A
3003da78-38ff-5327-93e1-7add060dee85 | button | Electrical connections correct | Yes,N/A
9fa4f9d0-7ae5-50e4-a995-52c4ab144116 | button | Remote operation correct | Yes,N/A
96f775c8-715b-5289-a875-4ac20e781985 | button | Local hand operation correct | Yes,N/A
1e2878e8-d699-5703-ac7e-4b52dd229efc | button | Torque switches and travel stops set | Yes,N/A
7d829060-f74f-56ec-b586-e00635137c82 | checkpoint | Miscellaneous Equipment
dd2193cf-450f-522e-9330-aaf0e6a2d7ff | textbox | Description
05d4c2dc-1e67-5653-986b-0445b024b51e | textbox | Manufacturer
a3940dc7-1266-583e-ac24-f1d0978f7aff | textbox | Model No:
334edf41-6e51-5019-999d-03dd0b9909d1 | textbox | Serial No:
e3ddc484-f2ad-5601-8d8a-4881522e51e1 | textbox | Range:
18003b78-0bf7-5e2f-9e09-b614d9233ece | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
b7eaa2f1-f3b6-5768-9905-32e5b3f1655f | checklist | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation) |  | ITR-CL-1-120 Analogue Valve & Ancillaries (Pre-Installation)
56377b54-fde7-5406-837c-3890686afe74 | checkpoint | Equipment
517f5143-2410-513c-8d7d-2f49f3d447d4 | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
e22f1dcd-0f91-56a9-b6cb-a657c721443f | button | Equipment checked for additional items as applicable | Yes,N/A
2c404141-581b-5dcf-b0bb-fb18186bd505 | checkpoint | Valve
9c92b41f-7204-5212-aed6-3257e9f1b7cc | textbox | Valve Size:
7d24d3e9-9f5b-5d1c-a74f-957af5d4b1f3 | textbox | Flange type:
0a702e8c-08c2-5464-b2d8-fd941f8a3d01 | button | Material certification correct | Yes,N/A
92bb5ec1-ca60-5b8f-b9cc-d35f849c577a | button | Trim material correct | Yes,N/A
b7a66705-312c-5a37-9753-203ae866d715 | textbox | Rating:
5c677dbd-6c51-56ca-b12d-e43861762262 | textbox | Service:
e53a853d-d881-565d-b124-03e1435e4930 | button | Body material correct | Yes,N/A
4d94fca5-e1ce-5478-bf38-7f1643e91e5b | textbox | Leakage class:
0610e54b-0dee-561d-8cbb-5ea26874b2fb | checkpoint | Actuator
9b7a3aed-3141-5b36-9b2e-2f29c818b119 | textbox | Input range: |  |  |  | kPa
e668a569-7003-53d4-8b08-8e4c92694a20 | button | Failure action | Yes,N/A
2cc0eae6-ebc3-52de-9a88-26880a470426 | button | Hand wheel operation correct | Yes,N/A
a1a658d5-b431-5d40-b5b9-296b18cd0c83 | checkpoint | Positioner
b353380f-c770-5581-9f3c-7bc0f3062240 | textbox | Signal range
692a4b53-6dd2-5d34-b8ee-c78765cbf08d | textbox | Output range
0c71f2ec-255a-5b0d-b0cf-ac779f8e58bd | checkpoint | I/P Converter
23899687-e4b5-5875-ab6e-0b992899d669 | textbox | Signal range
d9e416c5-a93e-555c-bcef-34fe261bf1ab | textbox | Output range
5d274912-fff7-50ca-a3f4-56a014ce13c4 | checkpoint | Filter/Regulator
133eac93-481f-5f9c-a0fd-083ac3e95430 | textbox | Range |  |  |  | kPa
afb87505-cc8c-590d-a8ab-f4fbe6467c95 | textbox | Pressure setting |  |  |  | kPa
12af7e2a-fcf5-563a-ada2-83262dee1165 | checkpoint | Fail Action
ec04e265-647e-56b6-8b48-479e5b1f7d91 | dropdown | Electrical Fail Action | FO, FC, FL
1f215402-4968-5151-b202-9151944b4fa6 | dropdown | Motive Force | FO, FC, FL
68e785a0-34a3-5d35-8fc4-1b0a402ae766 | checkpoint | Proximity Detectors
a6571574-2216-51c5-87cc-f29592cd916a | button | Open switch set, correct mode setting | Yes,N/A
a5c32505-2c84-5fb2-883c-dc82759dd51e | button | Closed switch set, correct mode setting | Yes,N/A
66d0472f-bc64-5a28-bdb5-47499a2c6fa0 | button | Electrical connections and certification correct | Yes,N/A
ca31728d-089a-5a86-91f8-e6fa49290174 | checkpoint | Solenoid Valve
477ffd2c-7a55-5882-b145-66e2e665aa61 | button | Operation correct | Yes,N/A
5e5836a0-2ecc-5161-83ad-45659d110dd2 | button | Electrical connections correct | Yes,N/A
1ed1de9a-41c6-55d5-9c48-622ffc409103 | button | Electrical certification correct | Yes,N/A
3689c809-ad49-5bd0-99c2-7966adc57484 | textbox | Voltage: |  |  |  | V
a9b111b0-2063-56fc-b003-48e1eab4f337 | button | Pneumatic connections correct | Yes,N/A
a48a85ea-943d-5624-90ad-a23cfcdbae12 | textbox | Pneumatic pressure |  |  |  | kPa
cf469d5d-719b-5c9f-939e-4b3f14281521 | checkpoint | Pilot Valve
f7ba09ab-1e8a-52b3-ae21-6066c26d4698 | button | Pneumatic connections correct | Yes,N/A
9e3f4bdd-0d8a-54fe-a5bd-b25a21d04ff5 | button | Operation correct | Yes,N/A
e739200f-9bd6-5986-9259-34611ad5a919 | button | Action/Lockup | Yes,N/A
d95c96d9-19e7-5920-8c36-be758c1c94e6 | checkpoint | Hydraulic Actuator
3e3f1287-83ab-5697-a097-d3fb85193daf | textbox | Working pressure
ce6ad7ab-df42-5863-9dc3-92275dbbab72 | textbox | Manifold pressure
47db2c3b-2c8e-5791-92b3-a2f611270808 | textbox | Fluid type
00b85d2f-e7eb-54fe-8746-2b6cd1a8e3de | button | Hydraulic connections correct | Yes,N/A
cfea285c-20c6-5066-afe1-e5ea2b77b970 | textbox | Regulator pressure setting
81455763-1465-59ed-9c39-72ef5c753235 | button | Pilot operation correct | Yes,N/A
3feee96c-5f87-541b-a1db-c34642a76ff9 | checkpoint | Accumulator
5fe56fca-7110-5ccf-8f3a-2b4f73566419 | button | N2 Charge required | Yes,N/A
28b774b6-e360-5287-ae20-275ef49ca2fb | textbox | N2 Pre-charge pressure
60cc1dcc-44df-567a-b2ab-1eabd920de9a | textbox | Pressure switch setting
c4bb92f6-e099-50ca-b2b0-829d0328b7d4 | textbox | Working pressure
de143b9b-52d2-54e5-9891-144af16a37d1 | textbox | Output range
d81fa3fa-09ec-5bfa-8162-7b63a087e6fa | button | Volume tank & check valve installed correctly | Yes,N/A
5bae141a-6bec-570a-8885-6c22a91756da | checkpoint | Electric Actuator
d2e1d6f4-25f5-5405-80f3-5b2f510618d2 | textbox | Voltage:
56ea04ca-b789-5764-ae95-c2a9a5e23027 | button | Electrical certification correct | Yes,N/A
82255a42-1ddb-53fb-a6a3-d64f51011a20 | button | Electrical connections correct | Yes,N/A
babce00a-1db7-5a22-b91a-4a9c1e9df755 | button | Remote operation correct | Yes,N/A
65f0b7d2-9988-5b1c-926a-12f183b4121d | button | Local hand operation correct | Yes,N/A
a27675c1-7419-56b3-a584-16fe4381ca7e | button | Torque switches and travel stops set | Yes,N/A
7d829060-f74f-56ec-b586-e00635137c82 | checkpoint | Miscellaneous Equipment
b2608af8-33a2-5723-b44f-13b93084cf30 | textbox | Description
f037109f-9268-5948-bf2c-6432b6d71b72 | textbox | Manufacturer
f217159e-30b0-5085-b0f1-0d648c1f56cd | textbox | Model No:
7aa41820-86e2-5bde-a60c-fcbbe8f5f391 | textbox | Serial No:
2e603b63-0a65-5ca2-8ae9-d1d1e046e97f | textbox | Range:
18003b78-0bf7-5e2f-9e09-b614d9233ece | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
66b9bb91-851f-562e-a7b8-bfbc7a8b6142 | checklist | ITR-CL-1-121 Instrument Installation |  | ITR-CL-1-121 Instrument Installation
ed193010-c972-513a-b2cf-5f996216c7be | checkpoint | Instrument Installation (Mandatory Photo)
1012254a-4972-5fdc-8d71-df31d7dadfa9 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
0c741fc8-02f3-53e1-ab33-06f15918df18 | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
54a6e2ff-164b-58bf-8867-c6cb5e7af121 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
8a3d1bdb-9159-5dbd-aea9-7619d3191e3a | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
60d133f8-3ef0-50a2-9179-acecbf0cbeb6 | button | Vent lines are directed into a safe area. | Yes,N/A
d050cc4f-30ba-5466-b4b8-df2714d53a47 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
7f312423-2e54-5722-97cc-15062feec468 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
daaa6797-cafb-5a0f-85ad-b402e355489f | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
d21240e8-c68e-5dae-bad1-45031304c583 | button | Instrument earthed in accordance with project specification. | Yes,N/A
2a3c1515-03df-5008-91cc-d1feedd102d0 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
ffebb209-372b-5459-8ce8-573575508c8e | checklist | ITR-CL-1-122 Instrument Calibration |  | ITR-CL-1-122 Instrument Calibration
d061d535-ea64-5fe6-81d5-c825708b16c6 | checkpoint-no-value | Required Data
41757319-167a-5cd8-aa07-c7199b9ba8d1 | textbox | Type and Size:
42e7d429-c339-5e32-90b0-dff5c5fa554d | textbox | Make and Model:
9525ed89-0474-5d44-8ff0-3f1f965963c5 | textbox | Serial No:
5f6e8c41-a08b-5394-94f3-dfaee7420291 | textbox | Instrument Type:
ef6e8d81-b952-543e-b989-618e5fc54fce | textbox | Instrument designation/equipment no
013ed506-2f7b-5333-b447-51c85cc51039 | textbox | Calibration interval
b514c3b3-3339-571b-bb05-9d42ed54d281 | textbox | Calibration method
92652948-f8e5-5c46-aac9-dc8673169287 | textbox | Calibrated at
a084b1a2-8688-51e4-824f-3472c8608254 | checkpoint | Instrument Power Supply
e3a84c82-da34-5d47-8dd7-17426f6e7f45 | dropdown | Supply type | VAC, 2 Wire DC, Other, None
487fbee1-964d-5c75-8eaa-c3d60db995b2 | textbox | Supply value:
8d9f507d-31de-553a-8602-8f512697a4b5 | button | Calibration sheet completed and attached below | Yes,N/A
4c28aeec-b4cb-5c6b-b9e8-2300245cb34b | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
8bc3774e-d4dc-586c-a938-daea54489cc5 | checklist | ITR-CL-1-123 Instrument Pre-Commissioning |  | ITR-CL-1-123 Instrument Pre-Commissioning
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
897e9c39-89a6-5075-b9aa-fde697807612 | button | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface | Yes,N/A
47f1318b-307e-5a97-a5fe-c77d0c3a625d | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
a985c65a-ed7f-54f2-9666-2867917a834e | checkpoint | Analogue Input:
850f66cd-8570-4223-bca4-d6c8d4c8bd9e | checkpoint-no-value | Analogue Input:
378a8d55-eb5f-5b57-b324-9108a86e2635 | textbox | Input range & units:
62d06d33-8cad-5af8-ae02-814d936f92c9 | textbox | Indication range & units:
9e6d1123-a43a-5dcb-af67-05f749afcd30 | checkpoint-no-value | 0% Rising
6c3091b6-dc01-598f-a533-d3e2ab0b9468 | textbox | Input Signal:
ac589bf5-4f15-5503-aa6d-71bab343ea42 | textbox | Control Interface Indication:
fcfac1e9-ea11-5c67-948c-fe55efe6425c | checkpoint-no-value | 25% Rising
e8415b3f-3ac1-50f6-914c-a30b2c89be64 | textbox | Input Signal:
7af91f29-8b47-5538-877f-01c0ce9d0f7b | textbox | Control Interface Indication:
9ecae5c3-f2b8-50c2-9b5f-723437759c7f | checkpoint-no-value | 50% Rising
b3dfbaad-7d56-5932-8ccf-19733cf462cd | textbox | Input Signal:
235fb3ca-b4c1-571b-8dab-a2b4ef0dcafc | textbox | Control Interface Indication:
29c9954d-e249-5bc1-9560-fbb01a69bbec | checkpoint-no-value | 75% Rising
abc5d65e-8e20-5c2e-b704-d6bc0a5f2e67 | textbox | Input Signal:
a230595e-ee97-53ee-8ac5-45f9654d7297 | textbox | Control Interface Indication:
ac15c64f-eee2-5f7e-ab91-e63b2c5857de | checkpoint-no-value | 100% Peak
e961078d-a3f4-5808-bd61-5427a76bb78b | textbox | Input Signal:
6c5546a6-4215-59b3-a07e-f36021f29bcb | textbox | Control Interface Indication:
88444607-51fe-5cec-a192-b792e4061f64 | checkpoint-no-value | 75% Falling
b3deb643-40c6-5199-9484-e024b9980ae4 | textbox | Input Signal:
4863c711-1488-5deb-a5b3-2c60e9183372 | textbox | Control Interface Indication:
835f9c0a-db31-5f17-9338-7e6e972233c7 | checkpoint-no-value | 50% Falling
98a2b6df-5603-5b93-9a8a-48c41df189b2 | textbox | Input Signal:
fc09dfe3-c9a3-523c-89ac-a6e00319a87d | textbox | Control Interface Indication:
7d146d2d-713d-54cf-8b13-ec9f009430a6 | checkpoint-no-value | 25% Falling
014656fd-4bef-53ad-ade6-bf4f401a9cbf | textbox | Input Signal:
b65a9234-d2a4-5ce8-96bc-3cd215943c6a | textbox | Control Interface Indication:
0ac731dc-a181-58a4-861f-0bb6758b3d16 | checkpoint-no-value | 0% Falling
a99fedbf-ba52-53a7-b23b-51f8c31c2f5b | textbox | Input Signal:
9df90556-69b2-53bc-b89c-6537f4f59540 | textbox | Control Interface Indication:
1ed325df-44c7-55d1-9f72-c6a25205dbcf | checkpoint | Digital Input/Analogue Alarm Trip Points
42de2ed8-1938-53b2-b3db-e7a83f0bda82 | checkpoint-no-value | Alarm Lo:
962425e6-dcc3-5b54-9225-40b97d1fc357 | textbox | Alarm setting
08f42cc8-e309-5ef5-9e0f-82d963771251 | textbox | Measured Alarm Point
aebb232e-e92e-5ca4-b6ec-b9f513b43530 | textbox | Filter/Time Delay
52d9be6f-a683-52ed-a0ec-d858870ce05f | textbox | Result
60ad5ba8-5e46-5008-886d-8d142348550c | checkpoint-no-value | Alarm Lo-Lo:
a1abf795-19f3-5a51-8298-ac0238d21741 | textbox | Alarm setting
fd85b330-89f1-55eb-860d-701a06f98bd2 | textbox | Measured Alarm Point
a118d913-ab14-5f51-96db-e8d2833c9ee3 | textbox | Filter/Time Delay
1ab1dc99-d556-555b-b45b-e3abd75ff08f | textbox | Result
a1e8fb6c-7d43-5228-93d0-750be74f1f5a | checkpoint-no-value | Alarm Hi:
d85a7b2b-4c84-5a58-aeac-f60b7a795eae | textbox | Alarm setting
84a67f05-f22e-5bca-8d4d-91fb178fdc1d | textbox | Measured Alarm Point
60d46a44-257f-5dac-9985-54bb773aae1f | textbox | Filter/Time Delay
c9fd08ad-30c3-5610-8e1b-2cb691acee86 | textbox | Result
a83cc59e-3e67-551a-8cb8-e7450169cc26 | checkpoint-no-value | Alarm Hi-Hi:
8698d97d-6c93-53e2-a922-f98558c5c64b | textbox | Alarm setting
27d38d77-62a4-5bcd-a195-02d0467b1ce4 | textbox | Measured Alarm Point
20462948-5499-5de0-b84e-83595ed54bf2 | textbox | Filter/Time Delay
36f57217-6430-5d43-884a-41842a0a23e9 | textbox | Result
66aabf17-dff8-5b2d-9eec-dc7c136d5509 | checkpoint-no-value | Control loop set points correct:
2a301152-a39d-59d5-becf-713d8ab86590 | textbox | Set Point 1:
5602cd0c-76fd-54b1-8d63-7518b1e2cfa4 | textbox | Set Point 2:
82912c49-655e-5895-9ec0-1823330525b3 | textbox | Set Point 3:
936ef3ac-8cea-5e81-a069-e7683e2e71f0 | textbox | Set Point 4:
29cf032d-63bf-5627-8282-9da087e897bf | checkpoint | Startup, Shutdown and Override functions
140999e7-21db-5d8f-8c3e-64acb045e0a7 | button | Control system graphic display | Yes,N/A
f92b149f-fe16-55fc-8508-4cedcd34d717 | button | Control system point display | Yes,N/A
51d22c96-e685-5d6f-a000-240b788b14d0 | button | ESD graphic display | Yes,N/A
c2dccac6-6065-55ee-821e-cfe8f4cda715 | button | Alarm Recording and Text | Yes,N/A
4a998987-8120-5498-b98d-bdc0f10f4da8 | checkpoint | Additional checks
7b1d1578-812d-51d2-8657-7f08d153646e | button | Control system display and alarms are correct as per control functions | Yes,N/A
a813ba46-f34e-5288-80be-4b607bb1c24b | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
ec7ef43b-b63a-51cb-8c64-8940affd60dd | button | Switch action verified, including power loss | Yes,N/A
895842f3-ac96-5241-b3ef-bb893805d6df | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
19513ac1-0858-54b3-8f99-b38a549be2fb | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
c515ca60-95bf-54b5-82d4-84a2ff73a660 | checklist | ITR-CL-1-124 Commissioning Instruments |  | ITR-CL-1-124 Commissioning Instruments
d061d535-ea64-5fe6-81d5-c825708b16c6 | checkpoint | Required Data
7d782c52-bbaa-504f-a90d-8788404f7508 | textbox | Instrument range:
759396e7-a65e-5b5d-bfde-afdd21fdd322 | button | Installation complete | Yes,N/A
32fdef0f-346b-52b6-b9dd-bcc8b2ea83d9 | button | Point-to-point | Yes,N/A
1d10c968-6216-5936-8f24-5d70acc19c2b | button | Haz. Inspected | Yes,N/A
ddb0305c-1859-54dc-99f4-287a62ae8a8a | button | Tag correct | Yes,N/A
2b8bbdd7-9ffc-5fad-809f-29d35a4b5514 | button | Hook-up correct | Yes,N/A
722314e4-0baf-5c5e-89a3-942255c8940f | checkpoint | Alarms & Set points
7b922954-94ff-517c-bc1c-5b267e18a853 | checkpoint-no-value | Alarm Lo
39ed4655-2862-588c-a3b1-153d512e527e | textbox | Activated:
209e76cf-9d08-579d-bddd-4ac0865c8a8f | checkpoint-no-value | Alarm Lo-Lo
651f931f-b1a4-5b08-a49d-c2cb17ce66f5 | textbox | Activated:
0e4fcb7b-fece-565a-8d4c-cce4b8905bf6 | checkpoint-no-value | Alarm Hi
74d6c4a9-b6b2-5e02-b52c-839395a706c7 | textbox | Activated:
6bf74d78-37d3-5492-82ce-337fde21a23e | checkpoint-no-value | Alarm Hi-Hi
be9d0b2e-14c9-5375-8f6a-e84a29a6505d | textbox | Activated:
10bd4618-eefc-5c44-8115-50d1b98dae65 | checkpoint-no-value | Set Point 1
be81ac26-8dcc-5ac5-8b01-d8277febae29 | textbox | Activated:
332eaf77-70b6-59b3-ae63-8b9da1ab368a | checkpoint-no-value | Set Point 2
cd52fb7d-5e3b-5a43-b82c-5acecbdba150 | textbox | Activated:
c317bac7-22a2-55aa-a7ca-ec364f340b8f | checkpoint-no-value | Set Point 3
20dcee58-d50d-5e32-b540-749665832549 | textbox | Activated:
31056f22-f138-57d2-aa0f-0e4d2f9ef078 | checkpoint-no-value | Set Point 4
957a2329-e4e4-5280-b20f-203083a54a14 | textbox | Activated:
075b6472-07b1-5c7f-813d-cd6eb5eafea3 | checkpoint | Calibration settings
408edc55-83c2-5e4f-82e9-1175ffc54db0 | textbox | Zero
56d1d0ef-0eab-5bdf-bba7-5a3960989452 | textbox | Range
e0e4a04e-ff82-5a4a-a5bd-6b458db51718 | textbox | Other (Specify)
f29fef1b-2a7d-5f18-8a8d-81d046c28d9c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1242d43c-fa3d-5dce-b762-f7be1a1de523 | checklist | ITR-CL-1-125 Cone and Thread Tubing Installation |  | ITR-CL-1-125 Cone and Thread Tubing Installation
0959a2d8-a8b6-5a53-a6c5-1b35e12647be | checkpoint-no-value | General Data
7141cf95-5dea-5b0f-8d8c-81f196d5a59d | textbox | Location:
255cbc42-9802-516c-a136-c042f69c7857 | textbox | Duty:
6887b83d-bc70-53e8-b553-80544ea43fe2 | textbox | Reference Drawings/Hook-up drawing:
f71a1a13-44f7-556b-996b-2b1398f630d8 | textbox | Related instrument tag no:
3b8c7d90-5404-50c9-9cb5-ff74c7cc5ca7 | textbox | Tube diameter and wall thickness:
7904017c-f83b-5cbf-bbee-0b2b1547e5a9 | checkpoint | Cone and Thread installation - Stainless fittings
d43e5bc0-c8bb-5532-b2df-b69f7cceeaed | button | Correct thread compatibility and engagement | Yes,N/A
39be5582-98e9-5b64-bf35-b56df54e22ac | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
11c86109-300b-5d46-bd80-5b4e8b2204b7 | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
6b9ea312-508f-5804-ace3-ed7b548bba4b | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
920b9894-e0d8-5af6-80e5-a90c1b5d34f1 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
418c3109-140f-5b00-ba6d-c39a3593e4b4 | checkpoint | Cone machined face. No defects, lines, bumps etc. (MANDATORY PHOTO)
2f419ae7-c5f8-5b75-9102-aadd65f3b4ee | note | Attach photo of cone and thread.
c671b1f1-0075-575a-a232-168cde2fc86f | checkpoint | Thread cleanly cut, de-burred and cleaned. (MANDATORY PHOTO)
6b9e5d58-35a2-5767-8ee8-64320309ab65 | note | Attach photo of collar.
33b6b064-7fb6-5c17-a57d-ab015a8f638f | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
675acade-cf00-58b2-be9e-8c885504bf48 | button | Correct Tube nut used for the right sized tube | Yes,N/A
6390f66d-ee7b-532c-a0cc-ae3ab696094e | note | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
7bcc3afc-9160-54a2-9b81-be483b83d27a | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
f354ef76-4789-5085-ad39-925286a57219 | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
dfb2e174-954a-5a61-b637-6609eb938380 | button | In service leak test performed and passed | Yes,N/A
1126d282-7850-5605-aa0d-367ec4066b64 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
ce82cdf0-99c5-552a-9572-eb505115723c | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
accaa90b-ea40-58ee-ab7f-1eb4fc813ead | checklist | ITR-CL-1-126 Cone and Thread Pressure Testing |  | ITR-CL-1-126 Cone and Thread Pressure Testing
0959a2d8-a8b6-5a53-a6c5-1b35e12647be | checkpoint-no-value | General Data
9bdca364-c6e4-5032-9956-643da41dda63 | textbox | Location:
96a72ebf-1e66-59ad-b053-72910f7c9442 | textbox | Duty:
cbf08a12-f724-5e20-8708-9376e9c32c97 | textbox | Reference Drawings:
3ffd6b5a-1297-55c2-a17b-d946fdedbca2 | textbox | Hook-up drawing:
41943411-c78c-5e38-929d-e23a499f8658 | textbox | Related instrument tag no:
b53090f0-055e-57a8-bd2f-8e79b7d37312 | textbox | Tube diameter and wall thickness:
2171e8d5-93f4-5777-a9e1-95c814f5ef9a | checkpoint | Checklist items
4cddb07c-c76a-539b-baf0-14863ebb25b4 | button | Tubing orientation as per hook up drawing. | Yes,N/A
623dbe2f-d69c-5ccb-93e7-44635f6c4d19 | button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
fb1b199d-5938-5a8b-a26f-b0107005353d | button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
f23cd556-ae2c-55d3-abac-643c35a70465 | button | Tube as per specification and hook up drawings. | Yes,N/A
76a67493-fab4-57c4-9a27-a6abb7748fc3 | textbox | Max design pressure:
6cc939ae-1c2d-5e20-b4e3-1b666eb3cda5 | textbox | Test medium used:
1c71bf2f-6b10-5fb9-aa9b-c87225790e6f | textbox | Record Testing pressure:
3661e20b-d462-54c0-9f7e-9f01d240b545 | textbox | Test pressure duration: |  |  |  | Minutes
df8aaede-7e79-54e6-9f6e-53339dd0db91 | textbox | Test leak rate: |  |  |  | Litres/minute
b50cedcc-0f97-5536-b30e-e74667a73118 | button | Chart recorder used and attached (where applicable). | Yes,N/A
7ad8258c-4c5a-5f9f-b969-c11763f0a080 | button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
b4354c34-3058-51b6-bf55-9a43cc123035 | button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
2a69bb8b-cafe-5fb6-a250-a5c95445879f | button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
9ec7e675-e0a2-55ea-aa72-182664bc922d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
866c6d15-65d8-50c6-b60e-3a3783574536 | checklist | ITR-CL-1-127 Telecommunications Equipment Panel |  | ITR-CL-1-127 Telecommunications Equipment Panel
b734ea26-8173-5b2a-9ba2-f4a76d9c2596 | checkpoint | Telecommunications Equipment Panel
484f6359-9b8f-514e-ba92-38eb94aff49f | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
19e9f9b1-d7c3-5daf-b1f0-fb51ee88b1b4 | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
12f8ffc5-c8e6-55f5-9522-76a209bd3e60 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
936ffdf6-019d-527d-99ec-4e8a7ea64003 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
012a506c-b61a-55c4-8ea9-fa509bbb8ecf | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
849f4624-9b10-50af-b750-6f5365a1266e | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
27341d97-8db3-512a-8b5e-bfa4629b0fc5 | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
512848cc-59c8-57dd-9043-e46615bf02fa | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
8c99f84b-0bbb-5acc-bb39-35d6e62b3517 | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
ceb55166-fde4-5dbd-97cf-f2ddde176c60 | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
27bd8155-5aaf-5348-b08b-d3d172ebdbcd | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
9e4c60d9-10b1-5af2-8aaf-48920f19ce54 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
def6d813-ea1c-5313-b111-fc49eecac804 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
815a165e-dbd6-5cc1-bfea-cc2299917df6 | checklist | ITR-CL-1-128 Temperature Instrument Installation |  | ITR-CL-1-128 Temperature Instrument Installation
5a8339ca-f486-54f5-95fb-e84dfef1da9c | checkpoint | Temperature Instrument Installation
40121701-d5a4-5d7b-8ca5-f5bcf7e868c1 | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
435b3ada-fb4a-5318-b7d8-e7f8b08d1b33 | button | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
1191fafb-f55a-5e82-a46c-1a722f57b6c7 | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
bf1a36c6-83ba-51b3-b211-e2e6b22ce900 | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
804640f3-5ffc-5ca7-b188-b5a50885a2e0 | button | Internal depth of thermowell checked and recorded | Yes,N/A
7763a5c3-ed16-5a59-85c6-62931a0298ae | textbox | Depth:
f4cf64b4-ecb3-598b-aa05-16a76c52e56e | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
94922c1b-4642-512e-bc43-8cbae749d22c | button | Thermowell CE marked | YES,NO
726fe10c-739c-5d4b-a353-c91634bbd281 | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
cd94768a-6a61-5a85-8c74-80e37f6052bf | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
aff5e9b0-f0bb-5825-bce5-8ff6cec3eb69 | checklist | ITR-CL-1-129 Flow Meter Installation |  | ITR-CL-1-129 Flow Meter Installation
455173c9-ff6a-5288-b65b-4c5fc763b7c9 | checkpoint | Flow Meter Installation
79d399e8-6bf1-5cf5-8726-622bba11e82f | button | Check instrument nameplate details are correct in accordance with the instrument index | Yes,N/A
cda7b0d1-4555-5c62-b89f-a442ee69f159 | button | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
ff13f8b1-514d-5390-8877-9a74428cc7b7 | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
6235fc3d-b0ef-5cc5-b169-4aef086a088a | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
6ac08eff-e464-5c4f-b8ad-bcbcac0b0234 | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
a3eb006e-3fed-5fd6-a7bd-7667a3be5301 | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
d1c16033-5856-5923-b04f-9286452fea9b | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
d9e10f5b-05b1-52b1-a51e-e01317f8a08b | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
cf3283ce-ca96-5de1-a013-6b55da6c109b | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
4a5d8526-d718-5e6d-a2ba-d4025509da1a | checklist | ITR-CL-1-130 Pressure Instrument Installation |  | ITR-CL-1-130 Pressure Instrument Installation
6543ef08-8703-5786-8c08-ea5e55da06ba | checkpoint | Pressure Instrument Installation
3551c246-6b6b-5e9e-b168-09e9da476d8c | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
9bac761e-4fd1-59f5-a25c-77efd674b87a | button | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
1a2f2ebd-21bf-59d5-93f8-de0becef9f63 | button | Instrument mounted as per hook-up drawings | Yes,N/A
0207d236-be36-57d4-a64d-492b83b4ce92 | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
ed2879d7-7bdc-55ba-88c1-b177386890a1 | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
6ce27fe2-de24-57b7-b477-4fd4ddbb6236 | button | Correct bolt size and material/grade used | Yes,N/A
87d4819e-9699-57b5-a505-c6ba0a9c6515 | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
95901383-a398-57fe-917c-498e0f9b050f | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
32276249-0f52-5741-863f-5d512f6e0457 | button | Isolation valve installed | Yes,N/A
1a781a60-bb87-565c-9929-787928f070a9 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
ee31de9e-4a23-50fa-9d7a-741ec55c02b8 | checklist | ITR-CL-1-131 Level Instrument Installation |  | ITR-CL-1-131 Level Instrument Installation
76879399-6f0a-53e6-a86a-76af925a85df | checkpoint | Level Instrument Installation
cb30df0e-b480-5026-8139-809f2feb861e | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
a3c4b616-52ed-524a-a54c-5a33cf1c7e6d | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
be629b31-5e80-55b1-8d2e-e063834710b6 | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
5e6da57c-3caf-50b2-9afd-49e3456a6a9a | button | Bolts and studs are to site specification | Yes,N/A
9af8105c-9d64-58c2-ae6f-c6aa3c928578 | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
0363c507-fc6b-5a10-9f56-544a45013556 | button | Ensure gasket and studs are used as per specifications | Yes,N/A
8b14497a-acf8-579b-b824-7b51bb902980 | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
a760aff2-422b-5236-81f7-a9621af1693e | button | Verify antenna/source are installed correctly | Yes,N/A
734d1561-7cff-5d9e-add6-f610b703003e | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
29b45421-dea1-525b-8648-a82b6ae57429 | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
1c54a465-cc50-55d1-a7ca-8a0b872e7469 | checklist | ITR-CL-1-132 - Instrument/Control Cables |  | ITR-CL-1-132 - Instrument/Control Cables
43c7b5f3-337f-5425-8176-89305ffc0c21 | checkpoint | Instrument Cable
75deae0c-8214-566e-a6cd-4514849c1069 | tickbox | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
14994549-f4a3-5430-93cb-89cc0e9db4db | tickbox | Check dressing / cleating, cable undamaged
ece2796f-aee9-5c81-ba47-8dd04b8bd289 | tickbox | Cable mechanically protected
439029a7-4320-5538-8d56-f06ab2239de9 | tickbox | Cable terminated with correct lugs and crimped with the correct die.
414385c1-2b44-5fe3-8774-9f8d725dd069 | tickbox | Screen correctly made off
12f1e79b-0574-50c7-8808-2c4f3849c703 | tickbox | Glanding / Locknuts correctly installed.
db41e706-3bee-5a39-b705-e8998c49fb8d | textbox | Gland type - from: |  |  | Haz. Area Rating
10aa8414-45c4-509b-8e17-031bd9e1679d | textbox | Haz. Area Cert Details.
265346b5-b21b-5492-ac2a-264dff32e381 | textbox | Gland type - to: |  |  | Haz. Area Rating
69e039ca-0eeb-59fa-b7af-dadd4efaf624 | textbox | Haz. Area Cert Details.
a8f71738-adf4-5f1c-8a9a-d0b3d1c6ec6f | tickbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
e81b1718-6384-533f-b7d4-bc742872d0b7 | checkpoint | Electrical Checks
132e99c5-0646-5123-916a-d4bb9e2cc252 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
6972ff00-cc4b-4ee8-b3d5-3f45a2af7dcb | checklist | ITR-E-01 General Electrical Equipment |  | ITR-E-01 General Electrical Equipment
c86849bd-b89b-4d9b-ae4f-b84b2207378a | section | Details
e435427c-5964-4f96-bd49-6ce137be7e57 | checkpoint | General Electrical Equipment
560248f0-9ed6-5709-a668-cc676f4b7f0f | textbox | Tag Numbers:
4a24f3d4-9191-5da1-a094-977fad1ce899 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
dfda4166-b99f-52ea-ab94-40b622e62a51 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
2bfc5ccc-dc8a-58e9-a138-aaf31844b7eb | button | Installation is clean and tidy | Yes,N/A
073d2a0f-a78f-5231-9ac9-3a5debcde00d | button | Mounting arrangement correct | Yes,N/A
20a793d1-9705-59ea-85f5-b6ea2df6e898 | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
ab4d1d24-06f0-5443-99eb-a5f14068dec1 | button | External cabling is correctly installed and labelled. | Yes,N/A
66617061-7c85-593a-a00d-40cfa83b48a9 | button | Check that Equipment is correctly earthed. | Yes,N/A
573f2fb5-ab2f-5e1e-9d72-a66d70532507 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
a6999ef3-1a34-5799-a93c-62d83fc27c59 | button | All spare entries blanked off with correct plugs. | Yes,N/A
def99205-d672-59c2-9cc5-6e177909798f | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
a557d976-e6ed-5ce3-90a3-4d66062e2fef | button | Conforms to Specifications and Drawings. | Yes,N/A
576d196a-232e-4093-933d-65e149fe19cc | checkpoint | Insert Photo
cfcd31d9-417f-5e99-bd3d-b52c401fb231 | button | As-builts complete. | Yes,N/A
4ea2bbe8-d298-45c1-b369-40486496352f | checkpoint | Electrical Checks
0e2f1082-d2f2-55b6-bc97-f4684deef3aa | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
f385e585-686b-4cfa-b29f-e5d64e256542 | signoff | Installed by:
3bcc0771-cfdb-4441-8bd6-78d4000c0247 | checklist | ITR-E-02B Cable Supports Above Ground |  | ITR-E-02B Cable Supports Above Ground
dc9bbd39-f066-4f8f-a6df-6f987f1fbfd9 | section | Details
012b9eaf-e0f1-462e-b067-621b072affec | checkpoint | Cable Supports Above Ground
c25f419f-93e5-5e94-a83e-149c018730db | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
406b64d5-1ab5-54e0-955d-b2b46b46fcac | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
52409092-774f-56e9-ad14-ab3065311fd6 | button | All covers fitted if applicable. | Yes,N/A
24e62584-0fa9-5473-a9f9-1faf10567bd1 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
056fa257-b077-5262-af95-edfe7ddecbec | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
7913f7c0-a4dc-5418-af2e-47f4bc00fa62 | button | Splice plates, barriers, earthing system secure. | Yes,N/A
1b3dde26-9793-554a-9385-7d356bd82f48 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
5f65388c-1475-58b9-ad0d-49268466467b | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
271b7346-567d-5c5d-a2c9-0b0acaed237c | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
181cabc5-689e-5c4f-a678-3dda35cbc742 | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
142aac46-9825-5599-bbfe-01322f79a9c4 | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
b3d6c129-2f25-570a-9b7d-d9faef430d94 | button | Tray bonded to structure at correct locations. | Yes,N/A
3026c7df-f961-59c1-b3d3-b8b44af34dd9 | button | Earth bonding continuity tested – record result: | Yes,N/A
89fe4a98-49db-5034-b040-052843ab7e58 | button | As-builts complete. | Yes,N/A
2d1a0349-3fa5-47b2-844f-f50942fca7ef | signoff | Installed by:
d2c5e22f-a72b-4548-b223-7d16cefd99ce | checkpoint | Add applicable signatures
21aff9ef-a038-4d8a-8604-7f9ef5b128d5 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
02f7b784-b0d3-43d5-b2be-ec9453341f8c | checklist | ITR-E-02C Cable Transits |  | ITR-E-02C Cable Transits
19b0fb79-6b16-4517-8f60-002a1301ea20 | section | Details
9618301a-b36f-431f-a842-2aab2be41434 | checkpoint | Cable Transits
3c5a58eb-1acb-5d6d-b74f-4df574521e46 | button | Transit frame installed as per drawings. | Yes,N/A
28a7703a-b5bc-52d1-a12e-ac5963bd8c9a | button | Transit frame identification marked correctly and visible. | Yes,N/A
541b4ec3-928c-54b4-a2c8-52ca950184b7 | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
76d7fbc6-c87f-59ec-a2e3-1f7af4fa214c | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
330385e6-223d-546c-94f2-ab56f7b69d3d | button | Rated insulation installed to transit (where required.) | Yes,N/A
22717022-a464-5f9c-a6c0-77bac04e9666 | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
6de7bf1d-0051-53e6-85ba-d81202c9ea7b | button | Cables pass through frames without strain on blocks. | Yes,N/A
19069bef-c3e2-5423-83c7-e1dde48a2576 | button | All cables identified on both sides of transit and visible. | Yes,N/A
da5fbbd4-1013-5ada-88b3-0a80e1925dc4 | button | As-builts complete. | Yes,N/A
e3a9c5da-557c-4b05-8bb6-f799e34ec1b6 | signoff | Installed by:
4a26c9ab-6e81-45df-a37f-9de5240edd90 | checkpoint | Client Representative
69173f9f-2cd6-411b-811d-5321cf97e851 | signoff | Client Representative:
a637d8c4-d2fe-414e-8534-4e47a9908c29 | checklist | ITR-E-03 Entec - Distribution Board Installation |  | ITR-E-03 Entec - Distribution Board Installation
ca6f4ebc-851a-49a9-af99-7c509e924326 | section | Details
356713ed-104e-4223-998f-51bdba894cc2 | checkpoint | Distribution Board Installation
6ebd7e1f-17d4-5bfa-8577-0c33b90c8d36 | button | Inspect for mechanical damage from freight and handling | Yes,N/A
f4abc9e3-3a67-55ea-8286-32b0ef2a3cfe | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
840bb6f5-44ee-53bd-8b3f-183437e469b7 | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
31f86cee-a8f2-5c5c-87e7-50fa1366a062 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
362bba8c-d76e-593c-bd21-8d8e165eb5af | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
c150b82e-3d67-5cf6-8794-6d3230594ea9 | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
a35a7651-1d89-55f2-8940-6cb0a0419d42 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
626e5861-a640-5855-b74e-5137f50be06c | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
d3013f7b-f8c8-5dee-b6c8-eefe9c292a11 | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
b17c05ae-55c6-57ad-bd7f-d82a4078c986 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
44eb29fc-8362-438b-87a3-8660cad00356 | checkpoint | Test Results
fd089107-10bf-5725-9e06-3bff97a95209 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
0e1c2d74-a900-52ec-9bf5-52dfc571c4c2 | textbox | Earth Continuity |  |  |  | Ohms
30979b4c-0220-52d5-a550-a70ff503f598 | textbox | Earth Bond |  |  |  | Ohms
0800d314-8c32-5c17-9b56-c58875c736df | textbox | Fault Loop Impedance, PSSC.
2ca4068c-a238-5e30-93b6-0e5d0340b7f5 | textbox | RCD Test results (1/2x I, 1x I, 5x I)
2126bd54-4380-5b3b-8019-0b18afa0a781 | textbox | Voltage and Phase Rotation
5e3456b5-ca32-588f-a474-a49b2d5367a3 | button | As-builts complete. | Yes,N/A
f1d5e748-5f3c-48f5-9426-acc4b1407517 | signoff | Installed by:
01157b8d-1937-40f0-b5c4-4d7d0b819e8f | checkpoint | Add applicable signatures
080e1b27-9cf2-4222-a486-6b180909fc6f | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
d1c66120-192e-4078-b37f-5a7b5dc5e49f | checklist | ITR-E-04 Schedule of Test Results DB |  | ITR-E-04 Schedule of Test Results DB
d0ff28dd-59c0-44e9-97b5-6037fdf771dc | section | Details
fe62beb0-2391-4fb8-9d76-f1794e1fce06 | checkpoint | Upload completed ITR scans
9641aaa9-dc77-46cf-8daf-1bbc84dcc609 | signoff | Installed by:
be19bc15-64fd-4ebd-91cc-cac5082b3207 | checkpoint | Add applicable signatures
e70a9b73-8de7-49d1-ab01-c304cb7137f3 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
2d0074df-c0ff-4b4c-9fae-795aa6f7b0a5 | checklist | ITR-E-05 - Low Voltage and Control Cable |  | ITR-E-05 - Low Voltage and Control Cable
48e1d185-4234-4fee-9371-8b976821629a | section | Details
d996e8a1-b7cc-4343-b8c2-03378b5be85e | checkpoint | Low Voltage Cable
cc9019c2-7471-5d91-a729-e9fec01d5d3e | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
03557d37-4f88-5193-801c-2fb9ab3e0351 | button | Check dressing / cleating, cable undamaged | Yes,N/A
a951a25c-ee43-5ba7-9e9b-846d0daae3c6 | button | Bending radius satisfactory | Yes,N/A
375c2283-82db-55d6-b57e-2645215f7ad0 | button | Check cable cores correctly identified and labelled. | Yes,N/A
30f120a9-9343-54ea-b9f3-bd62f7134c23 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
e229d503-5378-5ecf-a339-f4cfcef320fd | button | Check Armour / Screen correctly made off. | Yes,N/A
b424ab3b-5c1e-578f-97f7-69b79b3a4e14 | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
df093cef-ad25-5fae-bee4-aca0734fbc3a | textbox | From:
81b554fe-cb15-5e09-b692-3a4d596a08b6 | textbox | To:
7a70b6df-ab0e-5a8d-a460-255fa386bf55 | button | Glanding / Locknuts correctly installed. | Yes,N/A
d8ff1f73-1e21-5bcf-a1a2-8b1524bd409c | textbox | Gland type - from: |  |  | Haz. Area Rating
d39aa7dd-d997-5f14-a96e-cd27a6efa3b4 | textbox | Haz. Area Cert Details.
b7f4c2bb-8170-554d-8ccd-7e662996f82c | textbox | Gland type - to: |  |  | Haz. Area Rating
1ea0afb3-4e2a-55b5-b1c8-f35384849455 | textbox | Haz. Area Cert Details.
84902148-137e-505b-85a0-bcf130b2e4fc | textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
55253af8-4db7-435c-93b4-7abec3bfb1bc | checkpoint | Electrical Checks
24f91d96-8b33-5fa7-a042-6cc96c1f5049 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
b2c1d66b-90b2-4a03-a751-9b72127efe6a | signoff | Installed by:
1e541faf-8c3f-40e4-9b31-1502a575b39f | checkpoint | Client Representative
6c26375f-44ac-4214-b24d-440152e87601 | signoff | Client Representative:
e8dcdaa4-96a2-4284-9abe-5400cb019b0b | checklist | ITR-E-06 Control Panel |  | ITR-E-06 Control Panel
f3392cae-220f-449e-8532-942942f50a55 | section | Details
377808c1-ec56-4515-9614-9611db04649e | checkpoint | Control Panel
cd94d204-51ae-544c-a5df-ecbe9e1db494 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
effc1db6-375b-53a8-81ce-fb59b24d9bc7 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
c5f5f494-5575-5712-b8e9-3c4acfbb4d46 | button | Check for mechanical damage. | Yes,N/A
8ebb4f59-ee20-5d27-9411-b941e35c1e76 | button | Check tightness of circuit connections. | Yes,N/A
0cb14175-d835-5019-acc2-6bcad32b6219 | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
14787578-fefe-52cf-828a-348ad991b290 | button | Ammeter scale and current transformer correct. | Yes,N/A
c2eac609-154e-5f50-b23c-14ea176fc903 | button | Check internals for cleanliness. | Yes,N/A
592b3660-baab-593c-a798-857b00ca5f9c | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
6597578c-2da7-54f7-9e86-b27780af95ef | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
336a11a9-26fc-56db-99b2-dcac867b8355 | button | Heaters correctly installed. | Yes,N/A
67c33365-5c68-5851-a4f8-a51e732abca7 | button | Fuse rating correct. | Yes,N/A
983d1f59-a4fc-4970-a623-6bd99d129ce5 | checkpoint | Insert Photo
610ba3af-e931-52e3-a202-e861afee1992 | button | As-builts complete. | Yes,N/A
7e8e073e-40c1-427e-9f5f-cc4543a5a19f | checkpoint | Electrical Checks
3e80bafa-c792-57a9-9667-6e9ee6d3262c | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
21907058-0416-4d32-ba44-63d10e709911 | signoff | Installed by:
ead3c631-6c22-4f59-bd46-8397f60161c9 | checkpoint | Add applicable signatures
910a10ea-b696-4d5f-afc1-95380681fc58 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
02a042b3-203b-47f6-aab0-b520443ace31 | checklist | ITR-E-11 Generator Package (LV) |  | ITR-E-11 Generator Package (LV)
18e60573-9b86-4e2a-bcf7-f348a0d81516 | section | Details
80aed476-4ff6-4fa7-9642-085aa8ae861b | checkpoint | Generator Package (LV)
ae188fcd-5b0f-557a-9845-6aaf49bebf9a | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
60db0211-badf-5abc-a37c-f81e76cb2156 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
c42aef92-f1b8-5e9b-8b96-bbd171aa4d88 | button | Check terminal boxes and glanding correct. | Yes,N/A
3f8e9426-9e24-5188-be64-0beac0c306a7 | button | Instruments correctly installed. | Yes,N/A
fc4ccd13-f3a8-5844-b25b-cfcbf1d11e09 | button | Heaters correctly installed. | Yes,N/A
c5f5a8b0-4d99-541b-840a-c736f83b0d58 | button | Check unit for cleanliness. | Yes,N/A
1fa1032d-726b-57ec-8916-96f15b3e9ed8 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
722b711e-356e-512a-95e1-2bad001955b3 | button | External cabling correctly installed. | Yes,N/A
b460b037-f50b-57e6-8477-86c49b944bfd | button | Protection of live parts adequate. | Yes,N/A
e2787fd4-9c1d-53c0-9f63-34bb277e0836 | button | Main terminal box complete and terminations correct torque. | Yes,N/A
0c7725d5-87d1-5ad6-ae14-4e5b0acd1322 | button | Ensure direction of rotation is clearly marked. | Yes,N/A
b06223a4-0b1c-521b-86fd-0df03851099e | button | Check gasket and seals are not damaged. | Yes,N/A
25f3cbb6-1a16-51fa-89f5-1c1e6954c8a9 | button | Unused cable entries are correctly sealed. | Yes,N/A
fb1c0830-64a1-53bb-bee1-b2cffac77338 | button | As-builts complete | Yes,N/A
5c1e8826-a437-43c5-b45a-545ac8bd0ed8 | checkpoint | Electrical Checks
b213a15f-bb8e-5251-a6b6-472bb9eb9397 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
1f77ece9-147a-5988-b992-54e2c6e2c61c | textbox | Heater circuit insulation resistance:
b4ca1054-b6dc-46cb-90ce-100d058d9b5d | signoff | Installed by:
86cbe42f-fb05-485c-9bc9-b18264a8d9f7 | checkpoint | Client Representative
90054f21-2b53-457b-a446-738c7361ddf5 | signoff | Client Representative:
12a6119c-cbb1-48eb-acc7-4d933504eeca | checklist | ITR-E-12 Electrical Earthing |  | ITR-E-12 Electrical Earthing
d3120a07-61d9-4e00-8b39-36ccc803ac8d | section | Details
6e46845d-c14c-4010-9b2a-4372e31ef281 | checkpoint | Electrical earthing system installation
504d6eec-e8e1-5e9b-afbc-c996d0c86da9 | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
7fafc840-9cb7-531a-bfc7-095d459e4bb1 | button | Ensure that all metal work is earthed as required. | Yes,N/A
27023def-b033-5515-9341-aa5a79665c6d | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
efc4a707-81bb-5d5c-af1b-af18da1f31a4 | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
228c9de7-856d-5f26-af48-04d73a4378e6 | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
7ce88420-2422-5a80-9af7-ac323aaad379 | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
3ae213c0-2f51-5b01-aadf-2022d4609940 | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
a8e47b77-3b83-5cd7-829f-26975141f1c5 | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
12d319b7-693c-58df-92fb-ec43a87d0040 | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
fb5cf413-e9c7-54d5-bab2-f72b550562f2 | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
33912942-3bbf-5dc9-a96f-2795566580ae | button | Ensure that earth cable identification markings are in place. | Yes,N/A
72032e7c-1aa5-5b80-9d2f-eb963efb7607 | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
416aabbe-c371-5ee2-8c91-a36f76184a8b | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
fdc837e5-11a4-45c4-9b98-65ba024ab4e2 | checkpoint | Test Results
c6428e7f-e14b-5582-b9ea-8d10d5d8fede | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
5c0e88df-7c79-5932-8eb8-b8bf6f8d7a84 | textbox | 3-Wire earth test results (If applicable).
95378180-fa28-5208-a039-7c0232af3ebe | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
8b91efb1-738b-4563-b504-37de4485c5ea | checklist | ITR-E-29 Cat 6 Communication Cable |  | ITR-E-29 Cat 6 Communication Cable
264a9614-9646-461f-80b0-5b6651de0390 | section | Details
9970d7df-a92a-492b-9049-5f72506c450d | checkpoint | Common to all circuits
726b6958-2b52-579a-9766-9d969cc9b6bc | button | check cable for damage | Yes,N/A
455b8ab6-e78f-599b-99c3-740db69959fb | button | Check cable is correctly identified and labelled | Yes,N/A
70d458bf-95e5-549c-b1d7-a68e80f40441 | button | Check glanding/locknuts correctly installed | Yes,N/A
a8c49320-2274-5b3d-8bde-5af67c1776ce | button | Confirm cable routing and segregation is correct | Yes,N/A
c37de2d9-2860-553e-8ec6-6c7fbf218e0c | button | Confirm to and from destination as per design. | Yes,N/A
ec479eb9-35d8-4d3f-886a-765af981c754 | checkpoint | Data Circuits
2d422b14-e0e0-5715-9f2a-96f3657cc968 | button | Check cable terminated with correct crimps | Yes,N/A
f3db4d9e-dc03-5f41-ab5d-0ac173190f1e | button | Check sheild/screen correctly made off | Yes,N/A
225c42d2-ad9c-5c0a-8aad-0588b7656834 | button | Check Cat6 end-to-end certification (outlet and cable) | Yes,N/A
14c14d58-0fb1-4d23-9455-ee7f63e5cac7 | signoff | Installed by:
fe82d385-85ce-4c3b-a494-79b861dcddb4 | checkpoint | Client Representative
97488435-783a-4f59-9dae-a03a5a37cabe | signoff | Client Representative:
f41a07b8-c1de-4ef8-b930-bad48906e766 | checklist | ITR-E-32 Battery |  | ITR-E-32 Battery
706ebd01-c4f0-4e98-84cc-fa24e93f2133 | section | Details
42e04d2d-63dc-4732-9240-4dea2966028c | checkpoint | Batteries
c0d25c5f-b900-5cb5-a2c7-3e26319045fc | button | Check equipment and nameplate details are correct in accordance with the data sheet and drawings | Yes,N/A
d0bc9591-fc60-5fff-b13c-3b09b527822e | button | Transportation packing and plugs removed | Yes,N/A
fdfddfa4-48a0-5fe8-9082-852a18ebd068 | button | Battery cells correctly rated and numbered accordingly | Yes,N/A
890cb04c-9dfa-5901-808b-274732f30279 | button | All cells correctly mounted, links tight and shrouds fitted | Yes,N/A
668ed837-ac18-501d-ab22-6338037804a0 | button | Internal cables correctly installed | Yes,N/A
56d50aa2-158b-5cd1-8974-7ca4e9689a2a | button | Protection of live parts correct and adequate | Yes,N/A
6c2612cd-b36e-5ce8-953e-38f12c024c78 | button | Electrolyte level correct in each cell | Yes,N/A
0dae0744-9ddc-5715-bc8a-2840d0e4cd25 | button | Check specific gravity in each battery cell | Yes,N/A
bfd55588-6923-5e7f-8305-05ef660ad9f0 | button | Check cleanliness of cells and battery racks | Yes,N/A
f6eb6a55-f6ba-55d4-accd-b2303455496e | button | Verify approved grease applied to battery terminals | Yes,N/A
c88911dc-7ace-5adc-bf23-aa80a8d592fb | button | Earthing correct and tight | Yes,N/A
9eecb3a3-da02-5523-b547-e0522f134a0c | textbox | Verify polarity correct per drawings and record voltage
75fcae0c-7ad6-5742-a68b-9fbc18f87393 | textbox | Perservation as per supplier instructions
53a61936-dafd-58c6-8ca9-fe6c69ca0f0e | button | Leave equipment with any isolators and/or circuit breakers switched and locked in the off position | Yes,N/A
60ba0336-9b1c-46eb-b474-c69a0a906b94 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
3e3fa6aa-542d-4911-a75e-d930e1393147 | checklist | ITR-E-34 Low Voltage Switch Board |  | ITR-E-34 Low Voltage Switch Board
d5357422-c26a-4968-874e-85d7b1659f4b | section | Details
c0d5c4e8-937d-42b4-8629-19a9f2a6a60a | checkpoint | Low Voltage Switch Board
376b1409-a59d-5424-81c7-5f9792706820 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
45f01c97-c3e9-537e-b5ee-d316f3765598 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
9c4a3238-44e6-5187-8c5d-90401a5d2111 | button | Check for mechanical damage. | Yes,N/A
74b7a6fb-70a6-5259-8dcb-a331281f4a4d | button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
276e3a6e-5578-5239-988a-a8b3b4173a16 | button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
800222b4-c83f-5b9e-8e5e-663792518175 | button | Phase identification correct. | Yes,N/A
e1738460-99ad-51f4-aede-f95e4658708f | button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
57ba15ee-2d49-5c45-89ad-31845a7df705 | button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
4594140c-586e-5da7-8817-85846711226e | textbox | Bus bar alignment to manufacturer's specification and connecting links tight to specified torque.
58740c50-b55a-535c-8c52-898a987815a8 | button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
950f2a70-18a6-57a1-8de0-f96e6c0f1f6d | button | Instruments, indication lamps and interlocks correct. | Yes,N/A
346225e0-2404-5801-bcd8-ae226bf17df4 | button | Ammeter and current transformer correctly installed. | Yes,N/A
6e8f766e-11ad-5a51-bb0b-f8d076c3055b | button | Check internals for cleanliness. | Yes,N/A
75d3a77c-c044-5f8e-91cc-b85af81edcdf | button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
ca61d473-a9ff-5ead-a432-7499be4fd179 | textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
a7f4edf4-9ae7-5d96-9981-124c043a65d0 | button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
5d1d6b18-7d59-5b2c-88b9-c0b2a7186edf | button | Unused cable entry sealed. | Yes,N/A
24651238-80bc-5dd0-9891-d247075e69f3 | button | Heaters correctly installed. | Yes,N/A
e2747c9e-613a-5668-ada5-8254e470aef7 | button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
e692d9e9-e884-4f28-b719-7d63c877cb0a | checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
078b0677-9d36-5dbe-bddf-5ad91831d239 | note | – – – – – – – – – – – – – – –
cc160a8e-9ba4-52b3-ba16-8d3067406322 | note | System KV ¦¦ Test V (dc) ¦¦ Min IR Reading
f3ab9a84-d171-500e-8b23-7a702c51324b | note | – – – – – – – – – – – – – – –
19ae88f1-1c3a-50d2-9e75-2e1616265925 | note | < 1.0 ¦¦ 500 ¦¦ 10 MΩ
8d31d36f-d294-5071-b865-8055c6610061 | note | < 2.5 ¦¦ 1000 ¦¦ 50 MΩ
a40437e0-f7f4-5c0c-b9d0-4e65c2eabaeb | note | < 4.6 ¦¦ 2500 ¦¦ 100 MΩ
a256343f-56b9-596a-a07d-af184efed220 | note | > 4.6 ¦¦ 5000 ¦¦ 250 MΩ
c4c72bba-047b-5d7b-a96f-84c0634c4b2e | note | – – – – – – – – – – – – – – –
a5a6bbae-c13e-5307-935c-b0a5e4bac477 | textbox | L1 - Earth |  |  |  | mega ohms
e62081aa-1773-5aa1-9d46-3fa76ff65432 | textbox | L2 - Earth |  |  |  | mega ohms
be7a9d52-7387-5e03-9a12-28c9742dd016 | textbox | L3 - Earth |  |  |  | mega ohms
7a4764a0-26fc-576a-baa3-f34df765989a | textbox | L1 - L2 |  |  |  | mega ohms
ca25ee35-e193-5595-8eb6-35629ac9ef6f | textbox | L1 - L3 |  |  |  | mega ohms
156644f7-a79d-5b39-9cd3-960569d78ddc | textbox | L2 - L3 |  |  |  | mega ohms
944f866a-3b77-574b-9e29-da81a2be2f02 | textbox | N - Earth |  |  |  | mega ohms
687a411a-49d7-48c1-81ca-a5a69ec1fccf | checkpoint | Insert Photo
51221cef-f492-4c77-86f1-90cc8e880c0a | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
f308d4a3-59de-429a-a170-7c6ebd4cc455 | checklist | ITR-E-40 Bus Bar |  | ITR-E-40 Bus Bar
7603c155-c052-4767-9f7c-82f9c21f05dd | section | Details
d44cffb4-eca5-429f-baa9-7033dbb91250 | checkpoint | Bus Bar
7ed210d3-1a41-5cc0-9f69-eefb65896f53 | button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
c1176ff6-c254-5816-8d78-3a7273f71537 | note | Please attatch photo of Bus Bar
b5a61714-84d5-53c9-a0ce-606d8647688b | button | Bus Bar alignment is correct | Yes,N/A
1e2949ac-9bf4-550c-a34f-7afdb3e07676 | note | Acceptable Bus Bar Torque Settings:
e031b357-7e19-5dae-ad07-4e261c5f8be7 | note | ○ Bolt: M6 M8 M10 M12 M16
889e5f26-af09-5289-a6fe-0927ec9d2939 | note | ○ Torque: 10Nm 20Nm 30Nm 40Nm 60Nm
e9aa4bb3-bac9-5741-9ef2-d83520c239bc | button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. | Yes,N/A
a8d83e34-ce58-5d3e-89e2-bca2207b8246 | button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
3c1408d7-785d-5eba-ac38-0b057de37895 | button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
dfd9f0a8-b5ea-57e2-9562-62741aa898da | button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
9b429f68-113a-5c7a-9e1e-cdf6db6d843c | textbox | Record the total number of bus bar joints.
d3b06dcd-fcbe-43ce-b399-0f8d2209eaaa | checkpoint | Test Results:
fef61f3b-1fe3-5cc8-b795-a34b35e6b6a9 | textbox | Results:
d3104c94-3f71-4c91-bae3-33c874799ef2 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
c7096cbb-1ea4-4162-8bf5-c56e7cbdda04 | checklist | ITR-E-63 Cable Lug Installation |  | ITR-E-63 Cable Lug Installation
d3324efc-130d-445b-871b-ae838aa4d51b | section | Details
bfb1076c-aecc-48d1-97c3-780f5c1bd3bf | checkpoint | Cable lug
9f94dadc-4b49-5f4a-be87-7fe995f8bb12 | button | Appropriate lug for cable size has been used. | Yes,N/A
31a8c122-a7ef-532a-863e-a7a3ef821f44 | button | Lug has been correctly seated with no loose copper strands outside of lug. | Yes,N/A
3357e83c-8b38-5926-bdbb-da8cabb89018 | button | Lug has been crimped with 60 tonne crimper. | Yes,N/A
77be2dc7-7b10-5b37-b65b-6f0a195071b9 | button | Joint sealing paste has been correctly applied to the contact surface of lug | Yes,N/A
23568835-fc46-4f5c-a84a-20c554d316a4 | checkpoint | Bolts
3c47376b-a1d1-5a0e-a851-0fcdb689a87b | button | Bolt has been torqued to manufacturers requirements | Yes,N/A
3e6c4b98-f0d8-588d-9d86-791e41e79d93 | note | If no manufacturer torque spec, use torques below. M8-20NM, M10-40NM, M12-70NM.
0922fbdd-99f8-5f6f-a1ba-17e566e38be1 | textbox | Manufacturers torque requirement (if applicable)
f3cf434e-ff59-4b45-a32a-2135b8fd81fd | checkpoint | Test Results
c7871057-6845-5390-9eed-90a1390818cc | textbox | Continuity test results
2a324fef-3220-5f31-8900-2950bfd6f20d | textbox | Ductor test results if applicable
3f6ecdb9-140e-4d4e-b932-7d848e2887b2 | checkpoint | Test Equipment Used
1fc40d17-7306-5b95-bece-d7ec464f6d06 | textbox | Description
5e8dcd46-2df8-56e3-af1e-3a79ca205942 | textbox | Manufacturer
839b3f9f-a253-53e3-a4ef-2a03d73d537f | textbox | Model No:
fbd631b5-23c6-5491-b3d2-ac1c87e2783a | textbox | Serial No:
5f385a88-7dbe-4911-bcc5-a7f18caf812d | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
d5441f36-8607-44ea-be02-a13cdf362a33 | checklist | ITR-E-64 General Lighting |  | ITR-E-64 General Lighting
b00039bd-c869-4111-a042-94e881fc24df | section | Details
934d421e-9310-4d07-a80f-6901ad53b1c0 | checkpoint | General Lighting
6e20103a-063e-5fb3-a87d-d636deacc921 | textbox | Manufacturer:
c0aad561-2557-58eb-a1c2-e2a994a9d2d4 | textbox | Model No:
36b42b30-f2c3-56a2-b079-c86645038149 | textbox | Serial and Tag Numbers:
494b8d01-3a47-5a7e-83ec-401136103337 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
bb35f644-b763-5166-8da1-87685ec77747 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
1e79a8eb-6079-5c39-8bd3-4b9bc93d48be | button | Operation of emergency lighting fixtures checked | Yes,N/A
43973b54-21d2-506b-88c0-7222e3bdda31 | button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
9b19254f-38ab-5b77-9088-73b8644b0cde | button | External cabling is correctly installed and labelled. | Yes,N/A
f0871091-5d4e-552f-b25d-846cbed1a3ec | button | Battery run-down test per manufacturers specification | Yes,N/A
08b68945-a4ca-5259-8dda-f5eecbb60375 | button | Power / load balance on distribution board checked | Yes,N/A
217e6dc3-e098-5015-94b6-27f2e3f7be90 | button | Operation of remote lighting control checked | Yes,N/A
30f795d7-54fe-584e-8c7e-d73c93a8038d | button | All spare entries blanked off with correct plugs. | Yes,N/A
92ca2b0b-7749-5e72-ba97-63a47d6390aa | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
0efa85dd-92f7-5315-9f4d-8a847f6790a9 | button | Conforms to Specifications and Drawings. | Yes,N/A
88cc0aff-01cb-5365-81af-83f788e0c777 | button | Insulation resistance of final sub-circuits checked | Yes,N/A
23588799-0979-5ba6-aa53-c48d979741ee | button | Operation of photo-electric cell control checked | Yes,N/A
cbf991da-dc9b-5936-a863-016f8529920c | button | Lighting pole is adequately earthed | Yes,N/A
e7295d81-271f-57c9-bb66-80033a677c62 | button | Circuit ID fitted to all light switches | Yes,N/A
6290a301-b1e6-5dd9-ab8a-04ffa773840b | button | All fittings correctly labelled | Yes,N/A
4ab2b3c9-92a4-5c58-9b6d-3b89097d7e56 | button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
3bd17a37-28de-4abb-885d-5987d475e35e | checkpoint | Insert Photo
c57e61fc-6ff5-5a67-b792-afec37634653 | button | As-Built drawings completed | Yes,N/A
37f57417-9078-40e2-9fe0-9a2714a4be10 | checkpoint | Lux Levels
d756e3a6-baf3-5c40-b344-fc8c1ce75b09 | button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
3abcc03d-eab0-5bd7-bea6-423c635cc524 | textbox | Lux Results:
cc1537b9-cc06-4636-8dd0-03ec78c99de2 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
0a03751e-92e8-43ae-824a-ebbeda58b5f9 | checklist | ITR-E-67 Final Checklist for PPR |  | ITR-E-67 Final Checklist for PPR
778dcc19-1caa-46af-a4e3-fd50661049d9 | section | Details
48d0d03c-759b-4e16-936c-69056c90e019 | checkpoint | Interior Checklist
f604db2f-9467-5b4d-9270-27beca1d8ea2 | button | All floor, wall & ceiling penetrations sealed. | Yes,N/A
bc3f6ca8-7873-51c0-a6b1-837c0a6af967 | button | All equipment has been installed | Yes,N/A
4ce9cb78-357c-5848-bc81-de29ee6036cc | button | All loose items in panels have been secured or removed | Yes,N/A
4ab1de8f-d300-59da-b103-71d79beee36c | button | Illuminated exit signs installed & operational | Yes,N/A
700ca5a3-a6e0-5f6d-8416-d4811a020751 | button | All doors and locks operational (including emergency) | Yes,N/A
4f6ccb11-8e16-59c9-a7df-24343c0ab52d | button | Ensure each cable has an ID tag | Yes,N/A
3d12f241-71b8-5cb7-a588-e2c23a48f650 | button | Distribution board legend inside door | Yes,N/A
fbcb1de9-27a2-5a99-99e4-e81c7d8136fa | button | All appropriate signage and labelling are visible – warning stickers | Yes,N/A
58950d25-9b88-5d63-886d-35741ff0dd90 | button | Panels and boards have appropriate ID tags on exterior | Yes,N/A
7eb8d49b-060a-5110-8f1b-ebe5bc947ca3 | button | All doors secured through secondary means, e.g. taped shut or tied to gland plate | Yes,N/A
fa922488-e8dc-51cf-b6ee-728633a93128 | button | All panels and boards locked | Yes,N/A
466c1001-5c2a-5b84-9554-e535fceaf289 | button | Room Interior is clean and suitable for presentation to client | Yes,N/A
d75d4b1a-80c0-47ed-a024-af838e41109b | checkpoint | Upload photo of interior
c502c7e4-385c-495b-808a-edbaf150af2f | checkpoint | Misc Equipment Supplied by Entec
e7c7d68b-2291-5651-92d2-1d6e41eeb209 | button | Fire Extingishers x2 | Yes,N/A
1c9ae59f-cac8-5d7a-b7de-63e7848c297a | button | Fire Extinguishers are bubble wrapped and safely secured for transportation | Yes,N/A
4d13404b-3fe7-5cda-9b5b-3118e2827b2a | button | First Aid Kit | Yes,N/A
ef76ca81-56f8-530b-a901-b4501e0a14bd | button | HVAC Controllers | Yes,N/A
619435ec-cb2a-5399-82ce-4a6f1434d8ed | button | Desk and chairs | Yes,N/A
519e0c65-d32e-5995-a485-8ef5d257d4b4 | button | Equipment cupboard | Yes,N/A
d894d595-df00-514e-8dff-e693c02a4149 | button | LV rescue kit | Yes,N/A
07860bcc-ec1c-54c7-b487-64aec6d575d5 | button | Emergency Eye wash station | Yes,N/A
7d7911be-66f1-4b04-8328-a9481c9e35fc | checkpoint | Exterior Checklist
88ab7367-c74c-5fcf-841c-04fbef65d9f2 | button | Container Exterior is undamaged, e.g. paintwork intact | Yes,N/A
de8d075d-9b52-5a8c-ab0c-5d83ee6815f1 | button | Earth Boss correctly installed and connected | Yes,N/A
fd0cdb13-2adb-546b-a845-18bbd0daae99 | button | Stairs have been verified to correctly suit container | Yes,N/A
41354397-7162-56c6-9193-0f2ac761fe41 | button | Stairs are available and ready for transportation | Yes,N/A
506f4269-8c62-4127-a069-683fae4e38ef | checkpoint | Upload photo of exterior
cb11a071-95df-4a23-8526-6d038c359520 | checkpoint | Final Checklist
d066e25b-b360-5114-858c-9dd87420922e | button | All other ITR’s have been completed | Yes,N/A
8f51f15d-54df-5ad1-b095-9ec25248f3b5 | button | As-Built drawings completed and signed off | Yes,N/A
bca9d4cd-c9b4-5763-a222-d5a5ee69db74 | button | All keys available handed to client representataive or project manager | Yes,N/A
14ca4fb2-b42a-4a2d-abe0-826c04832e07 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
0403cefa-1cdc-4d05-9661-38db8c0423ed | checklist | ITR-E-68 HVAC System |  | ITR-E-68 HVAC System
86d5ae6d-872a-4e6f-9442-86c277f2d210 | section | Details
df7819a5-5d53-40a8-801b-20c944b1a519 | checkpoint | HVAC System
8d264779-8e63-5604-961d-aa52a6b6b58f | textbox | Model:
85c93f6d-8f41-5231-8b25-50624e26d04b | textbox | Manufacturer:
c5a346dd-2c44-5bb5-9289-a67ce7fe367a | textbox | Serial and Tag Numbers:
c7fbd689-b837-5e40-b6cd-685bf1dd5157 | button | No mechanical damage and paintwork is in good condition | Yes,N/A
c748ec55-a9be-554f-b6ff-11c0eefc1810 | button | Operation of units verified | Yes,N/A
b71ff474-1415-5f60-9dab-1134a230ffa5 | button | Mounting arrangement is correct | Yes,N/A
e386b73c-33c1-5f78-a56a-d801daeb0a4f | button | External cabling is correctly installed and labelled | Yes,N/A
2a7721b7-b092-5123-9cbb-93b1f0641adc | button | HVAC unit isolator is installed and operational | Yes,N/A
0ff49cd1-eb72-57a0-ae39-09a1b7cf9405 | button | Remote holders are installed with remotes inside them | Yes,N/A
0c143930-5ec4-5936-a758-8373c692bf92 | button | Units are labelled with appropriate ID’s | Yes,N/A
be1e61ee-512d-5366-8677-89babd5a9cc7 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
93466c2f-77a4-560f-a75d-ee8e39183699 | button | Conforms to Specifications and Drawings | Yes,N/A
141822c4-7f54-56a5-8e64-35eaffe5503f | button | Any applicable control system configuration has been checked and is functional as per design | Yes,N/A
06597e95-e860-4d09-a2ae-777d621a225e | checkpoint | Upload QA pack from HVAC installers
a2033082-7913-5b6d-a954-1462ab71edfa | textbox | Confirm ENTEC witness of installers testing
438a3d50-9a36-4a08-a4b3-ca37b00ce3a8 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
ede5545f-f238-41e4-aca6-728b36b65e37 | checklist | ITR-E-69 Fire Detection System |  | ITR-E-69 Fire Detection System
950e054a-cc43-48c7-8ee2-135c2bae9e73 | section | Details
c4ad3eaa-d877-418b-a12c-fa3bb67436c6 | checkpoint | Fire Detection System
fb39413d-17f0-5db5-9bf6-098cf19c9392 | button | Fire Panel ITR has been completed | Yes,N/A
5d128b8b-8c6a-53f9-9555-fbcbc50c1e02 | textbox | Tag Numbers:
c6442bcb-b938-5b34-aa1e-740b0027de74 | button | Smoke alarms have been installed as per specification | Yes,N/A
0b92fcb0-56ea-52ad-ad3c-33ab301dcffe | button | Smoke alarms are ALL operational | Yes,N/A
e5548a1d-5b78-5d84-ab3a-d097d232c2ce | button | Alarm speaker has been installed per specifications | Yes,N/A
756f8c22-edeb-56a6-83a8-71908b805f25 | button | Alarm speaker is operational | Yes,N/A
8286261d-7c57-5026-8500-bba05f3dcdda | button | Fire alarm beacon has been installed per specification | Yes,N/A
19661363-bbe0-5b40-bbd2-0f3aabb3a201 | button | Fire alarm beacon is operational | Yes,N/A
06b711f5-258e-54ce-a709-5b912bfa5805 | button | Manual call point has been installed per specification | Yes,N/A
6c47160a-c016-5cec-a136-bc27e9737b2e | button | Manual call point is operational | Yes,N/A
76e9f142-9803-50fe-826b-0bfd1ad4eae8 | button | Installations are all unobstructed | Yes,N/A
a0c82a11-b97c-59f4-b8b1-6fa372984049 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
df98c795-499b-5b78-bc72-57b030e79ce6 | button | All installations have identification tags | Yes,N/A
a6d51a1a-4aac-5d7f-ba4a-679c248fe45a | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
215219d9-c304-5e6c-8d96-de2f1053f8fd | button | E.O.L has been installed as is operational | Yes,N/A
0bd33b8b-7396-5451-a6b0-5bab5151d855 | textbox | Other fire system installations have been installed correctly:
9a50aec9-246b-5a2f-8624-b98a00a69d22 | button | As-builts complete. | Yes,N/A
559e6df7-4299-4be5-b31d-994ed0310016 | checkpoint | Functional Check
e715b970-98ae-5ca5-b8db-5a654a37d770 | textbox | Selt test:
135f52bf-34d6-57fc-9055-5719c976b8ed | textbox | Alarm Operation:
670014ce-530e-5d3e-a422-efb9e5331d7f | textbox | Fault relay operation:
6876db35-595b-5949-9b6d-89fec9117817 | textbox | Measured output (clear path):
2024c168-da8c-588a-a7fa-0c743b2e0399 | textbox | Measured output (blocked path):
a95c56ff-d902-5471-b05f-7d701555943c | textbox | Measured output (filter in place):
29b0b1ba-3e09-4875-9aa9-2b2e8ef61cc9 | checkpoint | Upload QA pack from fire alarm installers
21774a32-c3cf-5d1c-85c5-195914db8e9f | textbox | Confirm ENTEC witness of installers testing
d7c41952-e640-40f9-933a-f708c493b038 | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
664496ed-d7c0-4437-a3eb-757c421e8297 | checklist | ITR-I-21A - Instrument and Control Cables |  | ITR-I-21A - Instrument and Control Cables
4f25b057-6dd4-4752-a31c-3e4db0596f55 | section | Details
bf96ea53-d0b3-4f74-84ad-e6e8bbf604d3 | checkpoint | Instrument Cable
a9860dc8-ea63-52ed-a622-7a72656980bd | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
dd71f274-d196-5633-be0e-13db9572b261 | button | Check dressing / cleating, cable undamaged | Yes,N/A
0ce53041-43f8-52f1-9415-e4d264d607c9 | button | Bending radius satisfactory | Yes,N/A
440abb7b-87ae-5e09-b389-ca7523cd8bad | button | Check cable cores correctly identified and labelled. | Yes,N/A
ee65d5a3-1169-5c21-b2de-22de2647a5d8 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
2d55bbcc-2dcf-5c52-a080-1bc5dac977c2 | button | Check Armour / Screen correctly made off. | Yes,N/A
cf5830d4-b733-5990-871a-942c9f4efac2 | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
ee570335-4161-5b79-b58d-0fa426bf0fda | textbox | From:
45232451-c6b7-55dc-9c00-570c25561f50 | textbox | To:
c2a642e6-c096-57ca-b164-6f3c4997a3c5 | button | Glanding / Locknuts correctly installed. | Yes,N/A
eba8e29d-0397-54ed-882c-afb0bbcca47d | textbox | Gland type - from: |  |  | Haz. Area Rating
6357e8b7-31cd-576f-ac9c-368882a91bb0 | textbox | Haz. Area Cert Details.
903a836c-cc42-59c9-b084-41b351c27d46 | textbox | Gland type - to: |  |  | Haz. Area Rating
43c4f0d3-6273-5371-b27a-ecfc5f6f2180 | textbox | Haz. Area Cert Details.
568fed47-e58b-5908-896e-f4fc43803186 | textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
d7070e1c-6648-406e-9f94-918975548945 | checkpoint | Electrical Checks
dc6b4329-d9c4-531d-8855-35c23f62b248 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
579ace85-0271-4d77-b85e-179b55667283 | signoff | Installed by:
c1620672-bbd7-4d76-b85a-7c7c6e6f07fa | checkpoint | Client Representative
020453db-9099-4c3e-bfe8-553d7cf4df50 | signoff | Client Representative:
0c5fb84d-f269-5543-8ae1-fd241e38c3be | checklist | JHA - Job Hazard Analysis |  | JHA - Job Hazard Analysis
1dd72c41-b476-54ec-8ebf-cab6567b715b | section | Job details
90129915-30b8-43d2-9129-df0debe8950a | checkpoint-no-value | Job details
9121b653-9465-5c94-8e98-616d3720b083 | date | Date:
2296b6cd-d4f1-5691-8da3-a529becb34bf | textbox | Permit No.
8c3c490d-c825-5522-bdbc-0b806270bda3 | textbox | Job No.
b79ea938-c5ce-52f8-af36-c62c2f65c8e3 | textbox | Site
e10cb77a-6c27-5a76-995b-93e170d648e0 | textbox | Activity Location
72676fca-63ab-5aef-bc4e-64505c74da15 | textbox | Asset:
2f2b1683-9a8b-5c8a-84d5-4dade0dd5aa0 | textbox | Work Details:
d0e2da1e-7bc7-5faf-bd9c-add02d8a5915 | section | Prompts for Hazards - Mark all that apply.
9c216722-725f-4ef3-902b-5c25d774b48c | checkpoint-no-value | Prompts for Hazards - Mark all that apply.
e2e74f39-287a-52bd-8eca-eb140dc9cf2a | tickbox | Sparks/Open flame
2acfc571-e5a6-505c-ac2b-eba8970a62d4 | tickbox | Disabled safety device(s)
65f6238a-90cd-56f6-ad6b-0554edd0bd36 | tickbox | Uneven surfaces
f9e713ed-53fd-5dc5-929f-d6ff97eeecf0 | tickbox | Fatigue, over-exertion
24e995ec-3dd7-569e-b330-0578c5373bae | tickbox | Crane movements
01452f54-e4bd-5c7e-8ec0-ffa875e8501a | tickbox | Moving/Rotating parts
1f7273b3-8cb8-5054-9bbf-90013ef12dfc | tickbox | Remote area, working alone
1e00237e-3a56-527c-95bd-1af4f5c47fa6 | tickbox | Conflicting work/SIMOPS
48550d8d-c109-5c4c-9a7d-ed410eba740f | tickbox | Electrical arc flash
d3c0a2b4-04b7-5bc6-aef3-4ca1c2480940 | tickbox | Sharp objects/materials
f9d836e2-dc1e-51ae-a045-3e021201afe1 | tickbox | Restricted/Difficult Entry/Exit
f0c52d3f-bfd4-53c0-92dd-c40489c22c79 | tickbox | Overhead obstacles
7c761f22-d173-52dc-8223-bd1285cc4716 | tickbox | Ignition sources (other)
3272747d-9450-5da3-a2ac-faa787d2363f | tickbox | Access/Egress
866f2e8c-c205-5d58-8086-23ecb0668fb0 | tickbox | Water body
d3e0555a-b9f4-5c0c-b061-e01105e6b7d3 | tickbox | Live equipment
24ac8cbf-ef66-53d5-a5ce-8bcbf39c061d | tickbox | Slippery surfaces
a3b30d7b-ec59-58ca-9313-26d2c562f387 | tickbox | Suspended loads
98b1bf54-a699-528e-821a-322c9c2430da | tickbox | Hazardous substances (chemicals)
22f019ba-6ada-5889-82f6-57f72a23a014 | tickbox | Use of non-intrinsically safe equipment
e3dc92c4-6d8c-5806-9d79-ba9d7375189c | tickbox | Weather extremes
317ef129-b4f2-5978-a01b-dd9b3f7ee83c | tickbox | Moving vehicles
789348a6-324b-5e45-98b9-5df2ad640f56 | tickbox | Task related noise
d4e3a79f-63f6-53ac-a71f-8f3f6f7034a1 | tickbox | Engulfment
f77e1ae9-20bd-5d76-b6fe-db40018c1738 | tickbox | General waste
bfa762a9-8535-532c-9647-bd72e4369d72 | tickbox | Hazardous waste
3f775ada-8d29-5732-8d34-4393bf241882 | tickbox | Hazardous/toxic substance, fumes, gas
6d0bf608-f379-595e-bf82-0b824ac63501 | tickbox | Flammable materials - Gas, liquids, solids
34bd77ea-7899-5601-b0fd-d9b499ba4ac3 | tickbox | Reduced visibility, lighting
fb4bb6db-ab81-5c66-b884-cb3f83b3f055 | tickbox | Electricity
3c73deb5-614d-59df-aa2a-6bc6c5952c80 | tickbox | Static electricity
337fec5f-a0d8-5f8b-bec4-6af9d689ac55 | tickbox | Work at height
317be1f2-c61e-5d51-9f28-b1926070f1fa | tickbox | Underground services
14ec678d-6ee2-5bda-a8e5-9a125d230adf | tickbox | O2 Deficiency/Excess
8303cc09-1e9a-5772-836c-820f27c974f5 | tickbox | Temperature extremes
82a98376-7688-5830-87bd-11ec437ec37c | tickbox | Heavy objects
39972442-f325-5a1d-93e7-200899637b63 | tickbox | Radiation
4f4b68b1-b454-55a0-a219-1a2333da1520 | tickbox | Potential energy - Tension/Compression
ff1407f6-56d7-5d5f-b604-0a466c33788b | tickbox | Flying particles/Dust/Objects
35a7f122-ad6a-5594-9946-aba2eb678cba | tickbox | Vehicle entry
5c89e163-bce5-5049-b6a2-5e1ebad30bfb | tickbox | Exposure to process temperatures.
bb7578a2-4875-54de-afed-194a7e08db79 | section | Prompts for Initial Consequences - Mark all that apply
75e38327-3706-4cf9-84cd-7bdab2981357 | checkpoint-no-value | Prompts for Initial Consequences - Mark all that apply
00f19fe5-1ad2-53fd-8229-8c082a6bd8bc | tickbox | Falling/Dropped objects
c7c51e4d-394e-5bb3-9043-2690d397d2d1 | tickbox | Fall from height
5fc58abf-df57-5cdf-b4fc-b936b095b1b1 | tickbox | Trip/Slip/Fall
963fbd82-7281-5cb7-b204-586311d1a02c | tickbox | Gas release
35caaac2-10b3-53bb-9464-4f613176c840 | tickbox | Pressure release
a8380d82-74a4-5f0f-8446-51917018e112 | tickbox | Struck by object
8b925c2b-16c6-5bff-a427-8a4f2cce1558 | tickbox | Exceeding tool limits
855f5e64-7af0-51fe-8436-0fda03120d74 | tickbox | Overloading people
51b43355-9c5f-57c3-8d84-1d991669a3d4 | tickbox | Unplanned shutdown
1c3f2082-961c-5c6d-b286-218a65f1a12d | tickbox | Exposure to O2 deficiency/excess
742ffc11-e2e1-556f-9da6-d85cdf6ab0c9 | tickbox | Exposure to hazardous substance
3c76c8a8-0ec2-58d3-b890-4b9f9c07f07c | tickbox | Entanglement
17cab252-ff5d-5afc-8c9f-0291ff00b395 | tickbox | Flying objects
545a0a83-f1ae-53ae-a51d-3559eee6d18e | tickbox | Loss of control
7c4c484c-cef0-50f7-9fdc-d2c237b59e35 | tickbox | Loss of containment
38e73858-15e2-530f-b6cb-687a3a5228b5 | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
a479994e-91eb-527b-8b30-780190b19085 | tickbox | Loss of structural integrity
07de0b49-6421-52ef-8c3e-90e955f5e47b | tickbox | Equipment failure
e42f97da-349e-5e21-a5f3-f9b5b4e59e24 | tickbox | Uncontrolled ignition source
3d7150c4-b075-5b3b-a8a5-2b2b91b8d6a9 | tickbox | Collision
b7287a6e-9b8a-5347-bfc7-686ff353c681 | tickbox | Ignition/Fire
c1e99fe1-fa68-5556-bb36-7462c665d8b8 | tickbox | Back strain/Injury
febb8172-fed9-5553-9762-1ed383864782 | tickbox | Burns
65f86853-2b43-501a-81fa-10802d729290 | tickbox | Heat exhaustion
7f2d7094-e12d-5779-8909-10e99c0c3200 | section | Initial controls - Mark all that apply.
64d5901f-79af-44b5-b2df-5ba274e0fd84 | checkpoint-no-value | Initial controls - Mark all that apply.
0531576a-0e0d-5e0a-9822-c90127d2c91f | note | People controls
cdb87cd9-aa83-552e-9f27-192ad19e29f1 | tickbox | Safety/Fire watch person
c7ce9b43-64e2-5a9c-8866-82a154afcba6 | tickbox | Barriers/Flagging
dcf6bb7e-a5f9-52f0-a099-4bfb78439724 | tickbox | Warning signs
bc6fc587-4cd7-57aa-8aac-b1885ff5d667 | note | Equipment controls
92675b30-30a9-58e0-af6a-1b04a7c62402 | tickbox | Master tags and locks
5ae218e2-4b86-5e4c-a9cc-6344228e94da | tickbox | Scaffolding for access
d3d8dc3e-2571-5fed-b558-c2a29d1d7824 | tickbox | Radio communication
56c8c170-dbe5-5304-a387-0e1d58901816 | note | Environmental controls
d74792dd-5e8d-54f1-8718-88bf002c7d28 | tickbox | Ventilation
08c2a88f-3143-553f-ba43-3884c222ed1c | tickbox | Lighting
15c09d2b-546f-5b76-a853-2b27f4dcf21a | tickbox | Gas Testing
24f619a7-6d34-5444-b150-524826812edb | note | High risk controls
17426f23-9ba6-535d-a26c-8d86191f6e73 | tickbox | WSCS Work permit
00147651-933a-5dad-83fd-9df182bf01de | tickbox | WSCS Certificates
b26db9bb-a7f2-55cd-9f17-ca969ff48d9b | tickbox | Critical lift/Fall protection plan
8d1fd861-b1cb-5271-acd4-f4cfd50bb495 | tickbox | Specialised PPE
2142844c-3e51-58fa-a1a1-06005b55fd4f | tickbox | Spill kit
35ee2540-5d3d-5bc6-abb6-1a93433e919f | tickbox | Fire extinguisher
0ea35b14-b47f-58c4-9129-58c1a83117dc | section | Signatures
66af9c5a-1f5f-4ddc-8e06-22ea9b5a07f8 | checkpoint-no-value | Signatures
08dd81cd-932b-58b2-9b84-2913f2f6f46a | signoff | Applicant signature
e9a3b389-05b5-5eee-9c5d-e3b61b2d14d1 | checklist | JHA - Job Step |  | JHA - Job Step
e62f412e-efbd-50c2-b348-57fee9e5a033 | section | Task Step - add task step for each individual task
00780faa-d665-40b2-87ab-6cadb24cd40f | checkpoint-no-value | Task Step - add task step for each individual task
26e2895e-46dc-55d8-91aa-d34462d3219f | date | Date:
edc2c497-a45f-5063-8c12-87586ccbfeb2 | textbox | Task step number (eg. Step 1, Step 2 etc):
a12b90eb-71dc-5936-b414-a3b4762a0526 | textbox | Task details:
90373697-09a2-52da-9093-db43db06e3e5 | textbox | Hazards:
f9753613-aa62-5d16-ba34-191186a9832b | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
578f357f-fae0-515e-99b1-60042e5723d9 | textbox | Potential consequence:
be7dc2f6-39bf-5087-a981-031a48ffe06d | textbox | Controls:
d61174a1-6a04-5f2c-90e9-2d589f32cacf | textbox | Recovery steps:
38bcca95-c251-5bb8-8ce5-ce18bef184a7 | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
00ec7ae0-a1a6-4644-9acd-be62a1ebf418 | checklist | Lighting, Power and Data |  | Lighting, Power and Data
d1cb23b2-fbf1-4b3b-9fa0-3114aa8674ee | section | Details
a90fd625-71ec-4541-b8a4-db4c8cedefac | checkpoint | Lighting Power and Data
3562114f-8cbe-5d1d-b5b6-225e69b3a08a | button | Internal and external lighting installed as per drawings | Yes,N/A
3f348f00-4731-5db7-af7d-f8265e3191d6 | button | Exit and emergency lighting installed as per drawing | Yes,N/A
ebc067b8-314c-520c-8685-1e9fc9fd6be2 | button | Power and data installed as per drawing | Yes,N/A
9de21eba-66cc-52f8-9961-bc4118e08542 | button | As-Built drawings completed and signed off | Yes,N/A
27a70162-f63e-400b-b054-9e84a6afe342 | signoff | Lighting, Power and Data checked by:
eb9d93b1-c475-4780-85eb-bb3111fe7d03 | checkpoint | Client Representative
80da5b77-d225-4f5b-95a7-20a0cee86bb8 | signoff | Client Representative:
d574a822-a52d-5be0-b1b6-4aa45276d0ad | checklist | MSDS |  | MSDS
8111ace1-1386-5c1f-8290-3df28e3c8d3f | section | Details
18f906b0-6744-555a-b652-e3773583a9dd | checkpoint | Please Upload MSDS Sheets
a9f20cf0-1241-5cbf-948e-19817bd6c7c4 | checklist | Record of Inspection (ROI) |  | Record of Inspection (ROI)
f8eb7881-7f3c-5872-b944-b0fa1e752a6b | checkpoint | Please upload Record of Inspection here when complete (ROI)
f105264a-6276-59b2-8673-abc19267a423 | checklist | Safe/Unsafe Observation Card |  | Safe/Unsafe Observation Card
111a524e-9e5b-5bca-9cbd-3549c888851d | section | Basic Details
355b34ca-ad4c-4e82-9b35-f533322eb808 | checkpoint | Basic Details
d602e59a-1a81-5f60-a7d6-2f827da33a73 | button | Safe or Unsafe observation? | SAFE,UNSAFE
cb033385-3086-53a0-bbac-3c20e33d057c | date | Date:
f49370b9-a829-5df1-9111-809ae08fe247 | textbox | Observers Name
d28cfffc-ddd4-5179-bcd9-5f78155c4826 | textbox | Site
96f36722-055e-5270-ad2d-69c7d78c54b4 | textbox | Task Observed
6aefe625-b4b3-55d7-a581-1a7b03689331 | section | Hazard Observation (select all that apply)
f1cf4dde-cdf0-495f-86b7-68a64ab39d2c | checkpoint | Hazard Observation (select all that apply)
17092683-2b10-5c80-8089-05b8947b07a7 | button | Mobile Equipment | YES,NO
7b7871e6-df54-557f-b017-58f42a9916cc | button | Hoisting & Lifting | YES,NO
fbdfbd64-b065-50c3-b73a-51c15673e56a | button | Dropped Objects | YES,NO
ae96e44c-d7d4-53ac-80bd-478435f9a4ce | button | PPE & Process | YES,NO
293008da-b8f7-5abd-be58-679497580893 | button | Pressurised equipment | YES,NO
057c83c4-04b1-554d-94b6-2faa2f064aa5 | button | Machinery & Tools | YES,NO
a4de9a3f-f26c-5ecd-9ef2-a0656e7698d4 | button | Electrical equipment | YES,NO
9e38850d-3fe1-571d-8d97-1c621613565c | button | Housekeeping | YES,NO
080c4ecc-937a-56fb-a4e0-3520ca024a33 | button | Person fall risk | YES,NO
75d1356e-4970-503d-8356-7e0ec8c43b6a | button | Manual handling | YES,NO
0c091747-fc77-5b1c-82c2-7840e1a97f4a | button | Exposure to process temperatures. | YES,NO
c2d1aff2-59c0-586f-bb05-7b9b11611ec1 | button | Confined space | YES,NO
48b40157-a891-5948-b3eb-9475aa0b0d1d | textbox | What I saw
45961bcc-530a-5d8f-919f-4a526f17c0fa | textbox | What I did
69046fb6-7bd8-5821-98a7-34e0bee56b6d | button | Is further action required? | YES,NO
f6ee80f1-5dc3-5f59-90e9-dd1c0fc30272 | checkpoint | Observation reported?
9e09ffc8-baf0-5b76-bf83-57ad64ebda26 | textbox | Reported to:
0e65806f-84ca-5b46-af40-22bafee761af | textbox | Other comments
92605c9b-0707-43de-a220-adfccffa4d66 | checklist | Stairs and Platforms |  | Stairs and Platforms
ac854523-4648-4677-81ab-ad7dfabfadbe | section | Details
d0b498d6-198f-499f-afbc-e037beb85dcf | checkpoint | Stairs and Platforms
95da4e2f-503a-5b61-b7ee-cef5e79ae2da | button | Stair and platform frames as per drawings with 38mm FRP Grating for platform and PT6 stair treads 275mm wide | Yes,N/A
c6ff91db-857d-4f64-b52d-6f18b9343b8e | checkpoint | Photo of stairs and platform frames
73c7a63f-396f-5281-9af2-ec081d996c2f | button | Edge of each step and edge of platform has high contrast, non-slip proprietary nosing | Yes,N/A
f6fb3883-ba23-4dcd-b075-9a9e6554317c | checkpoint | Photo of nosing
0863e5e2-a816-5f45-a2ee-21334ebfdba0 | button | Handrail system installed either side of the steps and around edges of platforms | Yes,N/A
f40135ce-6ddc-49bd-8b2f-30cbe7e2f775 | checkpoint | Photo of handrails
52392f83-fd8d-557c-83dc-c3dc5fbf9ef1 | button | As-Built drawings completed and signed off | Yes,N/A
080c9f57-8771-488e-b538-e7202529a25a | signoff | Stairs and Platforms checked by:
6a39d6b1-c236-4784-9e0a-d77b47ac0c23 | checkpoint | Client Representative
ff318522-0d6b-417f-8df6-17d182f0fc33 | signoff | Client Representative:
9190d35e-62ad-549b-b4b3-68404b96641e | checklist | Test Equipment Details: |  | Test Equipment Details:
8111ace1-1386-5c1f-8290-3df28e3c8d3f | checkpoint-no-value | Details
4a866a34-da33-5783-8eda-0803536fed2f | textbox | Make
d22df50f-1070-5906-b3c0-7c4dc5fe5ce4 | textbox | Model
ba416c92-406b-57d4-b40f-fbb09fe6ac82 | textbox | Serial No
6aecfb6a-a654-5cc3-8de7-e0850f9c3fd4 | textbox | Calibration Expiry Date
1bbd320a-0d22-5276-bc0e-2234c714606c | checklist | Toolbox Meeting |  | Toolbox Meeting
4bff8cf5-2f9b-5ff6-b60a-449bd8fb0518 | section | Toolbox meeting
b6514b73-7c79-4b26-966a-21a3871636ff | checkpoint-no-value | Toolbox meeting
da98d349-009c-5dbb-aded-33660590f394 | date | Date:
b0c2f5f3-8c74-5db3-ae82-57d532528533 | textbox | Meeting location:
1571e769-db4c-5060-be7a-4bdfe3bdaa39 | textbox | Meeting conducted by:
f08798a0-bb3a-5f99-bcdb-0c1b059e3de6 | textbox | Meeting attendees:
10be6db0-65fb-5ac7-a41d-09e750c341e4 | textbox | Today's work scope/Hazards
620957ff-5c29-5c5b-89f5-3b1f659122ee | textbox | Hazard controls:
8a582c41-2e7e-533d-a344-42036f914b8f | signoff | PICWS Signoff