## matrix
Matrix Name | Dimension | Name | Type / Data Field | Tag 1 | Tag 2
Cables
| Scope |  |  | Cables
Rows
|  | Control Cables | dynamic | Cables | Control Cables
|  | COMMS Cables | dynamic | Cables | COMMS Cables
Columns
|  | Low Voltage Cable |  | Low Voltage Cable
|  | Verify cable type, size, colour code and tags in accordance with Cable Schedule | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Low Voltage Cable
|  | Check dressing/cleating, cable undamaged | Check dressing / cleating, cable undamaged | Low Voltage Cable
|  | Bending radius satisfactory | Bending radius satisfactory | Low Voltage Cable
|  | Check cable cores correctly identified & labelled | Check cable cores correctly identified and labelled. | Low Voltage Cable
|  | Cable terminated with correct lugs & crimped with the correct die | Cable terminated with correct lugs and crimped with the correct die. | Low Voltage Cable
|  | Check Armour/Screen correctly made off | Check Armour / Screen correctly made off. | Low Voltage Cable
|  | Check armour continuity/earthing maintained by correct use of serrated washers and/or earth tags | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Low Voltage Cable
|  | From: | From: | Low Voltage Cable
|  | To: | To: | Low Voltage Cable
|  | Glanding / Locknuts correctly installed | Glanding / Locknuts correctly installed. | Low Voltage Cable
|  | Gland type - from: | Gland type - from: | Low Voltage Cable
|  | Gland type - Haz. Area Cert Details | Haz. Area Cert Details. | Low Voltage Cable
|  | Gland type - to: | Gland type - to: | Low Voltage Cable
|  | Gland type - Haz. Area Cert Details | Haz. Area Cert Details. | Low Voltage Cable
|  | Confirm spare cores & shields terminated & conform to drawings and client spec. | Confirm spare cores and shields are terminated and conform to drawings and client spec. | Low Voltage Cable
|  | Electrical Checks |  | Electrical Checks
|  | Record test results: Insulation Resistance, Continuity, Bonding, Other | Record test results: Insulation Resistance, Continuity, Bonding, Other. | Electrical Checks
|  | Client Representative |  | Client Representative
Cable Support / Cable Support ITR's
| Scope |  |  | Cable Support
Rows
|  | Cable Support | grouping | Cable Support
|  | Cable Support |  | Cable Support | Cable Support.
|  | Cable Support ITR's | dynamic | Cable Support | Cable Support ITR's
Columns
|  | Cable Support |  | Cable Support
|  | Cable ladder installed | Cable ladder installed | Cable Support
|  | Photo of cable ladder |  | Photo of cable ladder
|  | Vertical UT-3 Uni tray installed where required to allow cable access into cabinets | Vertical UT-3 Uni tray installed where required to allow cable access into cabinets | Photo of cable ladder
|  | Photo of tray |  | Photo of tray
|  | Fibre/comms duct insatlled | Fibre/comms duct insatlled | Photo of tray
|  | Photo of fibre/comms duct |  | Photo of fibre/comms duct
|  | Fire wall penetrations go through fire sleeves | Fire wall penetrations go through fire sleeves | Photo of fibre/comms duct
|  | Photo of fire wall penetrations |  | Photo of fire wall penetrations
|  | Cable Supports Above Ground |  | Cable Supports Above Ground
|  | Verify cable support installed as per relevant drawings/is correct size & type | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Cable Supports Above Ground
|  | Check all machined parts cut or drilled have no rough edges | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Cable Supports Above Ground
|  | All covers fitted if applicable | All covers fitted if applicable. | Cable Supports Above Ground
|  | Check cable support structures adequately fixed & present no hazard to personnel | Check cable support structures are adequately fixed and present no hazard to personnel. | Cable Supports Above Ground
|  | Welded support brackets wire-brushed & painted to completion | Welded support brackets have been wire-brushed and painted to completion. | Cable Supports Above Ground
|  | Splice plates, barriers, earthing system secure | Splice plates, barriers, earthing system secure. | Cable Supports Above Ground
|  | Trays/ladders, supports, brackets not interfering with other disciplines | Trays / ladders, supports, brackets not interfering with other disciplines. | Cable Supports Above Ground
|  | Check bends do not exceed the maximum cable bending radius | Check bends do not exceed the maximum cable bending radius. | Cable Supports Above Ground
|  | Cables have adequate mechanical protection as & where required | Cables have adequate mechanical protection as and where required. | Cable Supports Above Ground
|  | Inspect for system rigidity, & check levels to correct plane | Inspect for system rigidity, and check levels to correct plane. | Cable Supports Above Ground
|  | Earth bonding straps have been fitted to any sections that are split/hinged/flexible | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Cable Supports Above Ground
|  | Tray bonded to structure at correct locations | Tray bonded to structure at correct locations. | Cable Supports Above Ground
|  | Earth bonding continuity tested – record result: | Earth bonding continuity tested – record result: | Cable Supports Above Ground
|  | Cable Supports Above Ground - As-builts complete | As-builts complete. | Cable Supports Above Ground
|  | Cable Transits |  | Cable Transits
|  | Transit frame installed as per drawings. | Transit frame installed as per drawings. | Cable Transits
|  | Transit frame identification marked correctly & visible | Transit frame identification marked correctly and visible. | Cable Transits
|  | Frame correctly packed with correct sized blocks & infills | Frame correctly packed with correct sized blocks and infills. | Cable Transits
|  | Correct stay plates fitted (non-ferrous for single core power cables) | Correct stay plates fitted (non-ferrous for single core power cables.) | Cable Transits
|  | Rated insulation installed to transit | Rated insulation installed to transit (where required.) | Cable Transits
|  | Cables entering & leaving transits adequately supported & protected | Cables entering and leaving transits adequately supported and protected. | Cable Transits
|  | Cables pass through frames without strain on blocks | Cables pass through frames without strain on blocks. | Cable Transits
|  | All cables identified on both sides of transit & visible | All cables identified on both sides of transit and visible. | Cable Transits
|  | Cable Transits - As-builts complete | As-builts complete. | Cable Transits
|  | Add applicable signatures |  | Add applicable signatures
|  | Client Representative |  | Client Representative
Earthing
| Scope |  |  | Earthing
Rows
|  | Earthing | grouping | Earthing
|  | Earthing Checklist |  | Earthing | Earthing Checklist
|  | Copper Bar | dynamic | Earthing | Copper Bar
|  | Cubicles | dynamic | Earthing | Cubicles
|  | Other Earthing | dynamic | Earthing | Other Earthing
Columns
|  | Earthing |  | Earthing
|  | 50mmx10mm copper earth bar installed on cable ladder as per design | 50mmx10mm copper earth bar installed on cable ladder as per design | Earthing
|  | Photo of copper bar |  | Photo of copper bar
|  | All cubicles connected to earth bar using 35mm2 Cu earth bond | All cubicles connected to earth bar using 35mm2 Cu earth bond | Photo of copper bar
|  | Photo of cubicles connected to earth bar |  | Photo of cubicles connected to earth bar
|  | All doors have flat tinned copper braid earth straps fitted | All doors have flat tinned copper braid earth straps fitted | Photo of cubicles connected to earth bar
|  | Photo of doors with copper braid |  | Photo of doors with copper braid
|  | Earth bar penetrates floor | Earth bar penetrates floor | Photo of doors with copper braid
|  | Photo of earth bar |  | Photo of earth bar
|  | As-Built drawings completed & signed off | As-Built drawings completed and signed off | Photo of earth bar
|  | Electrical earthing system installation |  | Electrical earthing system installation
|  | Confirm earth grid layout, earth conductors/connections & number of earth electrodes is in accordance with drawings, drawings as-built | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Electrical earthing system installation
|  | Ensure that all metal work is earthed as required | Ensure that all metal work is earthed as required. | Electrical earthing system installation
|  | Check welding of earth bosses & associated surface finish | Check welding of earth bosses and associated surface finish. | Electrical earthing system installation
|  | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Electrical earthing system installation
|  | Ensure that brazing or welding of all joints has been completed correctly | Ensure that brazing or welding of all joints has been completed correctly. | Electrical earthing system installation
|  | Ensure that adequate corrosion & weather protection has been installed around all connections, joints, lugs, cad (thermal) welds & earth bosses | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Electrical earthing system installation
|  | All earth bosses & studs tight & fitted with shake proof washers & coated with protective coating | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Electrical earthing system installation
|  | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Electrical earthing system installation
|  | Check that all bi-metal connections have been performed correctly to manufacturer’s reqs | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Electrical earthing system installation
|  | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Electrical earthing system installation
|  | Ensure that earth cable identification markings are in place | Ensure that earth cable identification markings are in place. | Electrical earthing system installation
|  | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Electrical earthing system installation
|  | Check earth bar fixings, mounting points & terminations are tight & secure & conform to project spec. | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Electrical earthing system installation
|  | Test Results |  | Test Results
|  | Earth continuity test results | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify) | Test Results
|  | 3-Wire earth test results | 3-Wire earth test results (If applicable). | Test Results
|  | Earth grid test results | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids) | Test Results
|  | Bus Bar |  | Bus Bar
|  | Check entire Bus Bar & confirm there is no damage | Check entire Bus Bar and confirm there is no damage | Bus Bar
|  | Bus Bar alignment is correct | Bus Bar alignment is correct | Bus Bar
|  | Confirm all jointing bolts are present & have been torque tested in accordance with the manufacturer & design reqs | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. | Bus Bar
|  | Confirm all transit packing & preservation materials have been removed | Confirm all transit packing and preservation materials have been removed. | Bus Bar
|  | Confirm Bus Bar clearances conform to manufactures & design reqs | Confirm Bus Bar clearances conform to manufactures and design requirements. | Bus Bar
|  | Confirm all Bus Bars are secure within the supports | Confirm all Bus Bars are secure within the supports. | Bus Bar
|  | Record the total number of bus bar joints | Record the total number of bus bar joints. | Bus Bar
|  | Test Results |  | Test Results:
|  | Test Results - Results: | Results: | Test Results:
|  | Cable lug |  | Cable lug
|  | Appropriate lug for cable size has been used | Appropriate lug for cable size has been used. | Cable lug
|  | Lug has been correctly seated with no loose copper strands outside of lug | Lug has been correctly seated with no loose copper strands outside of lug. | Cable lug
|  | Lug has been crimped with 60 tonne crimper | Lug has been crimped with 60 tonne crimper. | Cable lug
|  | Joint sealing paste has been correctly applied to the contact surface of lug | Joint sealing paste has been correctly applied to the contact surface of lug | Cable lug
|  | Bolts |  | Bolts
|  | Bolt has been torqued to manufacturers reqs | Bolt has been torqued to manufacturers requirements | Bolts
|  | Manufacturers torque req | Manufacturers torque requirement (if applicable) | Bolts
|  | Test Results |  | Test Results
|  | Continuity test results | Continuity test results | Test Results
|  | Ductor test results | Ductor test results if applicable | Test Results
|  | Test Equipment Used |  | Test Equipment Used
|  | Description | Description | Test Equipment Used
|  | Manufacturer | Manufacturer | Test Equipment Used
|  | Model No: | Model No: | Test Equipment Used
|  | Serial No: | Serial No: | Test Equipment Used
|  | Client Representative |  | Client Representative
Equipment and Install
| Scope |  |  | Equipment and Install
Rows
|  | Switchboards | dynamic | Equipment and Install | Switchboards
|  | Distribution Boards | dynamic | Equipment and Install | Distribution Boards
|  | Control Panels | dynamic | Equipment and Install | Control Panels
|  | Batteries | dynamic | Equipment and Install | Batteries
Columns
|  | Low Voltage Switch Board |  | Low Voltage Switch Board
|  | Check equipment & nameplate details are correct & in accordance with the data sheet & equipment schedule | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Low Voltage Switch Board
|  | Check holding down/mounting arrangement is correct | Check holding down/mounting arrangement is correct. | Low Voltage Switch Board
|  | Check for mechanical damage | Check for mechanical damage. | Low Voltage Switch Board
|  | Confirm that all temporary supports, jumpers & ties have been removed | Confirm that all temporary supports, jumpers and ties have been removed. | Low Voltage Switch Board
|  | Incoming cables correctly installed, terminated & supported | Incoming cables correctly installed, terminated and supported. | Low Voltage Switch Board
|  | Phase identification correct | Phase identification correct. | Low Voltage Switch Board
|  | Confirm that padlocking facilities are provided & operate correctly allowing all circuit breakers to be locked in the open position & safety shutters locked in the closed position | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Low Voltage Switch Board
|  | Confirm all cubicle doors can be opened without obstruction & minimum required clearances are retained | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Low Voltage Switch Board
|  | Bus bar alignment to manufacturer's specification & connecting links tight to specified torque | Bus bar alignment to manufacturer's specification and connecting links tight to specified torque. | Low Voltage Switch Board
|  | Confirm components, fuses etc correctly sized & identified as per design drawings & Single Line Diagrams | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Low Voltage Switch Board
|  | Instruments, indication lamps & interlocks correct | Instruments, indication lamps and interlocks correct. | Low Voltage Switch Board
|  | Ammeter & current transformer correctly installed | Ammeter and current transformer correctly installed. | Low Voltage Switch Board
|  | Check internals for cleanliness | Check internals for cleanliness. | Low Voltage Switch Board
|  | Check that Switchboard is correctly earthed Check door, escutcheon, gland plate, gland & frame | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Low Voltage Switch Board
|  | Test & confirm the earth resistance between switchboard & local earth system is less than 0.5ohms | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms | Low Voltage Switch Board
|  | All internal cabling & wiring neat, correct & undamaged | All internal cabling and wiring neat, correct, and undamaged. | Low Voltage Switch Board
|  | Unused cable entry sealed | Unused cable entry sealed. | Low Voltage Switch Board
|  | Heaters correctly installed | Heaters correctly installed. | Low Voltage Switch Board
|  | Confirm that all insulating bushings & barriers are satisfactory | Confirm that all insulating bushings and barriers are satisfactory. | Low Voltage Switch Board
|  | Check Busbar insulation resistance between earth & phases For a duration of 60 seconds with the following voltages |  | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L1 - Earth | L1 - Earth | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L2 - Earth | L2 - Earth | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L3 - Earth | L3 - Earth | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L1 - L2 | L1 - L2 | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L1 - L3 | L1 - L3 | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | L2 - L3 | L2 - L3 | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | N - Earth | N - Earth | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages.
|  | Insert Photo |  | Insert Photo
|  | Distribution Board Installation |  | Distribution Board Installation
|  | Inspect for mechanical damage from freight & handling | Inspect for mechanical damage from freight and handling | Distribution Board Installation
|  | Check tag number is in accordance with Electrical Equipment List, Document No & nameplate details correct | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Distribution Board Installation
|  | Check type, size & number of breakers is correct as per drawings | Check type, size and number of breakers is correct as per drawings | Distribution Board Installation
|  | Ensure there is no visible damage to the equipment & all meters, LED indicators, switches & fittings are in good order | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Distribution Board Installation
|  | Confirm main isolator operates with associated switches & auxiliaries | Confirm main isolator operates with associated switches and auxiliaries | Distribution Board Installation
|  | Check equipment panel external & internal earthing connections are securely fitted & properly terminated on the cabinet protective earth bar | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Distribution Board Installation
|  | Check DB, sub circuits, DB Legend & internal cables correctly labelled As Built drawings complete | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Distribution Board Installation
|  | Check sealing of all cable penetration | Check sealing of all cable penetration (where applicable). | Distribution Board Installation
|  | Active, Neutral & Earth bar properly identified & labelled | Active, Neutral and Earth bar properly identified and labelled | Distribution Board Installation
|  | Confirm panel is readily accessible for inspection & maintenance | Confirm panel is readily accessible for inspection and maintenance. | Distribution Board Installation
|  | Test Results |  | Test Results
|  | Insulation Resistance | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) | Test Results
|  | Earth Continuity | Earth Continuity | Test Results
|  | Earth Bond | Earth Bond | Test Results
|  | Fault Loop Impedance, PSSC | Fault Loop Impedance, PSSC. | Test Results
|  | RCD Test results | RCD Test results (1/2x I, 1x I, 5x I) | Test Results
|  | Voltage & Phase Rotation | Voltage and Phase Rotation | Test Results
|  | As-builts complete | As-builts complete. | Test Results
|  | Control Panel |  | Control Panel
|  | Check equipment & nameplate details are correct & in accordance with the data sheet & equipment schedule | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Control Panel
|  | Check holding down/mounting arrangement is correct | Check holding down/mounting arrangement is correct. | Control Panel
|  | Check for mechanical damage | Check for mechanical damage. | Control Panel
|  | Check tightness of circuit connections | Check tightness of circuit connections. | Control Panel
|  | All internal cabling & wiring is correctly numbered, colour coded & terminated | All internal cabling and wiring is correctly numbered, colour coded and terminated | Control Panel
|  | Ammeter scale & current transformer correct | Ammeter scale and current transformer correct. | Control Panel
|  | Check internals for cleanliness | Check internals for cleanliness. | Control Panel
|  | Check manual operation of selector switches, MCB, push buttons, etc | Check manual operation of selector switches, MCB, push buttons, etc. | Control Panel
|  | Incoming cables correctly glanded, terminated & labelled | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Control Panel
|  | Heaters correctly installed | Heaters correctly installed. | Control Panel
|  | Fuse rating correct | Fuse rating correct. | Control Panel
|  | Insert Photo |  | Insert Photo
|  | As-builts complete | As-builts complete. | Insert Photo
|  | Electrical Checks |  | Electrical Checks
|  | Record test results: Insulation Resistance, Continuity, Bonding, Other | Record test results: Insulation Resistance, Continuity, Bonding, Other. | Electrical Checks
|  | Upload completed ITR scans |  | Upload completed ITR scans
|  | Add applicable signatures |  | Add applicable signatures
Frame Construction
| Scope |  |  | Frame Construction
Rows
|  | Frame Construction | grouping | Frame Construction
|  | Frame Construction |  | Frame Construction
Columns
|  | Frame Construction |  | Frame Construction
|  | Baseplate layout as per drawing spec. | Baseplate layout as per drawing specififcation | Frame Construction
|  | Photo of Baseplate |  | Photo of Baseplate
|  | Removeable Padeyes in place | Removeable Padeyes in place | Photo of Baseplate
|  | Photo of removeable padeyes |  | Photo of removeable padeyes
|  | Floor/room layout as per drawing | Floor/room layout as per drawing | Photo of removeable padeyes
|  | Photo of floor/room layout |  | Photo of floor/room layout
|  | Compressed cement board used | Compressed cement board used | Photo of floor/room layout
|  | Photo of floor board |  | Photo of floor board
|  | Frame construction adhering to all general steel work notes as per latest drawings | Frame construction adhering to all general steel work notes as per latest drawings | Photo of floor board
|  | Baseplate free from damage & paintwork is intact | Baseplate is free from damage and paintwork is intact | Photo of floor board
|  | Add QA pack from blast & paint |  | Add QA pack from blast and paint
|  | Add QA pack from fabricators |  | Add QA pack from fabricators
|  | As-Built drawings completed & signed off | As-Built drawings completed and signed off | Add QA pack from fabricators
|  | Client Representative |  | Client Representative
Floor, Duct Penetrations & Vents
| Scope |  |  | Floor, Duct Penetrations and Vents
Rows
|  | Floor, Duct Penetrations & Vents | grouping | Floor, Duct Penetrations & Vents
|  | Floor, Duct Penetrations and Vents |  | Floor, Duct Penetrations and Vents
Columns
|  | Floor, Duct Penetrations and Vents |  | Floor, Duct Penetrations and Vents
|  | Floor cable penetrations arrangement as per latest drawings | Floor cable penetrations arrangement as per latest drawings | Floor, Duct Penetrations and Vents
|  | Photo of floor cable penetrations |  | Photo of floor cable penetrations
|  | Battery Cabinet Ventilations as per drawings | Battery Cabinet Ventilations as per drawings | Photo of floor cable penetrations
|  | Photo of battery cabinet ventilation points |  | Photo of battery cabinet ventilation points
|  | Fresh air intake installed for control room as per drawings | Fresh air intake installed for the control room as per drawings. | Photo of battery cabinet ventilation points
|  | Photo of fresh air intake |  | Photo of fresh air intake
|  | Ventilation point for switchroom insatlledas per drawings | Ventilation point for the switchroom insatlledas per drawings | Photo of fresh air intake
|  | Photo of ventilation point |  | Photo of ventilation point
|  | Switch board arc vent installed & located as per drawings | Switch board arc vent installed and located as per drawings | Photo of ventilation point
|  | Photo of switchboard arc |  | Photo of switchboard arc
|  | Warning signs installed | Warning signs installed | Photo of switchboard arc
|  | Photo of warning signs |  | Photo of warning signs
|  | Deflection Check | Deflection Check - (+/-) 1mm tolerance in any 1 metre radius & a tolerance of (+/-) 3mm over the length of the switchroom. Record results: | Photo of warning signs
|  | As-Built drawings completed & signed off | As-Built drawings completed and signed off | Photo of warning signs
|  | Client Representative |  | Client Representative