## Checklist Templates
Warnings | Id | Type | Name | Values | Prompting Name | Prefix | Postfix | Resource Id
|  | checklist | As-Built Drawings |  | As-Built Drawings |  |  | 81dc3daa-75a3-461f-b2ff-56a905da84c6
|  | section | As-Built Drawings - attach scanned documents
|  | checkpoint-no-value | As-Built Drawings - attach scanned documents
| 0a8a4485-cabb-5d5f-af06-940765d098ba | textbox | Drawing no.
|  | checklist | Cable Test Record |  | Cable Test Record |  |  | 71adec48-fe24-462e-8b6d-cb5ef09cc876
|  | checkpoint | Upload completed ITR scans
|  | checklist | Certificate of compliance (COC) |  | Certificate of compliance (COC) |  |  | f62048d6-daa1-44ab-bf8a-adf52d4e9c7d
|  | checkpoint | Please upload Certificate of Compliance here when complete (COC)
|  | checklist | Earth Bonding |  | Earth Bonding |  |  | 5ed3eb59-8524-403f-a41f-b790f51051e0
|  | checkpoint | Continuity test from Point A to Point B
| 1ef392c1-7d9f-50cd-ac13-69b80b7bfcb0 | textbox | Results: |  |  |  | Pass if <0.5Ω
| 5e094a30-b140-58b9-82c5-c7c4e318678d | textbox | Size of bond cable
| 77db464b-b035-5fd6-934f-d20de8b26522 | note | Upload photo of bond connection
|  | checklist | Electrical Safety Ceritificate (ESC) |  | Electrical Safety Ceritificate (ESC) |  |  | cebd417f-49e3-4c03-a951-f9da46ccb290
|  | checkpoint | Please upload Electrical Safety Certificate here when complete (ESC)
|  | checklist | FAT Testing |  | FAT Testing |  |  | ae9616c8-c1ca-446a-9e7a-4a12b016b78d
|  | checkpoint | Upload completed test sheet scans
|  | checklist | ITR-1-11 Cone and Thread Pressure Testing |  | ITR-1-11 Cone and Thread Pressure Testing |  |  | abef7161-4a84-4feb-8835-fd7b930cd6f6
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | General Data
| 3994b7aa-158f-5fae-a7b4-c297b4331618 | textbox | Location:
| 61d68947-ccee-5d3b-be09-232bb36cbb83 | textbox | Duty:
| 9c8cf425-75d9-5dc5-be7b-774b69c66b5b | textbox | Reference Drawings:
| 48dbdc64-c731-5af4-a1c7-337df943abf8 | textbox | Hook-up drawing:
| 75ac7d0b-b51a-57fe-909f-7e7559a24b8d | textbox | Related instrument tag no:
| adbc7542-03d7-5de5-854d-d6d0b9eebbc3 | textbox | Tube diameter and wall thickness:
|  | checkpoint | Checklist items
| 97a2e6ed-1c67-5ac4-ab68-046c6d783be7 | button | Tubing orientation as per hook up drawing. | Yes,N/A
| 73940b4c-cafd-52b3-b60d-84550a619f11 | button | Checked with a Torque Wrench and marked and tagged | Yes,N/A
| eeae0ff4-f831-55b8-939e-324848ca6a4a | button | Ensure Area is barricaded off to restrict unauthorized entry to personnel | Yes,N/A
| 61e9972c-14b7-5013-b6d9-f6bbefcc4374 | button | Tube as per specification and hook up drawings. | Yes,N/A
| c9fe4b62-9a50-530c-b1c0-080fbef70ad8 | textbox | Max design pressure:
| c920eacb-2b72-57d3-a74d-ba6ea52cfa4e | textbox | Test medium used:
| d284b70b-35e1-5c7f-8dc7-4013977bd09e | textbox | Record Testing pressure:
| 72e73297-c645-5129-bb37-ef0dbdbbd953 | textbox | Test pressure duration: |  |  |  | Minutes
| 7063e3c4-841c-5e72-8581-e0b1622b6eff | textbox | Test leak rate: |  |  |  | Litres/minute
| b3c3e804-203a-59ec-b883-e810653e86b4 | button | Chart recorder used and attached (where applicable). | Yes,N/A
| 0a84c33f-6439-5841-b819-81ee452d0825 | button | Confirm all Tubing lines have been pigged / cleaned. | Yes,N/A
| 273e0ac2-276e-5f20-b9fe-df952626ab5b | button | Check all plugs are replaced (if removed), vents are closed, and isolation valves are in correct positions. | Yes,N/A
| 51efd6b3-af99-5e17-854e-0eed67f40960 | button | Ensure equipment is left clean and in a safe state for handover to operations to the standard of ITP-I-08 Cone and Thread cleaning procedure | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-E-01 General Electrical Equipment |  | ITR-E-01 General Electrical Equipment |  |  | 5467fac3-3629-485b-88de-78f31b8e071b
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | General Electrical Equipment
| dbc4bb46-bea4-59c3-9f9c-4dedd0bfdaea | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| 90792fe4-1f2a-533e-9e29-8eb9914e6948 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
| bf4fe38f-41e0-5ef2-a3ed-90079a245f43 | button | Installation is clean and tidy | Yes,N/A
| 499dc984-28ad-5d02-913c-5fadc6f17a8e | button | Mounting arrangement correct | Yes,N/A
| 417d2309-382e-5a5e-9c6f-3ee7b1998beb | button | All internal cabling and wiring correctly installed and labelled. | Yes,N/A
| 93ba0ee4-3ed6-59b2-a2d2-ed0047d9289a | button | External cabling is correctly installed and labelled. | Yes,N/A
| 9493ebb1-078a-559a-8d12-80e920e69366 | button | Check that Equipment is correctly earthed. | Yes,N/A
| c682b249-74d3-56a6-b975-6e380e006de1 | button | Check gland, plate, frame & door earth continuity | Yes,N/A
| 9d50507e-bed5-5ee1-920e-6ad4ae22b6f3 | button | All spare entries blanked off with correct plugs. | Yes,N/A
| f91b2fbe-25bf-5019-85af-dec1fb2d4cb8 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
| 59b2877b-52a8-5eac-93d3-35eaac9a6c16 | button | Conforms to Specifications and Drawings. | Yes,N/A
| e4272767-534a-522d-b81c-f84c3f8e48ba | button | As-builts complete. | Yes,N/A
|  | checkpoint | Electrical Checks
| 4e292423-9ff8-5c92-b49f-867496accf39 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other. |  |  |  | MegaOhms
| 52a0f751-d478-54ff-a592-7249bb01e432 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-02A Conduit/Ducting Below Ground |  | ITR-E-02A Conduit/Ducting Below Ground |  |  | 3be42744-a2b5-442c-a036-684079c9459d
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Conduit/Ducting Installation Below Ground
| 28f271c4-6125-58ee-b90d-8f0d1bf7b596 | button | Check equipment details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| 35e7407e-4719-5d97-96e4-ab9a63e3da3f | button | Check conduit cable enclosure installation is as-per design, layout drawings and specifications. | Yes,N/A
| 8bc11574-1ec6-5e76-ab8d-0fd516580058 | button | Check conduit has been installed to the correct depth, "cable below" tape or Magslab installed. | Yes,N/A
| 27976252-0fba-5fd1-994e-253a331743a4 | button | Confirm that there are no obstructions, and that the installation will be accessible for maintenance. | Yes,N/A
| 4a0b7980-a615-57b5-a7b5-ad1563657e06 | textbox | Record GPS coordinates End 1
| 4fcd51bb-2b28-5005-9db8-dd17550c947c | textbox | Record GPS coordinates End 2
| 670e04eb-3a9e-5d35-96b8-7111993e4b95 | button | Check all fixings are tight and secure. | Yes,N/A
| 07cdc14f-3495-5b4b-a749-57262bea8e56 | button | Check bends do not exceed the maximum cable bend radius. | Yes,N/A
| 6414017a-0e91-5e4a-b64a-a22f99ea54ce | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-02C Cable Transits |  | ITR-E-02C Cable Transits |  |  | e8dfb774-4ab1-43fa-b7b8-0c70d42d299a
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Cable Transits
| cc787a71-5955-5ecb-8fad-474529f7fe0f | button | Transit frame installed as per drawings. | Yes,N/A
| d715960b-c0e3-5ee7-a69d-762cfd515145 | button | Transit frame identification marked correctly and visible. | Yes,N/A
| ce239d9f-06a4-514c-b687-2192270b2e1f | button | Frame correctly packed with correct sized blocks and infills. | Yes,N/A
| e1a5844d-8f32-5413-9ef6-706d6654a4d9 | button | Correct stay plates fitted (non-ferrous for single core power cables.) | Yes,N/A
| fbde239a-3cea-5d14-933b-73ab7865b579 | button | Rated insulation installed to transit (where required.) | Yes,N/A
| 4d8711b1-bd02-53a7-9fdc-7ca510dff5ca | button | Cables entering and leaving transits adequately supported and protected. | Yes,N/A
| fb044028-0695-52e0-9f0b-83c81cf6c0a2 | button | Cables pass through frames without strain on blocks. | Yes,N/A
| 7d2b5807-8350-5c13-945b-8f42ec0b10ae | button | All cables identified on both sides of transit and visible. | Yes,N/A
| 99a9abe5-0fa3-5a62-952d-03edc2df82f7 | textbox | Record GPS coordinates End 1
| aeecdc89-ba40-5fde-a878-60297c4a8e35 | textbox | Record GPS coordinates End 2
| a479b7ad-e155-5cd1-99a3-0d24dbe6f9b2 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-03 Entec - Distribution Board Installation |  | ITR-E-03 Entec - Distribution Board Installation |  |  | 1b36dc60-255f-407e-ab1c-822bec34535a
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Distribution Board Installation
| 0a12f424-bc44-5d88-b2aa-0e25c07b7aa7 | button | Inspect for mechanical damage from freight and handling | Yes,N/A
| 6199b1de-aa0c-5aac-ae75-a2dba64f9ec3 | button | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct. | Yes,N/A
| 549c6545-7d97-5b9e-8e42-c4d1c49e1471 | button | Check type, size and number of breakers is correct as per drawings | Yes,N/A
| 64fd10af-23b9-5128-8ea9-816632d75ed2 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
| cdad4540-b929-5838-8026-874423d709c0 | button | Confirm main isolator operates with associated switches and auxiliaries | Yes,N/A
| 1a8bda9d-d06f-59ee-88de-28edb20f79cc | button | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
| aee5a296-7642-5154-beb4-8868375e33e2 | button | Check DB, sub circuits, DB Legend and internal cables correctly labelled. As Built drawings complete | Yes,N/A
| caaee73f-a586-505a-b616-63d8b38369ea | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
| 4c601402-5923-52a9-9c93-058b46e169b0 | button | Active, Neutral and Earth bar properly identified and labelled | Yes,N/A
| 103db616-143c-5ba5-9a60-cad5493c4195 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
|  | checkpoint | Test Results
| 8fe8948e-c15f-5890-a38e-df8338d290a7 | textbox | Insulation Resistance (Eg. P-P, P-N, P-E, N-E) |  |  |  | MegaOhms
| af485fca-7407-5fd8-9ce5-a150760ce5a6 | textbox | Earth Continuity |  |  |  | Ohms
| b9cace78-9c14-53f2-a7f9-c085f42f6f90 | textbox | Earth Bond |  |  |  | Ohms
| aa7fed1c-64c0-5b6d-bb59-c61ad0560cd9 | textbox | Fault Loop Impedance, PSSC.
| 4c74cad8-1bd4-55a0-b356-bbd108e8f6b1 | textbox | RCD Test results (1/2x I, 1x I, 5x I)
| d322783f-b62a-56e4-843b-ee676560dd3f | textbox | Voltage and Phase Rotation
| 1061db83-8be5-5459-b0b4-094f513f9bb0 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-04 Schedule of Test Results DB |  | ITR-E-04 Schedule of Test Results DB |  |  | 03db4db5-c467-47ec-bba2-7d5f4993da74
|  | checkpoint | Upload completed ITR scans
| 422dd788-4538-5543-9163-21e74b0f40e3 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-05 - Low Voltage Cable |  | ITR-E-05 - Low Voltage Cable |  |  | 165cf624-42a5-4f1b-9104-6a30b870037b
|  | checkpoint | Low Voltage Cable
| 61e2634e-4a4b-552f-8990-bbe0a1506402 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
| 234a1096-4fa3-59e0-a3c5-20e61c7684aa | button | Check dressing / cleating, cable undamaged | Yes,N/A
| a81ef502-50df-5f26-8940-87e1bc84f410 | button | Check cable cores correctly identified and labelled. | Yes,N/A
| 86fe7333-f24e-57c7-8fc4-1f43e8bd7303 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
| 50a1aece-d519-52cb-a637-48667ae5527f | button | Check Armour / Screen correctly made off. | Yes,N/A
| b01eea21-fbc7-573c-8af0-cc01c1f0574e | button | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags (if applicable) | Yes,N/A
| ea7836d2-f321-5f58-ad90-04f15111f7ec | button | Glanding / Locknuts correctly installed. | Yes,N/A
| 13aaa94b-36bc-5ee9-a0dc-ae9e706fc15c | textbox | Gland type - from: |  |  | Haz. Area Rating
| ea25c481-7a5a-5a0a-82d4-8c03c0284eab | textbox | Haz. Area Cert Details.
| 171b0396-46eb-589b-aef3-805e2205c349 | textbox | Gland type - to: |  |  | Haz. Area Rating
| 45c6b257-1fae-5f86-8684-643a7c6ca843 | textbox | Haz. Area Cert Details.
|  | checkpoint | Electrical Checks
| f464f1c2-7ac8-50a3-94fc-d99b700bdb2b | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
| 9f6c2b6d-0aaf-5ac4-a421-012784215aac | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-06 Control Panel |  | ITR-E-06 Control Panel |  |  | 99ca8d22-e862-4c6d-8c9f-70bba79885c6
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Control Panel
| 7720a876-d23b-51b2-8f9e-1ead929f94ee | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| 675fbc28-9522-573a-ade6-1f5849c1d969 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
| 307a523e-3a13-584b-8784-e3b376f9572d | button | Check for mechanical damage. | Yes,N/A
| fae8ae81-2fff-53af-9253-8319320e44cc | button | Check tightness of circuit connections. | Yes,N/A
| 16dc829b-0fd8-5034-8318-6731c3964801 | button | All internal cabling and wiring is correctly numbered, colour coded and terminated | Yes,N/A
| 09fcd2af-15d2-532c-8282-3054c899c0d8 | button | Ammeter scale and current transformer correct. | Yes,N/A
| 1bd05774-5639-5011-a4ae-69928c85c844 | button | Check internals for cleanliness. | Yes,N/A
| e5caa94f-d5d9-53e5-8811-2efd409b67cd | button | Check manual operation of selector switches, MCB, push buttons, etc. | Yes,N/A
| a131e15f-76a3-50a1-919c-3ed8e0fd1574 | button | Incoming cables correctly glanded, terminated and labelled. Unused entries sealed with correct plug | Yes,N/A
| 762870df-b190-58e8-a6d2-0e6249d4ba94 | button | Heaters correctly installed. | Yes,N/A
| 881da806-8017-5ee3-8769-fd8863717760 | button | Fuse rating correct. | Yes,N/A
|  | checkpoint | Electrical Checks
| 0d9a40ab-8832-5087-9084-84fe676df79b | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
| f586fd2d-0130-5947-b8cb-8718cff1d5b6 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-07 - Junction Box |  | ITR-E-07 - Junction Box |  |  | 7cbc8f54-139d-421d-98c7-c6e1b49b42bb
|  | checkpoint | Junction Box
| d927e126-e335-54a1-8ea3-cfa8b877c726 | button | Check Equipment and Nameplate details are correct in accordance with the data sheet and equipment schedule | Yes,N/A
| 048a4e98-1296-5faa-8fdf-004ae9f9cad3 | button | Check mechanical damage | Yes,N/A
| 9f99422e-6e6c-5dd8-b7ab-05cd915ee1d2 | textbox | Zone and IP rating
| 680d1e34-57ef-5441-a7f7-c20e819d86be | button | Earthing installed correctly and as per drawing | Yes,N/A
| 548aa581-9f6b-580f-9f28-86f1d0071674 | button | All internal cabling and wiring correct, (including segregation between ELV and LV, IS and Non IS circuits if applicable) | Yes,N/A
| 6b8812c4-29de-5182-ae41-761d34a0a623 | button | Incoming cables glanded correctly, empty holes plugged using correct plug for area classification to maintain IP rating | Yes,N/A
| c2993ef9-fc7a-5207-bb06-80c6d38da822 | button | Check all Cables & Cores are correctly identified | Yes,N/A
| 8f881223-fb12-5fb3-b255-d52f07b4e226 | button | Check internals for cleanliness | Yes,N/A
| 30f7de36-3000-5f20-a70d-1ee937dd30eb | button | Check manual operation of selector switch, MCB, push button, etc | Yes,N/A
| daddf929-8c1c-548e-945d-cbe2a9591262 | button | Check MCB/Fuse ratings (If applicable) | Yes,N/A
| f98e39fd-ef62-5b4a-84e3-efc723b68149 | textbox | Record earth bar resistance to earth bond
| c60420a5-e06b-5c8d-a4f0-b17b140a8ed0 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-08 Heat Tracing Circuit |  | ITR-E-08 Heat Tracing Circuit |  |  | 663fe5b3-773b-4ec7-9499-31f4456dc55d
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Heat Tracing Circuit
| 64168561-713d-5440-96d8-5fb813a267d9 | button | Circuit installed, connected & identified according to design drawings. | Yes,N/A
| 020624fe-110f-5ec8-8396-6c62cb1a00c1 | button | End caps and connection kits correctly installed. | Yes,N/A
| 6054c592-9c6f-5315-bdaf-4a3851876e96 | button | All junction boxes properly supported, and all cables protected against sharp edges. | Yes,N/A
| 4d240304-0e0a-56e8-8a77-8cc635c91d06 | button | Cable termination and glanding at all junction boxes correct. | Yes,N/A
| 9e88846b-fc8e-5b2e-86d3-e1135285e4d4 | button | All spare entries blanked off correctly. | Yes,N/A
| 5673650c-1123-5a30-bfb9-793e4d074dc7 | textbox | IR test: Phase - Earth, Phase - Neutral | Yes,N/A
| 6806e03c-34c3-5e87-b185-e809457e76b8 | button | Equipment certification meets the area classification requirements. | Yes,N/A
| ef635369-a672-53fd-bdf4-f7bdd3508ddb | button | Confirm warning labels are fixed on outside of pipe lagging | Yes,N/A
|  | checkpoint | Electrical tests
| aac4819e-29e6-5cd7-b986-74ff57bc544c | textbox | Insulation Resistance: Phase - Earth
| 86300057-2c90-5b8e-995f-1255bfcc0d20 | textbox | Insulation Resistance: Phase - Neutral
| 72407117-6712-58ff-81ad-fed4fb42960e | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-09 Electrical Switch Rooms |  | ITR-E-09 Electrical Switch Rooms |  |  | f0a00b59-a91a-4dc4-96ef-578bbeaaca2b
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Electrical Switchroom
| 58ae031b-9f7e-56bb-ad17-6710a4dd26d8 | button | Ensure all equipment is installed in accordance with layout drawings and equipment schedule. | Yes,N/A
| 2840a1cb-d4f5-5793-b2f7-f18a7541c6d8 | button | Ensure all equipment is installed as per manufacturers instructions. | Yes,N/A
| 0eb7cbb7-a48a-5150-b5af-88af912ff227 | button | Ensure there is no visible damage to installed equipment. | Yes,N/A
| e4b2136e-5592-5e36-8b32-884a5225f483 | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
| b80087a3-e9d4-5b51-b221-e919782a47d9 | button | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified. | Yes,N/A
| 0b0c389b-3d04-5346-8f0e-b749b10653b8 | button | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar. | Yes,N/A
| d7b90cd5-d26d-59ba-a2ca-bcc9bc25eda9 | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
| 0446e561-c9d9-5630-b4ad-798c60a6f177 | button | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
| fff326f4-0626-549c-9c70-089eddf9712e | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
| 8220372a-9629-58cb-bdf2-82841819e1ab | button | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel. | Yes,N/A
| 03850317-cde5-56d2-90d4-7fae72b8d740 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
| 4f1bbce8-df8e-5618-97fe-62e8490c16aa | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
| 5c719c2c-97ad-5a62-b4f4-e9fc4f9153d5 | button | Equipment IP, Ex ratings correct. Check tightness for all circuit connections | Yes,N/A
| 20466e59-6242-5e19-a77e-564aa2b79e5c | button | All internal cables and wiring is correctly numbered, colour coded and terminated | Yes,N/A
| ed3ac326-d2ab-5507-ae04-985e7073ccb9 | button | Check internals for cleanliness | Yes,N/A
| d7341fc1-d03d-574e-a6bd-cca9d9310a9c | button | Relays Metering and Protection ratings are correct as per design | Yes,N/A
| f5a2e9ce-84fc-5160-9da7-d929e789d1c9 | button | As-builts complete | Yes,N/A
| 32ade207-6862-52c6-8198-01fc03063955 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-10 Electrical Equipment Package |  | ITR-E-10 Electrical Equipment Package |  |  | 14b0fefb-dc8d-4b52-8a96-e94932c9d045
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Electrical Equipment Package
| a653f675-cd6f-54c8-83d7-8230ebb413b5 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| a1feedf7-3fac-58b0-9598-656fa014bb3f | button | Check equipment is correctly rated for the area. | Yes,N/A
| ce4421ed-2ca4-5d42-a5b4-e65b28a4cc18 | button | Check if package is complete with all accessories. | Yes,N/A
| 36250694-871f-5d79-94f9-b853078fbc96 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
| 344c790e-0179-5791-bce5-36c9b960d5d5 | button | All transportation supports, stops and fastenings removed. | Yes,N/A
| ae614b3b-8d50-5294-9511-9e310d3d7fb5 | button | Package fixing down bolts/shims/washers installed and tensioned. | Yes,N/A
| 961425d5-67e3-5500-88ab-64d3191c0008 | button | Check package is installed on a level plane. | Yes,N/A
| 26dcbfc8-1bda-5197-b492-1e0a455d1b9e | button | External cabling (if required) correctly installed. | Yes,N/A
| c40ee6a6-391d-58ab-883a-90480a6d0af1 | button | Internal equipment installed and all tests complete and accepted. | Yes,N/A
| 41ff1178-4c39-595c-9c7c-0756d8a7dd50 | button | Verify package using vendor and/or project P&IDs. | Yes,N/A
| 9c777f4f-add8-5e8f-8e70-7a34a807bb09 | button | Check that equipment is correctly earthed. | Yes,N/A
| 0f141883-c1ca-59e5-9f39-74adf80db68d | textbox | Test and confirm the earth resistance between equipment and local earth system is <1.0 Ohm |  |  |  | Ohm
| 677124df-ba56-560a-bda2-968e6d5397d9 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-11 Generator Package (LV) |  | ITR-E-11 Generator Package (LV) |  |  | a6fc6ca6-7020-46ff-8ac0-5f4158d7f3af
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Generator Package (LV)
| d5f19b17-fdd3-54df-80d0-1a7c358a566a | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| 53a0ef6a-af12-59ac-a919-30b5352ee75d | button | No mechanical damage and paintwork in good condition. | Yes,N/A
| 1eaffccf-a7a7-5057-a5c0-98bb42ff0fb5 | button | Check terminal boxes and glanding correct. | Yes,N/A
| 8c5d9104-f4f0-5156-b6c5-a5c75982e36c | button | Instruments correctly installed. | Yes,N/A
| 3a34dc6f-0f7f-56c6-9f85-5e71d2b56127 | button | Heaters correctly installed. | Yes,N/A
| 9940f5c5-c9b9-5831-856e-8209978cde59 | button | Check unit for cleanliness. | Yes,N/A
| 08f6fd07-18af-5b6f-a33a-9295e916f800 | button | Check manual operation of selector switches, MCB, push buttons etc. | Yes,N/A
| 2c7c08c4-e1c4-5cab-a17e-db53bc7465e3 | button | External cabling correctly installed. | Yes,N/A
| 69c6db30-17d8-5b53-9686-840c94670d13 | button | Protection of live parts adequate. | Yes,N/A
| fc7e54e7-6799-5192-a56c-b32d31bf53e4 | button | Main terminal box complete and terminations correct torque. | Yes,N/A
| 10111d93-183b-5ede-bf2c-b2fe08510b06 | button | Ensure direction of rotation is clearly marked. | Yes,N/A
| e9dbf813-2afc-5e86-94f2-bbf0056090d4 | button | Check gasket and seals are not damaged. | Yes,N/A
| 339c9c97-8e80-556e-acf1-d79415ae023c | button | Unused cable entries are correctly sealed. | Yes,N/A
|  | checkpoint | Electrical Checks
| e946553c-c592-5921-89a1-cb0dbedf8d27 | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
| ca63d6f9-54b5-52b0-a361-621abf60fe81 | textbox | Heater circuit insulation resistance:
| 95a20b13-ce8b-5134-8963-aaedd32db554 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-12 Electrical earthing |  | ITR-E-12 Electrical earthing |  |  | 0a23d377-c2cc-440c-bf5e-c200b8a329a0
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Electrical earthing system installation
| 9d454c7d-3538-55b1-8ee0-6ef16c69c95d | button | Confirm earth grid layout, earth conductors/connections and number of earth electrodes is in accordance with drawings, drawings as-built | Yes,N/A
| c8d5f37f-92d1-5e92-945a-fc41c70e90f9 | button | Ensure that all metal work is earthed as required. | Yes,N/A
| 35065497-a9a2-58b6-b5b8-b1d943bc0ac2 | button | Check welding of earth bosses and associated surface finish. | Yes,N/A
| 30d9230b-88c0-52b0-9a72-c231153ac6fa | button | Ensure that earth cables/conductors/electrodes have adequate mechanical protection i.e. conduits, tobys, kick-plates etc at points of high exposure. | Yes,N/A
| 176cc410-e125-5c4c-b049-63f096fe7863 | button | Ensure that brazing or welding of all joints has been completed correctly. | Yes,N/A
| 9e8b3c7a-61fe-5eb8-94b1-49fb30e1ff68 | button | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses | Yes,N/A
| e0ce1f66-e1f3-55d5-9cac-075b8aa82056 | button | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating. | Yes,N/A
| 10820299-c15b-550b-9964-5098f4184bac | button | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly. | Yes,N/A
| e8da0c69-dd4a-5639-ac34-9342ff56fc7b | button | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements. | Yes,N/A
| 0184597d-57db-5010-ae12-06e2729b33dc | button | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar. | Yes,N/A
| b6b3b4e4-555c-54d0-bb09-6d6ba67b5925 | button | Ensure that earth cable identification markings are in place. | Yes,N/A
| 0120e387-5082-5e1f-897b-d631ae991f79 | button | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible. | Yes,N/A
| 737f1196-597e-56b3-a5d3-716aea2aad14 | button | Check earth bar fixings, mounting points and terminations are tight and secure and conform to project specification (if applicable) | Yes,N/A
|  | checkpoint | Test Results
| a309fdf0-c039-5a02-ba1d-2e1fb8473993 | textbox | Earth continuity test results (Earth bar to Electrode, Grid, etc - please specify)
| 4bfbfc86-19e1-57cb-b053-589d849fe362 | textbox | 3-Wire earth test results (If applicable).
| ba99ed91-9b57-5f57-b090-bdced81a77c0 | textbox | Earth grid test results (if applicable). (HV earth grid, LV earth grid, combined earth grids)
| d21d01b2-3122-5a45-8d94-0ca7d61fbc61 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-13 Motors |  | ITR-E-13 Motors |  |  | 5592593d-a55e-4f7e-bb27-c402da410d1d
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Motors installation
| c5bde57c-b4d2-5d5a-a71e-68e169be28df | tickbox | Tag number, area classification, IP rating correct as per drawings and equipment schedule
| da0e887b-7634-5251-ad8b-07f5e8ff986a | button | Space heater | Yes,N/A
| 9ab9cedd-b751-5644-ac89-0b13950b10a1 | textbox | Space heater specification (Power (Watts) and Voltage:)
|  | checkpoint | Nameplate details correct and in accordance with the data sheet
| d2296419-9749-525e-9b6c-45e1e1904475 | note | Upload clear photo of nameplate
|  | checkpoint | Checklist items
| 26b47f47-c719-5dc9-ace4-d5e0d73d6661 | button | Equipment has been received in good condition and is the correct type as per the site drawings, specifications & data sheets | Yes,N/A
| 0e2a4cef-4b98-5d2c-a91e-c816e1ba5f6d | button | Identification Tag and Rotation Plate correctly fitted | Yes,N/A
| 9fa9aa08-a6eb-5d6c-a2ad-7766026c41f9 | button | Motor electrical coupling (Delta/Star) is correct. | Yes,N/A
| 320f5a25-abe8-5680-91c1-d51c9246a74a | button | Check for mechanical condition, air ducts and fan free of debris | Yes,N/A
| c3c5bbe8-f1ee-5b9e-9f0a-6b7bc501d2dd | button | Correct glanding for area classification. | Yes,N/A
| a31361ac-7bd0-581f-99ba-b0ca2ef8067f | button | Holding down bolts fitted correctly. | Yes,N/A
| 20748e93-d349-5413-bfac-946ff4efe518 | button | Check bearing lubrication, free rotation with shaft uncoupled | Yes,N/A
| dcb95e19-f430-53bc-978d-cc90cb94a51c | button | Cable(s) correctly terminated, labelled and colour identification | Yes,N/A
| a05a5da8-054d-578a-9836-8ac55ea2f4da | button | Terminations/connections torqued correctly to data sheets. | Yes,N/A
|  | checkpoint | Motor Installation Testing
| fc5c06f7-00ae-557c-bbe5-ff3dafd9b473 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 1 minute test
| 25c0d8bf-3308-5d4b-a363-8a67c432a50e | note | Insulation resistance U, V, W
| 83d4c820-fc82-531e-a586-0e7be554fb64 | textbox | LV Motor winding insulation resistance with supply cables disconnected; 10 minute test
| 4573b788-3865-5e94-a809-a24fc07a2408 | note | Insulation resistance U, V, W
| 488cc0a0-b769-570b-af0c-b615b5de53a7 | textbox | Motor continuity between windings
| c334a1a3-4c7a-517b-99f8-b3ad7231809d | note | Continuity U1-U2, V1-V2, W1-W2.
| b82c388c-fa44-5788-be2c-b8c6a45c4228 | textbox | Space heater continuity & resistance check
| ee2855a7-5586-5809-a744-016c88b6857b | note | Continuity & Insulation resistance results:
| bb95c1f8-c11d-5359-98fb-b56da56f0a46 | textbox | Thermostat or RTD wiring resistance check
| 0140f36c-a45e-547f-995e-2fcb86c79cf2 | note | Resistance:
| 37209ae2-2b2c-5d43-ba5c-021ffd038d29 | textbox | Check motor is earthed correctly and record motor earth bond:
|  | checkpoint | Additional checks
| 393f3f2a-9724-5485-b96f-a88ee40d5db5 | tickbox | Winding temperature detector
| ff2585e8-9f06-573a-8e6d-9c4c12fe11c8 | tickbox | Air temp detectors
| 80752eb3-bd13-545f-9d53-5e927d8fea86 | tickbox | Bearing temp indicators
| d6817326-cabe-503c-9aac-604374762294 | tickbox | Vibration Monitors
| 12d9afbc-1f31-5573-85ab-12bfaf8063b1 | tickbox | Condensation detector
| e4b603cc-ca1c-5309-8368-0587dab0dc9f | button | All spare entries in terminal boxes have been blanked off correctly (with certified plugs if applicable) | Yes,N/A
| e6ddd3d1-e61e-5990-86b6-3d90e45a311d | button | Inspect all Ex "d" terminal box flange surfaces and apply approved grease (if applicable) | Yes,N/A
| b13a7b50-e706-504e-86e3-024958f03676 | button | Installation conforms to specification and drawings | Yes,N/A
| 473a530e-da13-5f61-a75a-f04a1ec53bce | button | As-Builts complete | Yes,N/A
| 665ddcbb-e3be-5b1e-9ca3-88995b1780f3 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-14 Motor Control |  | ITR-E-14 Motor Control |  |  | 71817389-12d3-470b-aa20-a7c07666aa13
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | General Motor Control
| 686f3d13-a836-5bc6-8de2-148591d02b2e | button | Check all labelling and warning signs are correctly installed and visible | Yes,N/A
| ea2e020f-939b-52bd-9bba-415c8ad04567 | button | Check control equipment is clean and free from dust, debris and tools, no mechanical damage | Yes,N/A
| ad5f8ba0-6f0a-536c-8d60-92b0cbb19da8 | button | Check preservation and transit items are removed | Yes,N/A
| ee0d82c5-eb47-5731-8b39-d589f177b0fc | button | Check correct earthing is installed as per design from earth grid to the controls, the cable trays and the motor | Yes,N/A
| 814bd15e-fbee-5fc0-883d-dbb183810044 | button | Check all cabling to control gear and motor is undamaged, supported and tidy | Yes,N/A
| 1b72414e-e568-534c-b1ea-8936b9ba17c1 | button | Check earthing bar and connections are correct and tight | Yes,N/A
| 3ca14071-0090-55f5-986f-b93d24e753cb | button | Check incoming and outgoing power cables are terminated and glanded correctly | Yes,N/A
| f3e7ab2c-51e2-5b3a-b9a9-45fc60466a91 | button | Check phase identification on power cables is correct and visible | Yes,N/A
| c079cb83-6402-5d36-9ded-544b297c7b07 | button | Check incoming connections U1, V1, W1, outgoing connections U2, V2, W2, busbars and connecting links are correct and tightened to required torque | Yes,N/A
| 96a0fd2b-0dca-5c72-a226-c47f8c97031c | button | Check all other nuts and bolts are tight | Yes,N/A
| 4b6d7df8-ebc1-568a-b181-0c35aad8b258 | button | Check spare gland entries are plugged with correct rated plugs | Yes,N/A
| edcc4d2f-38db-5718-a1c2-7408e39ef3ea | button | Check all doors, drive cover, motor connection box and other protective guards are installed correctly and all live parts are protected | Yes,N/A
|  | checkpoint | Variable Speed Drives (VSD)
| bd8f2688-ca7d-57cc-8d71-d642d340d74b | note | Record VSD Details
| ba42d8a9-aabb-5689-a2c3-1d67a63188db | textbox | Volts (Input) |  |  |  | V
| b0df91f1-a649-5f36-8af6-43bdefc65b93 | textbox | Amps (Input) |  |  |  | A
| ba1588f2-6246-5549-ab61-bdd65d6be7e1 | textbox | Amps (Output) |  |  |  | A
| 93012617-cc20-520c-ab38-b14c0095d8e6 | button | Check mains Voltage (usually 690VAC) matches VSD nominal voltage (input) | Yes,N/A
| d97f8173-fe5a-5a5f-a70f-3aa8f319178b | button | Check input power and motor cables are appropriate and capable of carrying the load current. For motors >30kW a symmetrical shielded motor cable must be used. | Yes,N/A
| 4a102cb6-b6a4-5252-9278-df5d0d22e9db | button | Check all internal cabling and auxiliary wiring is complete as per latest design drawing, properly supported, neat and undamaged | Yes,N/A
| 3e5509c4-65f3-550f-a21c-c6938cc1fdd0 | button | Check control signal cables use twisted pairs | Yes,N/A
| bf779d73-d5e5-5c57-8924-0268c2833143 | button | Check control signal and profibus cables shield is earthed at one end | Yes,N/A
| 5b1454ad-e15b-53ff-83d2-32834b25b7b2 | button | Check analogue and digital signals are run in separate cables | Yes,N/A
|  | checkpoint | Voltage segregation
| 3f77c5c2-3b94-5e1e-8e2d-80126ee59556 | button | Distance between input power and motor cable >300mm | Yes,N/A
| 359ed98f-efdd-5381-b410-74eec82aee75 | button | Distance between input power and control signal cable >200mm | Yes,N/A
| 8beab586-4a6b-5b04-9b66-fe38595747b5 | button | Distance between motor cable and control signal cable >500mm | Yes,N/A
| a9cede62-7408-54f5-ae01-84a971a6486c | button | Check there are no power factor compensation capacitors installed on the outgoing power cables | Yes,N/A
| 406bded2-d228-5e43-b610-c948c1a95542 | button | Check gland plates with single core power cables are non-magnetic at VSD and LIS | Yes,N/A
| 676b8551-46e3-528b-afda-5a175e128ea5 | button | Check mains voltage cannot be applied to the VSD output by means of a bypass connection | Yes,N/A
| 412d5f29-d05e-5e7e-8985-612b66d499e4 | button | Check appropriate auxiliary 24VDC fuse / circuit breaker is installed at MCC | Yes,N/A
| 88635866-434d-5561-845b-95caba905a01 | button | Check VSD Incoming Supply has appropriately rated fuse disconnection switch (that can be locked in opened position) | Yes,N/A
| 9a121c72-a36b-52fe-b33f-54951a74cf6a | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-15 - UPS Installation |  | ITR-E-15 - UPS Installation |  |  | 49e0c47e-7dc9-420a-95b3-b73dda68bee5
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | UPS Installation
| c2bb6c3c-3a2a-5bd2-982b-d653f37ff7bb | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
| 1303d628-b073-5625-9ac5-27be208f0a66 | button | Check for mechanical damage. | Yes,N/A
| c59487b9-2b4c-5182-bf27-7a632ee79192 | button | Panel IP rating is correct. | Yes,N/A
| 8d0c60fd-a01c-5408-9a07-9247c9715133 | button | Holding down arrangement and seat alignment correct. | Yes,N/A
| bd19661b-46e1-5980-942e-d28cbbd5a41b | button | Panels aligned correctly. | Yes,N/A
| 38afef63-9746-5e88-be8c-eb1b2b09a17c | button | External bonding correct | Yes,N/A
| c4595ec5-2958-51c0-9278-9b5cf0f75def | button | Phase identification correct. | Yes,N/A
| 4102e402-8b69-54e0-8ac3-844bdf789ceb | button | Instrument, indication lamps & interlocks correct. | Yes,N/A
| c34c4a50-14c2-51b4-b841-5f7e0d9e73a5 | button | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings. | Yes,N/A
| fe0d0a51-75a9-5a62-b6ee-517cad54d6e9 | button | Check Main Isolator and Bypass switch operation | Yes,N/A
| 4f9e92ac-e728-5fd4-9843-e4e077154627 | button | COM Interface & Mod Link. | Yes,N/A
| 2c5f2fd7-d955-50e3-a82f-c41fc04f8481 | button | Padlocking facilities correct. | Yes,N/A
| 6e602e37-1ed1-528d-9a51-c03d3f93c197 | button | Check internals for cleanliness. | Yes,N/A
| 1aabaa65-7e1c-5bb1-9bf2-1774b2cb4d0c | button | Check manual operation of selector switch, MCB, push button, etc. | Yes,N/A
| baa592d3-5b67-5977-b3c7-4a8058dfd66a | button | Incoming cable correctly installed, terminated & supported. | Yes,N/A
| 86990802-a510-5da2-96ce-d70aa1915648 | button | All internal cabling & wiring neat, correct & tight. Unused cable entries sealed. | Yes,N/A
| 5b1dba39-96b3-5873-b51d-e5123922977b | button | Drawings marked up with relevant changes and As-builts complete. | Yes,N/A
|  | checkpoint | Test results
| 98e41d0d-874d-5075-98a2-b1e147642428 | textbox | Earth Continuity, Insulation Resistance, Temperature, Phase Rotation, Polarity.
| 61e0261e-01bf-5faf-9189-133588bd2e1d | textbox | Installed by:
|  | signoff | Client Representative:
folder-progress has incorrect meta.stepType checklist-sectioned |  | checklist | ITR-E-15 UPS Installation |  | ITR-E-15 UPS Installation |  |  | a4eedcee-695a-4698-9610-d2e4bda8cfe1
|  | checklist | ITR-E-16 Lightning Protection |  | ITR-E-16 Lightning Protection |  |  | f7353512-b549-41e2-9ffd-ff0d1f25bddf
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Lightning Protection Earthing system
| 03de160b-94f9-5fba-9ab5-96538e0fb159 | button | All checks done in accordance with Client specification, drawings and AS/NZS 1768:2007 | Yes,N/A
| ec62fb85-917f-5ac5-ae01-49de04d5ea7d | button | Lightning conductor is 2 metres or more above the entire protected area | Yes,N/A
| 0c4854b4-9cf2-5124-85e7-7d4e3a5371d9 | button | Check the materials and equipment used for the down conductors are suitable | Yes,N/A
| 361509b3-e73c-5e90-affc-48d639c4c4f8 | button | Check the down conductors are routed, located and electrically bonded as required | Yes,N/A
| 0fdd6b5c-86dd-57ec-81e6-cb437801f33c | button | Check all installed components are firmly secured | Yes,N/A
| 9c90aefd-6514-545e-a7dc-2c74da8d106d | button | Check the method of protection against electric shock, including the measurement of distances | Yes,N/A
| 91133551-ce2d-5acd-a7b6-96a610e4de2e | button | Check earth termination systems are interconnected | Yes,N/A
| 01906048-e544-5290-8ff7-90e62962b4d1 | button | Check isolating and switching devices correctly located | Yes,N/A
| b5cab2ea-4664-5f68-bf93-6f35623643a4 | button | Check warning signs and diagrams are installed | Yes,N/A
| 78d419f8-876d-5414-a748-c599718912b9 | button | Check accessibility for operation and maintenance | Yes,N/A
|  | checkpoint | Test Results
| d0885730-33d2-5c8f-afd7-5b9031775f02 | textbox | Resistance of all connections at the location of the connection. (The resistance of each connection shall not exceed 0.05 Ohm) |  |  |  | Ohm
| 65965911-6d26-5deb-b387-351d4babf32f | textbox | Earth termination system resistance is correct and record value |  |  |  | Ohm
| 252a6e8a-c394-5093-aee5-cb902e85354d | textbox | Record the insulation resistance of the electrical installation |  |  |  | MegaOhm
| c4ad09fa-3938-5326-abe4-0a81547b22ec | textbox | Continuity of the main and supplementary equipotential bonding: |  |  |  | Ohm
| e89cb3bb-cc4f-549c-92b2-03b9ce600f1a | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-021B Cable Supports Above Ground |  | ITR-E-021B Cable Supports Above Ground |  |  | 3a1bd203-0e50-4a8f-9e1d-a9d8fc92ff2c
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Cable Supports Above Ground
| 502e1dcc-60e7-51df-a529-01aa1d9ac0ca | button | Verify cable support has been installed as per relevant drawings, and is correct size and type. | Yes,N/A
| a6d7a012-8df0-56f7-a2db-7b8e92d262aa | button | Check all machined parts cut or drilled have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection. | Yes,N/A
| 2a8bf18c-256d-586f-8fc4-3d80529a221b | button | All covers fitted if applicable. | Yes,N/A
| f1c73d17-3ba3-57d2-ba8d-822cf5ca36f9 | button | Check cable support structures are adequately fixed and present no hazard to personnel. | Yes,N/A
| 15e23bed-250e-57d8-93fa-4dfb820f8b65 | button | Welded support brackets have been wire-brushed and painted to completion. | Yes,N/A
| 2fd04392-f7e8-5227-8096-a68a77207e8d | button | Splice plates, barriers, earthing system secure. | Yes,N/A
| 73cf8046-db89-5a2d-a92b-7b5d8ea02887 | button | Trays / ladders, supports, brackets not interfering with other disciplines. | Yes,N/A
| d04de691-07be-5761-afc8-abe1f1d3b882 | button | Check bends do not exceed the maximum cable bending radius. | Yes,N/A
| 4922c7d4-3e67-5e96-b69b-1bb8d08cebb6 | button | Cables have adequate mechanical protection as and where required. | Yes,N/A
| 0ceb7778-2b70-5f5d-949e-8df3a089c2a2 | button | Inspect for system rigidity, and check levels to correct plane. | Yes,N/A
| e4e96509-8445-5d19-b8b7-a367f8908bd2 | button | Earth bonding straps have been fitted to any sections that are split, hinged or flexible. | Yes,N/A
| e46f2cfc-e9ad-5562-8179-d43d6a549abf | textbox | Record GPS coordinates End 1
| 0e9d595d-1e62-5624-beab-7bed7668ca3b | textbox | Record GPS coordinates End 2
| cbbf4357-8f92-56be-b9e8-e4a78dbc5ed1 | button | Tray bonded to structure at correct locations. | Yes,N/A
| 565f60aa-6400-58af-9114-f57c4e18f01f | button | Earth bonding continuity tested – record result: | Yes,N/A
| 850333c8-72ad-5a5a-93bd-a14da45ebb89 | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-E-29 Cat 6 Communication Cable |  | ITR-E-29 Cat 6 Communication Cable |  |  | 7ea52b2b-e44b-488e-be74-45abf6b2ecc3
|  | checkpoint | Common to all circuits
| 14315019-2211-5187-9df5-7af99b85e063 | button | check cable for damage | Yes, N/A
| 75368809-8f59-5194-8267-28f06d324b80 | button | Check cable is correctly identified and labelled | Yes, N/A
| 5fd7d8d2-856a-5326-a4c4-8da73c461f93 | button | Check glanding/locknuts correctly installed | Yes, N/A
| c1827c12-a3df-54ee-809e-ffa9aec51afa | button | Confirm cable routing and segregation is correct | Yes, N/A
| 6828fd9d-9334-55d1-ae0f-c634cb20a630 | button | Confirm to and from destination as per design. | Yes, N/A
|  | checkpoint | Data Circuits
| e627a857-5acc-5dfd-8234-d3852e45d531 | button | Check cable terminated with correct crimps | Yes, N/A
| c00e5e0f-3ddb-55c1-8547-2c1c30557af7 | button | Check sheild/screen correctly made off | Yes, N/A
| 6bd63312-d4fe-5ecf-8e15-b1225b64d3cf | button | Check Cat6 end-to-end certification (outlet and cable) | Yes, N/A
| 234c4201-1ca2-58ac-99af-aeea81d863be | textbox | Installed by: | Yes, N/A
|  | signoff | Client Representative:
|  | checklist | ITR-E-30 Earthing Electrodes |  | ITR-E-30 Earthing Electrodes |  |  | 8b434b84-bd05-4e72-b092-acfd688e3367
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | Details
| b821d876-4789-5be5-a9c8-30198b563fef | textbox | Location of electrodes:
| 444b76b5-6e9f-51b2-9436-e078e1e41625 | textbox | Electrode length/size:
| d78d9e09-5021-591b-8cfc-60edb82b6cb4 | textbox | Electrode type:
| 22df744a-d12a-5bf1-841a-53a55560de3f | textbox | Method of installing electrode:
| 8f541568-0adf-5d20-8ae5-916b7d45b38a | textbox | Method of attatching to electrode (E.g. Clamp, cadweld, lug/bolt):
| ed2511e3-4594-5c08-a8a8-b0b210ee030e | textbox | No. of electrodes:
| c18a9712-7cc0-5dd8-97e0-1d93b7d3e6b2 | button | Earth pits correct as per specifications, covers, no damage | Yes,N/A
| 611b75e6-e5e2-519d-8dbc-3450f46baab6 | button | Connections to electrodes are secure | Yes,N/A
| 75989239-63ef-536e-bcc7-dd8b6403beda | button | Structural and equipment earth connections secure | Yes,N/A
| 3978ee3c-d4cd-5e02-8062-a2b84e5a46b1 | button | Earth cable lugs secure, cable passes through concrete in PVC. | Yes,N/A
| 37b51c8a-d4ec-572b-997b-88a5cd3c7085 | button | Equipment bonding, connection to main earth bar secure | Yes,N/A
| b2bc7d4e-aa21-59fd-8523-b3903dfac2c2 | button | Earth electrode identified, MEN linked, installed and labeled | Yes,N/A
| c3d06196-6e3f-55ec-b7f4-4bb847f34e2e | textbox | Insert any relevant test results:
|  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | ITR-E-34A Low Voltage Switch Board |  | ITR-E-34A Low Voltage Switch Board |  |  | ca6c14af-7b72-4dd7-808c-355d3c8c5a1d
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Low Voltage Switch Board
| a0261057-cfb3-57b7-80c1-92a83ce8d27e | button | Check equipment and nameplate details are correct and in accordance with the data sheet and equipment schedule. | Yes,N/A
| b3c42ed7-3aa6-5706-9829-bdd3bb912616 | button | Check holding down/mounting arrangement is correct. | Yes,N/A
| b165d78d-7526-5cf9-8481-bd509bc6b1d6 | button | Check for mechanical damage. | Yes,N/A
| 3f13cf31-3e71-5ced-852e-dbb3b7b896cd | button | Confirm that all temporary supports, jumpers and ties have been removed. | Yes,N/A
| 123d1d61-29d9-5251-ad49-be822cb9d11d | button | Incoming cables correctly installed, terminated and supported. | Yes,N/A
| cae874c9-9d91-5ff1-80b6-52ebad8aea19 | button | Phase identification correct. | Yes,N/A
| 5c57cdf0-ca2c-5f95-8ece-fd82075d62ff | button | Confirm that padlocking facilities are provided and operate correctly allowing all circuit breakers to be locked in the open position and safety shutters locked in the closed position. | Yes,N/A
| 266919d7-f55d-5893-ae19-8e80131b7d9e | button | Confirm all cubicle doors can be opened without obstruction and minimum required clearances are retained | Yes,N/A
| 145ca052-7e66-5ca8-8afe-2d38cf98209c | button | Bus bar terminations tightened to specified torque | Yes,N/A
| 5a3ac355-8ed6-551a-bbeb-5d240b314fce | button | Confirm components, fuses etc. correctly sized and identified as per design drawings and Single Line Diagrams. | Yes,N/A
| c0a43810-9c40-5ec1-9c8a-01e61a8bed8f | button | Instruments, indication lamps and interlocks correct. | Yes,N/A
| 85773e7b-a74f-50de-a169-a5ee6981f99b | button | Ammeter and current transformer correctly installed. | Yes,N/A
| dc987bf8-d192-515b-aa35-2c5fc66ceea1 | button | Check internals for cleanliness. | Yes,N/A
| 264a0354-024a-5960-999e-1a53b988a68d | button | Check that Switchboard is correctly earthed. Check door, escutcheon, gland plate, gland and frame. | Yes,N/A
| a0217ea8-9ccb-539f-8ca8-06c89f685446 | textbox | Test and confirm the earth resistance between switchboard and local earth system is less than 0.5ohms
| 088c1c5b-f554-5ab2-9a6d-224bca03bf2a | button | All internal cabling and wiring neat, correct, and undamaged. | Yes,N/A
| 567fc932-59b0-5bf5-8ae6-55e6bd54900a | button | Unused cable entry sealed. | Yes,N/A
| e0b657ec-086b-5671-bee2-d1d2377af26a | button | Heaters correctly installed. | Yes,N/A
| b06f42db-c7d1-56fd-9968-5f1b53a95425 | button | Confirm that all insulating bushings and barriers are satisfactory. | Yes,N/A
|  | checkpoint | Check Busbar insulation resistance between earth and phases. For a duration of 60 seconds with the following voltages. System KV Test V (dc) Min IR Reading <1.0 500 10 MΩ <2.5 1000 50 MΩ < 4.6 2500 100 MΩ >4.6 5000 250 MΩ
| c90719b8-315e-58c2-a4d4-0f3b1cd7d824 | textbox | L1 - Earth |  |  |  | mega ohms
| c47c759e-be69-52c6-87d2-36a2c52f9943 | textbox | L2 - Earth |  |  |  | mega ohms
| 6ab742fa-7498-521a-beb5-6b8db0d85afd | textbox | L3 - Earth |  |  |  | mega ohms
| 70dfcb89-eb3f-54bd-8da5-6bcc2030f3a7 | textbox | L1 - L2 |  |  |  | mega ohms
| ad79b9a9-5acc-5aa4-825c-1aaa43703d93 | textbox | L1 - L3 |  |  |  | mega ohms
| c469756b-d254-5ee4-9607-e84996075f31 | textbox | L2 - L3 |  |  |  | mega ohms
| ca693dbd-042a-5c20-8476-f7c8830e8ea6 | textbox | N - Earth |  |  |  | mega ohms
|  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | ITR-E-40A Bus Bar |  | ITR-E-40A Bus Bar |  |  | d08f32f1-522f-4db0-a537-7e56a712177c
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Bus Bar
| d335304f-1e76-59ef-bb15-2bc2e9b80410 | button | Check entire Bus Bar and confirm there is no damage | Yes,N/A
| 1f442c99-5a5d-54f6-989b-182e53c1ce64 | textbox | Verify zone bus-bar is rated for
| 811a7d73-fc04-5504-b791-98654f5d6e04 | note | Please attatch photo of Bus Bar
| d47f91a5-e117-590f-98c0-4803431eea23 | button | Bus Bar alignment is correct | Yes,N/A
| a62ce469-20d0-5b2a-98a8-bc8ec7885109 | button | Confirm all jointing bolts are present and have been torque tested in accordance with the manufacturer and design requirements. Acceptable Bus Bar Torque Settings: Bolt: M6 M8 M10 M12 M16 Torque: 10Nm 20Nm 30Nm 40Nm 60Nm | Yes,N/A
| 9dea6744-403d-5267-af6e-22a46b342f3e | button | Confirm all transit packing and preservation materials have been removed. | Yes,N/A
| 1c22e84d-1e5c-5033-b96b-f30956139082 | button | Confirm Bus Bar clearances conform to manufactures and design requirements. | Yes,N/A
| ef2c9716-7646-5c4a-997d-e7b643d95832 | button | Confirm all Bus Bars are secure within the supports. | Yes,N/A
| 0ade9cf3-cf24-528b-9cc8-dd533dd7cd78 | textbox | Record the total number of bus bar joints.
|  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | ITR-E-64 General Lighting |  | ITR-E-64 General Lighting |  |  | 43e0e4b0-0591-48d6-9a9a-dde613f93b75
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | General Lighting
| c960bfe6-82ed-5856-a538-e73c4e15f706 | button | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule. | Yes,N/A
| 404363c9-8026-50e1-9c43-483c1c5dad57 | button | No mechanical damage and paintwork in good condition. | Yes,N/A
| c7b0807d-5fac-525b-a348-11b2cfdeff7d | button | Operation of emergency lighting fixtures checked | Yes,N/A
| 146a3011-4291-59c9-a455-020fc1a84fcf | button | Mounting arrangement and degree unit is installed is correct | Yes,N/A
| 18a9cde5-5b10-5351-8512-ee648d64e562 | button | External cabling is correctly installed and labelled. | Yes,N/A
| 28798d33-69f9-524c-9532-69ee768fafb2 | button | Battery run-down test per manufacturers specification | Yes,N/A
| 68e86261-df54-5111-b27d-db99f753d63d | button | Power / load balance on distribution board checked | Yes,N/A
| 1ec42513-1dbc-5136-9d65-aecfb955fe79 | button | Operation of remote lighting control checked | Yes,N/A
| 5c334361-7d61-5029-9bcd-a17cf8007d8b | button | All spare entries blanked off with correct plugs. | Yes,N/A
| d5ed7940-3531-5dc8-bd51-e951972bed07 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
| cd509c74-467e-53f0-9dd1-9849d4557d99 | button | Conforms to Specifications and Drawings. | Yes,N/A
| 090f60a8-2658-5b40-b292-63c25e7bd1dd | button | Insulation resistance of final sub-circuits checked | Yes,N/A
| 3ae4c759-0b12-59d5-852c-c4480d062ca8 | button | Operation of photo-electric cell control checked | Yes,N/A
| 7e1a7605-9f3e-568a-af10-d5f8727835b1 | button | Lighting pole is adequately earthed | Yes,N/A
| 912055fa-6136-5f70-be33-fc2aa711e3b0 | button | Circuit ID fitted to all light switches | Yes,N/A
| 66e66d0c-a133-5c04-a7f4-b4b3cdf2e1d1 | button | All fittings correctly labelled | Yes,N/A
| 203deab3-7883-5f0c-bf33-28df89dcd169 | button | All switching tested and confirmed as correct (two way, intermediate, on/off/auto etc | Yes,N/A
| ae280a2b-4edd-5af9-9c89-83f1521e60bb | button | As-Built drawings completed | Yes,N/A
|  | checkpoint | Lux Levels
| 66c0316b-b0b5-5dcb-a182-9350f6d6ff67 | button | Lux levels meet minimum client specifications. (Closed door and measure lux level at darkest point of personnel accessible area) | Yes,N/A
| 43caf231-5342-5605-9c99-e1ce06d3e93c | textbox | Lux Results:
|  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | ITR-I-01 Fire and Gas Detection Alarms |  | ITR-I-01 Fire and Gas Detection Alarms |  |  | 8878ddfe-d8b5-4565-9180-c51f0da9a828
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Fire and Gas detection alarms
| cdb7122d-5734-555f-82e5-6e0a5ecca9a3 | textbox | Make and Model
| eb8350d9-bc63-5faa-a0ca-a0686866c098 | textbox | Type
| 44f9cbf5-465f-500d-b912-c7b177b57c2f | button | Location correct as per drawings | Yes,N/A
| 9cf43f45-007a-51f5-acd1-cdade6ccbc62 | button | Component & Type / Model correct per equipment schedule | Yes,N/A
| 66e9d9aa-4ea3-5b24-b419-6fdcfeed51f0 | button | Cable connection & termination correct | Yes,N/A
| 0737699b-f30c-5c79-b1c3-bcb7b0859ed5 | button | Installation free of mechanical damage and clean | Yes,N/A
| e54571f3-15fa-5324-a767-11dc17f410c6 | button | Glanding correct and spare entries plugged with correctly rated plug | Yes,N/A
| 947afd06-af7f-5652-a2b0-c5415f303423 | button | E.O.L Installation | Yes,N/A
| ca7b2b2b-4c13-58d4-83fb-c37a5df0683b | button | Test tubing installation | Yes,N/A
| 7ef36585-8a6e-5721-9a59-d931b92f54f0 | button | Detection Path Clear | Yes,N/A
|  | checkpoint | Inspection
| a2a0e7fe-4688-5c3e-889e-7889eaf68d8d | textbox | Tag No.
| 8d1a9a07-a139-5e8a-98e9-80226034ec48 | textbox | RX Tag No:
| 5fb2513b-c354-591e-b63d-62830cf43c28 | button | Area Classification correct | Yes,N/A
| 2fc6e387-81f0-5e3e-9c4c-95f0573084c9 | textbox | Hazardous Area Certificate:
| f73f9cc0-1a40-548c-9653-23773450c7b6 | textbox | Detector Type:
| 92609335-3d50-5390-a749-3e1c1388a6a6 | textbox | Gas Type:
| dce4b8f9-ac29-55da-a813-33236afada22 | textbox | Supply Voltage:
| 67bd3eb8-c2fa-531c-b1ba-49e06d4f9885 | textbox | Output Signal:
|  | checkpoint | Functional Check
| 0652ea71-72ad-59de-a28b-a580fe047e55 | button | Self Test | Yes,N/A
| fda43ee5-6830-50a2-88fe-bbb78f940ca5 | button | Alarm Operation | Yes,N/A
| 524deab1-dd8c-54f4-a607-e5f2f9970844 | button | Fault Relay Operation | Yes,N/A
| 63d6dda8-28e7-5a6c-bd47-2d13679d0c03 | textbox | Measured output (clear path)
| 4876feda-20be-5706-b2ce-d57d259bdca5 | textbox | Measured output (blocked path)
| d0144758-a282-58e6-a86a-a16dd0c41702 | textbox | Measured output (filter in place)
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-02 Instrument Tubing Installation |  | ITR-I-02 Instrument Tubing Installation |  |  | 534027ae-e23e-4aa9-ab1b-71b4fccf06c2
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Checks Pre-Installation
| 038140c8-b501-5a5c-842f-1ddcc16f67db | button | Tubing connection to and from equipment as per drawings. | Yes,N/A
| 77b627d2-1356-59c8-92b1-6a65405b050d | button | Tube material type, size, gauge and standard confirmed and available | Yes,N/A
| d61d2b96-c245-5c7a-903a-cfc984b8aa66 | button | Tube fitting size and type confirmed and available | Yes,N/A
|  | checkpoint | Checks During and Post-Installation
| 5813d6aa-8114-5fac-b67e-747e19bc31ef | button | Correct thread compatibility and engagement | Yes,N/A
| 5dd12c7e-da12-55cf-950f-a56cde09c38d | button | Correct thread tape and sealant used on fittings | Yes,N/A
| 6d5ab8a9-aafb-5d1c-96b4-6652ccfcae20 | button | Check fitting ferrule orientation and confirm prior to connection | Yes,N/A
| 4c2a5a5f-ddf6-5ac1-b57f-b062d2866c53 | button | Tube installation is in compliance with the client specification. (Supports, bracketry, slope, expansion, vibration, access, cables) | Yes,N/A
| 28a6dc59-77d1-52fe-83f0-b64378446fea | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
| 78361d3f-561b-5475-84bc-9c2e9038aa38 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
| 4ef602a5-bd2d-569a-90ed-ec57d1481883 | button | Depth insertion tool used; witness mark visible at all stages of process | Yes,N/A
| 3640f307-66c0-5cb2-8490-673c0976150c | button | Tube fitting hexes marked to ensure correct swage tightness | Yes,N/A
| a709424d-887e-54b5-9d60-6b4d43353ebc | button | Random check with No-Go gap gauge | Yes,N/A
| 9f7c3f32-dbfa-5bf7-bede-acfaa93b7ee8 | button | In service leak test performed and passed (ITR-CL-1-118) | Yes,N/A
| 61b3dcf2-8396-5223-b568-642a54fd76b7 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
| 475c2adc-e178-5f9e-ad56-e65f5a936876 | note | Refer to Swagelok book for tube/thread size pressure ratings
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-03 Instrument Pressure/Leak Test |  | ITR-I-03 Instrument Pressure/Leak Test |  |  | 4d9e552c-dbd0-4f53-9d7c-7b9132fc81b2
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Checklist items
| 509028df-369b-5327-aaef-5af450fb0bf2 | button | Tube identification correct | Yes,N/A
| 59d43169-6ef4-5ad5-ab1b-4fcf25a68564 | button | Mechanical damage visual check | Yes,N/A
| c357cf45-c5ca-5046-8f31-b035f2a1711a | button | Flow direction and instrument orientation correct | Yes,N/A
| c8db1e23-e747-5744-a3c8-9899a304cdb1 | button | Tubing size and installation correct | Yes,N/A
|  | checkpoint | Testing
| 9d6d8aa0-2be6-5ff2-b58d-e52f10eab5d1 | note | Verify test pressure and medium is correct per project and manufacture specification prior to test
| 86fa7c71-1328-5833-bd03-720773661c98 | textbox | Test fluid:
| 4d38437a-7172-5500-aacc-fc3a42aa6f33 | textbox | Test pressure:
| 40f8cd2b-02cd-59e5-9f71-ed8959263baa | textbox | Max design pressure:
| c67d4bca-1445-538a-b75c-5c02570aead2 | dropdown | Test pressure unit: | kgf/cm2, PSI, kPa, bar, Other
| 76f19350-42f2-517c-8e73-6da4c4eb1942 | textbox | Duration: |  |  |  | Minutes
| 41c1a8ac-5533-5c70-8d6b-41e8aad94e04 | button | Confirm all impulse lines have been drained and cleaned | Yes,N/A
| 56f86fe6-8713-51a9-b8ca-1a76a4062215 | button | Confirm any temporary test connections, valve etc. are rated for the intended test. | Yes,N/A
| ecb15b9b-3b82-50e4-ba9c-82e38e7e7711 | button | Confirm pneumatic, test gas and aspirator lines have been blown clear. | Yes,N/A
| f96e27fd-69fe-5b84-948b-e9edf8539afa | button | Check hydraulic lines flushed to project specification. | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  | ITR-I-04 Valve & Ancillaries (Pre-Installation) |  |  | 57b202bf-6745-4968-9a2e-23f784ec193d
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Equipment
| 2ca10126-f7ed-5133-aca4-17474c6dc0da | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
| 6cd25b52-8b0d-5d64-b1c6-d59f2e99bab6 | button | Equipment checked for additional items as applicable | Yes,N/A
|  | checkpoint | Valve
| e0720dbb-aced-50e1-af53-288aa540ab3d | textbox | Valve Size:
| 9895ba6a-0846-5d7b-ac0b-16f8faffed6c | textbox | Flange type:
| 758247af-c1b3-53d0-9485-2d9d9b744503 | button | Material certification correct | Yes,N/A
| b5cf21ae-3de5-58c9-b5ea-342db4e57158 | button | Trim material correct | Yes,N/A
| b1c352ae-0bd3-5d84-9322-e998e2af6bdc | textbox | Rating:
| e3e1fcdc-6189-564f-a9a3-ce1bd54b173d | textbox | Service:
| 4e2b8f60-84b1-5c5a-850a-cb9676d917b8 | button | Body material correct | Yes,N/A
| 55f5d838-09f5-5d48-ba3a-8965405fe8f9 | textbox | Leakage class:
|  | checkpoint | Actuator
| 977db039-8db6-5cb7-ac5b-746bbc32ca0c | textbox | Input range: |  |  |  | kPa
| 86abb98a-819a-5624-bcd0-3342ff07ec47 | button | Failure action | Yes,N/A
| 1071d65a-f5ca-5897-9962-cc75c03cc5f2 | button | Hand wheel operation correct | Yes,N/A
|  | checkpoint | Positioner
| 5e906d94-8840-5d64-8f42-eac49554dafc | textbox | Signal range
| e0465090-da92-5901-8457-d65bdafe969e | textbox | Output range
|  | checkpoint | I/P Converter
| 1dcc31f8-474e-51ab-8513-05ca2cf61433 | textbox | Signal range
| fc0df323-ed22-5a39-8af7-38ad9d31c12a | textbox | Output range
|  | checkpoint | Filter/Regulator/On-Off Valve
| e9404bda-e47f-5ce4-a2bf-85b3184c53a6 | textbox | Range |  |  |  | kPa
| 0ea62196-67d4-54e1-82b6-832b8af3eb92 | textbox | Pressure setting |  |  |  | kPa
| 34e330ac-e128-551c-a22c-0eb6135ba3d8 | button | Stroke Time correct | Yes,N/A
| cc6bdeb9-03a1-5ca5-ad91-35956ab80549 | textbox | Open |  |  |  | sec
| 2e924f6d-f699-5a85-ae8b-efaa6359734b | textbox | Close |  |  |  | sec
| a330f21f-4ded-5dad-ad55-4d38f5f31c79 | button | Open/Close times conform to commissioning specifications | Yes,N/A
|  | checkpoint | Fail Action
| 4544604e-6497-5042-8ae0-6d2ddc12b1b2 | dropdown | Electrical Fail Action | FO, FC, FL
| 62f0002b-3185-5f8b-ad9d-128cffa471c2 | dropdown | Motive Force | FO, FC, FL
|  | checkpoint | Valve Field Calibration and Hysteresis Check
| 2c7a5eff-63ff-57a3-8285-c12eecf3abd5 | tickbox | Confirm test equipment is within calibration period prior to testing
| 29018037-eec5-589c-a23a-0c89746cb9af | note | Valve to be calibrated according to manufacturer's data sheet and to be within quoted accuracy.
| aec274f6-8119-5fe2-99a3-345a499ce369 | button | Check at the following range percentages; both rising and falling 0%, 25%, 50%, 75% and 100% | Yes,N/A
|  | checkpoint | Proximity Detectors
| 94ee9dc5-68cf-5bc7-b0ab-ae38760ac2bf | button | Open switch set, correct mode setting | Yes,N/A
| 1da29e09-4009-53ec-a425-8de6be5179d8 | button | Closed switch set, correct mode setting | Yes,N/A
| 3bbb76e0-627a-5a0e-9a16-710f6c0bb8b2 | button | Electrical connections and certification correct | Yes,N/A
|  | checkpoint | Solenoid Valve
| 80204599-c101-558a-bd91-8e2d7b4776f4 | button | Operation correct | Yes,N/A
| f6ea06b1-500e-54b3-ad46-ec9dbbae8731 | button | Electrical connections correct | Yes,N/A
| bdaa4dfd-9746-5a59-9d94-8692c437055c | button | Electrical certification correct | Yes,N/A
| de203014-e49e-5f43-ada8-4ed24754797f | textbox | Voltage: |  |  |  | V
| d8f1675c-9490-550c-9461-bb893df474b2 | button | Pneumatic connections correct | Yes,N/A
| 24e75e0f-18c4-582c-a179-ab49f2ead45e | textbox | Pneumatic pressure |  |  |  | kPa
|  | checkpoint | Pilot Valve
| c0e72848-0e0c-58a7-b51b-631fac175fac | button | Pneumatic connections correct | Yes,N/A
| b9436454-c56a-59a0-a704-549e6e7da1c3 | button | Operation correct | Yes,N/A
| 3be9d9bc-9d7d-5fed-bc53-58acb23cae50 | button | Action/Lockup | Yes,N/A
|  | checkpoint | Hydraulic Actuator
| 668d99f2-8d0f-5cde-9140-b9a19c44e787 | textbox | Working pressure
| 38cc9e91-e284-5293-b8d2-f29978bd08fc | textbox | Manifold pressure
| abd06765-b4f9-5017-a1cc-4899746a0c44 | textbox | Fluid type
| 49d5fc96-f3d6-5a7b-b81d-a4a374e67229 | button | Hydraulic connections correct | Yes,N/A
| 39135ac4-8f9d-5fed-9ccc-3f6360299040 | textbox | Regulator pressure setting
| 929b2c23-3c38-5d1e-8111-c90ffead7d39 | button | Pilot operation correct | Yes,N/A
|  | checkpoint | Accumulator
| 17f3da0c-efd4-5ded-8d4b-8f2ce170c1bf | button | N2 Charge required | Yes,N/A
| d1f7fe26-f867-571f-8976-622851f6e3c7 | textbox | N2 Pre-charge pressure
| 1f2cd819-24a8-56f8-a58a-40616168c621 | textbox | Pressure switch setting
| 3354c003-dd24-5002-8988-3195b5f33392 | textbox | Working pressure
| 34d8aa6f-e896-5b5a-9e65-aa9d8ed2bf3b | textbox | Output range
| 9cd08d0b-a5c4-552f-b65d-4d57779450c8 | button | Volume tank & check valve installed correctly | Yes,N/A
|  | checkpoint | Electric Actuator
| 55a58d07-3d92-5e18-a9db-94ef6f0ded43 | textbox | Voltage:
| 4baa1a94-93bd-562d-9333-15c50334f7ac | button | Electrical certification correct | Yes,N/A
| 32c9ec48-0615-5047-8de6-df9a58325ea7 | button | Electrical connections correct | Yes,N/A
| e7be206d-3520-546d-8133-424305263b7b | button | Remote operation correct | Yes,N/A
| 1b9fda5a-5a36-5e4f-861e-c1736770db75 | button | Local hand operation correct | Yes,N/A
| fb019502-4c9d-5ed7-8190-d664299dbde4 | button | Torque switches and travel stops set | Yes,N/A
|  | checkpoint | Miscellaneous Equipment
| 0a55328f-7e29-5b3f-91ed-d8acdae05333 | textbox | Description
| 67926e3b-c420-58b8-8534-28e4fb86919c | textbox | Manufacturer
| f19d6fa3-b487-508a-83da-150c82707d25 | textbox | Model No:
| 543ab0c8-051e-5ea8-81d2-75926ca6304d | textbox | Serial No:
| 7b5ca16d-ad05-549f-8e61-e2c2d1f47f34 | textbox | Range:
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-05 Analogue Valve & Ancillaries (Pre-Installation) |  | ITR-I-05 Analogue Valve & Ancillaries (Pre-Installation) |  |  | 74ba2d3d-632c-4ed5-bbd3-9e548b155fb3
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Equipment
| c64c261a-6c80-59fa-a361-97b8e22a6322 | button | All equipment checked against correct revision of Instrument index for Manufacturer, Type and Model No. | Yes,N/A
| 03a05d37-eeea-5f69-b684-567ae622e479 | button | Equipment checked for additional items as applicable | Yes,N/A
|  | checkpoint | Valve
| 830f5d9d-812b-5091-8148-9ff625e0b0ef | textbox | Valve Size:
| aec35237-2b35-58ee-9577-3c1fe59d997a | textbox | Flange type:
| dd699b83-3652-566e-b309-21793af07719 | button | Material certification correct | Yes,N/A
| 68bae21c-ba9e-56f9-bebb-a7c74d9a3f84 | button | Trim material correct | Yes,N/A
| 409866c3-d38d-59b7-93d5-45e2b3e2428e | textbox | Rating:
| 28625273-0a22-550c-82e4-47ff82d58d62 | textbox | Service:
| b9242661-6a31-58e1-a88f-6989146e97ae | button | Body material correct | Yes,N/A
| 9659ce4e-51fc-52fe-9d7f-258c30513427 | textbox | Leakage class:
|  | checkpoint | Actuator
| bc142626-e945-5aab-99aa-45485b9cdc15 | textbox | Input range: |  |  |  | kPa
| 9a5eba06-fc41-59fb-979a-3e055d91382e | button | Failure action | Yes,N/A
| 2c78d0bf-d9ed-502c-8b5d-fbbf9c50948e | button | Hand wheel operation correct | Yes,N/A
|  | checkpoint | Positioner
| 971a6747-23e6-5a68-9119-926c6354afb4 | textbox | Signal range
| fb6d9aa3-182d-577e-aae9-40c0f077a868 | textbox | Output range
|  | checkpoint | I/P Converter
| 23562f4c-a0f9-5397-8882-73c38c59791a | textbox | Signal range
| 31074246-3ea0-541d-ba91-21f22f5dcb8b | textbox | Output range
|  | checkpoint | Filter/Regulator
| 7eda178d-414d-5118-8695-a629597dbf42 | textbox | Range |  |  |  | kPa
| 35e9cf9d-7d1f-58ce-9304-214ff1280815 | textbox | Pressure setting |  |  |  | kPa
|  | checkpoint | Fail Action
| 8676ec9b-f779-57c7-8580-5a5730e1252d | dropdown | Electrical Fail Action | FO, FC, FL
| 5f39c53e-cb22-55c5-bae0-015f201af960 | dropdown | Motive Force | FO, FC, FL
|  | checkpoint | Proximity Detectors
| 1574f384-ebf8-53e3-b5f0-2c6c5a009562 | button | Open switch set, correct mode setting | Yes,N/A
| 45247beb-b51a-5d66-a33b-e9fddc18301d | button | Closed switch set, correct mode setting | Yes,N/A
| 2a2a9378-6bf0-5b19-a07a-287c0fe491b8 | button | Electrical connections and certification correct | Yes,N/A
|  | checkpoint | Solenoid Valve
| fd57e0b7-16f7-58ac-8dcb-3be11d33717e | button | Operation correct | Yes,N/A
| f2ef8f85-142b-5cb5-8dfc-9f1d8fd3758e | button | Electrical connections correct | Yes,N/A
| 94e6c587-10b8-5585-ba20-da90236a3e23 | button | Electrical certification correct | Yes,N/A
| 9008672b-845c-5616-8d7e-b905ff6591b3 | textbox | Voltage: |  |  |  | V
| df7cfc4e-9204-5fa7-af72-5c2a0b81b0c3 | button | Pneumatic connections correct | Yes,N/A
| 15a518b2-d6f5-54af-98c5-ca8c015d7cfb | textbox | Pneumatic pressure |  |  |  | kPa
|  | checkpoint | Pilot Valve
| ee800c4d-ad0e-54d3-a6b6-bf6dd4c8a39f | button | Pneumatic connections correct | Yes,N/A
| 4c70722e-35be-5507-b20b-4e8e1f7215cb | button | Operation correct | Yes,N/A
| f575358f-0c99-5236-a67a-8f2f3f5a553b | button | Action/Lockup | Yes,N/A
|  | checkpoint | Hydraulic Actuator
| 8e653d25-4090-595c-9bde-b61285fe1906 | textbox | Working pressure
| e2cd5b19-48d4-5919-be8e-3f2111cd376c | textbox | Manifold pressure
| b977be8d-4c90-53d0-9732-2a7c11796d66 | textbox | Fluid type
| 943700e8-196e-5988-b227-8e3f0924781e | button | Hydraulic connections correct | Yes,N/A
| 65f11454-227a-5cb4-9fd7-2a05e549a15a | textbox | Regulator pressure setting
| 4a2a6602-48c3-5e5d-814b-e93625516843 | button | Pilot operation correct | Yes,N/A
|  | checkpoint | Accumulator
| aac0d10f-2804-5493-bfdf-6ee07efd3b0a | button | N2 Charge required | Yes,N/A
| 9a9bfe33-c08f-53e7-ae28-449e2adb5890 | textbox | N2 Pre-charge pressure
| 5eccb4a5-33b1-580c-ba37-e1253370df35 | textbox | Pressure switch setting
| f5cc3e4f-b79e-5ac3-86a3-db13ab39c16f | textbox | Working pressure
| 8df992dd-a895-5715-abde-fc419671f384 | textbox | Output range
| 5f6c7774-f283-58c6-a697-dab70963fd5f | button | Volume tank & check valve installed correctly | Yes,N/A
|  | checkpoint | Electric Actuator
| 731af0c2-ecf1-51e5-8829-c1ac7b7346e3 | textbox | Voltage:
| 5b17d0a4-529a-5684-b3bc-b212bf4b3137 | button | Electrical certification correct | Yes,N/A
| 3ebb1a56-0876-5a4a-a6e6-3ba0224223a4 | button | Electrical connections correct | Yes,N/A
| 18de8938-ac45-5fef-b18e-7cfb3b509304 | button | Remote operation correct | Yes,N/A
| 65220e15-38a5-5bd5-916c-f350e5f4e351 | button | Local hand operation correct | Yes,N/A
| c000f655-3ba7-59d6-aa40-ed929c23c085 | button | Torque switches and travel stops set | Yes,N/A
|  | checkpoint | Miscellaneous Equipment
| 37415fc8-081a-5b58-a8b3-812e40f4ad81 | textbox | Description
| c62ca60e-fc9e-50b3-8632-f2e2c5efdd42 | textbox | Manufacturer
| 866993af-5942-56c2-8c86-1195c1829d63 | textbox | Model No:
| adf9c868-703d-577a-b1a0-6ab63c67c30c | textbox | Serial No:
| 39ed6722-e7de-56c4-ac96-9f298e14a3ff | textbox | Range:
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-06 Instrument Installation |  | ITR-I-06 Instrument Installation |  |  | bc59667e-6716-40d4-bf38-079096a477cf
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Instrument Installation
| 4a6b0db6-cefd-502f-bb5b-70f7012b1695 | button | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/datasheet. | Yes,N/A
| 56b1d4b8-beb7-53a9-abc7-9fd57e2a133f | button | Instrument is suitably rated for area. (Ex Rating, IP Rating) | Yes,N/A
| c9380884-270a-5dde-8d4b-01e0a9c24ae3 | button | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration. | Yes,N/A
| de0ea07a-72c9-5c47-ac38-d4f626716b94 | button | Instrument is accessible for maintenance and clear of obstruction and debris. | Yes,N/A
| abafd73d-c121-538e-be3b-aca721fab63a | button | Vent lines are directed into a safe area. | Yes,N/A
| 0ef36933-dd56-53d5-bba6-ff5f033cbc22 | button | Cable/s glanded and installed correctly, IP washers fitted, cable label installed. | Yes,N/A
| e20f07bd-39f7-574e-8948-71d3d3457566 | button | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported. | Yes,N/A
| f3159a51-4fe3-5ba4-86c0-709f056f0373 | button | Spare entries plugged correctly, using certified plug. | Yes,N/A
| ee451f8e-68c5-5572-b71a-c6ad533fbd5f | button | Instrument earthed in accordance with project specification. | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-07 Instrument Calibration |  | ITR-I-07 Instrument Calibration |  |  | d1ec96c5-1abd-4241-9a7a-c7722a7726c9
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | Required Data
| 9bce876a-64d8-578f-9bb7-2a5cb73258c7 | textbox | Type and Size:
| e1de4023-9032-5698-a207-b955f756ae2f | textbox | Make and Model:
| 4e97a375-15d7-5f9b-8899-f4415fed569f | textbox | Serial No:
| a6d6e821-42ee-55b4-81a7-c95a56379a60 | textbox | Instrument Type:
| c09725b9-fbb1-5573-b5ae-3bb00febcfa8 | textbox | Instrument designation/equipment no
| f1ae2877-4b19-5125-a7b3-5d6874964b51 | textbox | Calibration interval
| 7d6a3672-e63c-515b-896c-004203732055 | textbox | Calibration method
| d2d7df63-be30-55d7-bd42-014ca73b48e8 | textbox | Calibrated at
|  | checkpoint | Instrument Power Supply
| fd388fda-b607-5040-b5ee-0150da66439d | dropdown | Supply type | VAC, 2 Wire DC, Other, None
| 191bacb8-c776-523b-8e90-6123ea2f00db | textbox | Supply value:
| f57c1a99-04bf-50b5-abcf-e822b449397b | button | Calibration sheet completed and attached below | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-07A Transmitters/Gauges/Hand Valves |  | ITR-I-07A Transmitters/Gauges/Hand Valves |  |  | a7eed241-1831-4255-b4d3-d637950898a1
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | Details
| 5429e776-05cf-51e2-b39f-b6060d38e302 | textbox | Tag No.
| 03aa5fc5-27a5-54f4-9174-027f5836072f | button | Indicator Range Correct | Yes,N/A
| d414ff8a-d4c1-544a-9183-065fd9f628b7 | textbox | Hazardous Area Certificate
| 5c3a0dd6-ed37-5466-9e45-78b0bf9c22aa | button | Shipping stops removed | Yes,N/A
| 43f1809d-1cf2-5968-8a00-4de90100a1b4 | button | Check item is suitably rated for area (E.g. IP rating, Ex rating) | Yes,N/A
| 10d50a21-d894-5e94-bd3a-1e4d80e808f4 | button | Body material is correct | Yes,N/A
| a37363dc-a72b-5d4a-99d8-d79339b1b613 | button | Unit condition is acceptable | Yes,N/A
| 9893110c-8a1f-529c-bceb-b3b88db7bde1 | button | Process connections correct | Yes,N/A
| 4886f581-8b45-58d4-8084-318d2e0f728e | button | Pneumatic/Elec. Connections correct | Yes,N/A
| 3e849124-d2db-5136-94f5-e6cfd5d01886 | button | Supply settings correct | Yes,N/A
| e17d9538-bc6c-5b3a-b08a-98225d700a33 | textbox | Operating Range:
| 3df3b690-4dfd-5441-ba2c-dab7329194c4 | textbox | Output Signal:
| ce321514-5991-597a-81e1-8c7abf2f12fe | textbox | Calibrated Range:
| 0f289888-ae81-59b6-a755-58c8cff007e5 | textbox | Insert any relevant test results:
|  | signoff | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | ITR-I-08 Instrument Pre-Commissioning |  | ITR-I-08 Instrument Pre-Commissioning |  |  | 6602277a-1e5f-4820-b2c1-b855296c31e7
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Checklist items
| 7d0d4ea4-6823-5864-be68-9cf38107888c | button | Verify transmitter loop connection - Remove wre on transmitter and confirm at Control System interface | Yes,N/A
| d8b9b008-666b-5e99-abf6-c1db74c52e97 | button | Relevant individual control system/ESD loops have been checked and test sheets completed | Yes,N/A
|  | checkpoint | Analogue Input:
|  | checkpoint-no-value | Analogue Input:
| ef93edd3-35d4-530c-a643-cbfbd7f73080 | textbox | Input range & units:
| db1179e4-05f5-5842-a9b1-71203772268c | textbox | Indication range & units:
|  | checkpoint-no-value | 0% Rising
| b81edddb-d0cf-508d-8742-fbfa7955dec7 | textbox | Input Signal:
| 8fd63f7f-8332-50a7-8ef4-822e40baa207 | textbox | Control Interface Indication:
|  | checkpoint-no-value | 25% Rising
| ebb02037-2ff1-531f-b2a2-92a5ec2b7050 | textbox | Input Signal:
| 4b345f4b-46e5-5261-ae10-f513848e5c3c | textbox | Control Interface Indication:
|  | checkpoint-no-value | 50% Rising
| 61ad865b-c6d3-5b7f-9649-87bc7a14d2b4 | textbox | Input Signal:
| c611f67f-d459-5a2c-a4f8-ace30213752a | textbox | Control Interface Indication:
|  | checkpoint-no-value | 75% Rising
| daa1c3b9-9c0d-59a0-b291-9eca809a0526 | textbox | Input Signal:
| 881c82e0-c6da-587e-971c-44d6bb1a1d6f | textbox | Control Interface Indication:
|  | checkpoint-no-value | 100% Peak
| 3650757f-d9c8-5d57-becb-09f1a70954fa | textbox | Input Signal:
| 589465b6-b87e-54d8-ab98-07832004e9aa | textbox | Control Interface Indication:
|  | checkpoint-no-value | 75% Falling
| 59bc7211-a36c-5a1c-ada1-7dd40b9b3497 | textbox | Input Signal:
| c371cfd6-cd56-524e-a263-aee75509a02d | textbox | Control Interface Indication:
|  | checkpoint-no-value | 50% Falling
| 6d52f8d3-c015-5e4d-a74a-1042d696147a | textbox | Input Signal:
| b2f0fc2c-2671-5748-b61e-cf68e5e021d9 | textbox | Control Interface Indication:
|  | checkpoint-no-value | 25% Falling
| 19ad08e4-3336-50f9-91cf-9fb1f410e866 | textbox | Input Signal:
| 631c45c7-7d61-5eaa-8516-ae76fd28d747 | textbox | Control Interface Indication:
|  | checkpoint-no-value | 0% Falling
| 8e3113f5-9227-5c96-a479-15613e2515ce | textbox | Input Signal:
| 5649aedf-2148-59fa-a05d-f90ad8210c62 | textbox | Control Interface Indication:
|  | checkpoint | Digital Input/Analogue Alarm Trip Points
|  | checkpoint-no-value | Alarm Lo:
| 2a09f45c-82b9-5e0e-a463-78791743eb25 | textbox | Alarm setting
| 9dc638ad-ced3-5ab8-8cd6-121a86efbede | textbox | Measured Alarm Point
| 3ae6c6b5-5e03-5e23-852f-b5b4ab751aa6 | textbox | Filter/Time Delay
| eea6aca0-35a2-55a5-b470-4f9994dedc90 | textbox | Result
|  | checkpoint-no-value | Alarm Lo-Lo:
| dcc4e247-bd16-55dd-b850-faf65374844c | textbox | Alarm setting
| 918e795e-87ad-5001-b655-12ba8e7c7947 | textbox | Measured Alarm Point
| c468d9da-51e3-5392-893e-08c2bdaa2f29 | textbox | Filter/Time Delay
| bb03fd54-a53e-5b56-8e0b-c81003ffe8e0 | textbox | Result
|  | checkpoint-no-value | Alarm Hi:
| 52a4beaf-7009-549c-86cb-690f98c62324 | textbox | Alarm setting
| 3fb51ab3-4083-54f6-870d-3c538b692ff3 | textbox | Measured Alarm Point
| 9d129847-5acf-5d30-a32b-0ca494edbbde | textbox | Filter/Time Delay
| f6ecd88d-cbf0-51dd-b878-717fde8cff14 | textbox | Result
|  | checkpoint-no-value | Alarm Hi-Hi:
| 8333e281-a13a-5a7e-a37a-aed7aba14a37 | textbox | Alarm setting
| 17e6f04b-bf4e-58b3-a3ec-f1b5240ed7a2 | textbox | Measured Alarm Point
| 37f5c9a4-e209-5078-9a68-255ea05f6f15 | textbox | Filter/Time Delay
| 29a3492b-d5cd-5731-8e3d-cd5e619a4729 | textbox | Result
|  | checkpoint-no-value | Control loop set points correct:
| daf508f6-263e-5a69-82ee-3ae71d7de5c2 | textbox | Set Point 1:
| c18de64a-97d2-516d-b9b7-27c2d93693b9 | textbox | Set Point 2:
| d44513fc-ad74-5f8d-8f10-7352f99e2849 | textbox | Set Point 3:
| 0e8f9e16-18e0-5719-8458-34bbaee29b2b | textbox | Set Point 4:
|  | checkpoint | Startup, Shutdown and Override functions
| 79e626e0-e699-5a85-a82d-01b8e7c5271f | button | Control system graphic display | Yes,N/A
| a8b699b9-b572-5d3b-a771-dea7eb3d0d61 | button | Control system point display | Yes,N/A
| 4dfa3de8-6d3f-5c9f-99fb-2b9b72b62753 | button | ESD graphic display | Yes,N/A
| 1ece6233-a142-580a-b69c-bcc46d8a8989 | button | Alarm Recording and Text | Yes,N/A
|  | checkpoint | Additional checks
| d0aaa4a6-0d19-57a1-a2d7-cdd50109db8d | button | Control system display and alarms are correct as per control functions | Yes,N/A
| f4490aa0-6b90-5783-8dc9-8614686c8ea1 | button | Transmitter fail direction and burnout are to spec (Upscale/Downscale) | Yes,N/A
| 6889205e-f337-5a93-af73-04fcc1ec59ee | button | Switch action verified, including power loss | Yes,N/A
| 119bf7bc-cfb8-5a48-9149-5403d29d7baa | button | Drawings, documents and As-Builts scanned and attached | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-09 Commissioning Instruments |  | ITR-I-09 Commissioning Instruments |  |  | 3d991b9e-d3ab-4405-b65c-e3f8a9e2d4c1
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Required Data
| c11f23b3-055d-50aa-be8e-cd817b71fa72 | textbox | Instrument range:
| 1b2b8ee9-b775-564c-a713-d589365a839d | button | Installation complete | Yes,N/A
| aba1c2de-c7af-5e9c-a56c-a14b62ff813e | button | Point-to-point | Yes,N/A
| ecc58f4c-0ee5-5ffc-8af4-d6f71dd0f003 | button | Haz. Inspected | Yes,N/A
| 4c069352-53b1-5929-bf0e-32ba06cc7ab4 | button | Tag correct | Yes,N/A
| 046c689d-3c2b-5e23-9237-b6dbae724173 | button | Hook-up correct | Yes,N/A
|  | checkpoint | Alarms & Set points
|  | checkpoint-no-value | Alarm Lo
| c91d5a31-1d3c-580d-a7e2-9b739e77382b | textbox | Activated:
|  | checkpoint-no-value | Alarm Lo-Lo
| 9ab1a471-5ea0-5976-9ff9-b9dbf2ff86ce | textbox | Activated:
|  | checkpoint-no-value | Alarm Hi
| 360046a0-7877-5b6a-ac61-e084561c531a | textbox | Activated:
|  | checkpoint-no-value | Alarm Hi-Hi
| e1175f44-75d7-5d8c-af11-729e382ce6cb | textbox | Activated:
|  | checkpoint-no-value | Set Point 1
| e7fb2071-f263-5ad2-a2f4-47a2d6ccdfe2 | textbox | Activated:
|  | checkpoint-no-value | Set Point 2
| 76a022b2-63e7-58e5-8ddb-85ac9b041e51 | textbox | Activated:
|  | checkpoint-no-value | Set Point 3
| 152ae4fc-6b3c-5092-abda-f20f3e6d5266 | textbox | Activated:
|  | checkpoint-no-value | Set Point 4
| 3d4f86dd-5c3d-5191-8302-42f2fe582b50 | textbox | Activated:
|  | checkpoint | Calibration settings
| f252044c-77cd-5c63-b9aa-481a92fdf9d0 | textbox | Zero
| 2a0dc1de-5ac1-56e4-bd64-e3d722e11edc | textbox | Range
| 5c618edd-bc9b-5e6b-b27d-e6e640369317 | textbox | Other (Specify)
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-10 Cone and Thread Tubing Installation |  | ITR-I-10 Cone and Thread Tubing Installation |  |  | ab69af50-cc61-4db2-b9ac-982b49887a1c
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | General Data
| d1a182fe-bd24-5dbc-a53f-8989e6bd5694 | textbox | Location:
| 77abf1f2-eb12-5875-9068-ad911d39b7eb | textbox | Duty:
| 2d8b87a1-adce-565d-845b-65e9e7361f2a | textbox | Reference Drawings/Hook-up drawing:
| 56772ba8-a6ea-5d0d-b773-b0394493756e | textbox | Related instrument tag no:
| 98bdc5d5-05ae-5feb-9d3f-896ffd9efa31 | textbox | Tube diameter and wall thickness:
|  | checkpoint | Cone and Thread installation - Stainless fittings
| 491696ba-d4b5-5e58-a64c-1d7ce4d1bad6 | button | Correct thread compatibility and engagement | Yes,N/A
| 3cb49051-1778-592b-b0cc-cace8b2cc931 | button | Check fitting collar prior to connection - 1 to 2 threads visible at cone | Yes,N/A
| 0495e1c9-17d9-597d-b314-8c1faf3ad0a1 | button | Tube installation follows the client specification. (Supports, Bracketry, Slope, Expansion, Vibration, Access, Cables) | Yes,N/A
| 6d6720c9-8ef7-5340-839b-0c674f3ef7bd | button | Tube bent correctly, sufficient straight section into fitting | Yes,N/A
| f4b5315c-f57a-5a20-a360-266846693aa9 | button | Tube cut clean and straight, de-burred, reamed, and blown through | Yes,N/A
|  | checkpoint | Cone machined face. No defects, lines, bumps etc.
| dfe835ba-1029-5aa8-985b-4cdf28efc330 | note | Attach photo of cone and thread.
|  | checkpoint | Thread cleanly cut, de-burred and cleaned.
| dfc81ba5-b773-57e6-b4c0-368d9b385980 | note | Attach photo of collar.
| 2cfe42e6-d1e3-5543-9f7d-5deabf966678 | button | Lubricate collar, cone and gland thread at assembly to prevent galling as required | Yes,N/A
| 2d7e7064-60dd-50da-8339-ae17ec306fb9 | button | Correct Tube nut used for the right sized tube | Yes,N/A
| 78af06e2-bac3-5a12-aa5e-302875763ef8 | note | Ensure No thread tape or sealant are used on tube nuts | Yes,N/A
| d9356ba5-8670-55b7-8222-5479e9aca31e | button | Tube fitting hex torqued to ensure correct tightness, marked with pen | Yes,N/A
| 51c978e5-9134-5699-a5f1-f2099394b630 | button | Ensure Weep hole is unobstructed and clean | Yes,N/A
| 2a53e7dc-7aaf-505b-a70d-562ba549512b | button | In service leak test performed and passed | Yes,N/A
| c96dda66-c6a8-5604-9e90-3a5adbbb0435 | button | Fitting completion tag completed and applied to each fitting | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-12 Telecommunications Equipment Panel |  | ITR-I-12 Telecommunications Equipment Panel |  |  | 282cd826-f62f-42be-bd29-35535ddfa07f
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Telecommunications Equipment Panel
| 1c4154cd-0ced-56db-afd7-e46a785a20a1 | button | Ensure equipment panel is securely mounted within the Telecommunications Cabinet in the correct location as shown on general layout drawings: | Yes,N/A
| d1f47028-5bc0-591a-8739-0859f0eb98e3 | button | Check tag number is in accordance with Telecommunications Equipment List. | Yes,N/A
| a90262a8-6b23-553d-b5d5-313ccac387a1 | button | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order. | Yes,N/A
| 2cee0598-bb4f-57fc-915b-5fd898bf56ec | button | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation. | Yes,N/A
| ecb320c8-4f47-54b3-a232-535c0a8929ca | button | Confirm any slide-in cards are firmly fitted to the equipment panel and properly identified. | Yes,N/A
| 9ee8cddf-2746-5bcb-b817-edb4b6de7d75 | button | Check panel air vents are clean and free of dust and dirt. | Yes,N/A
| 6025e44b-05a5-566a-874d-e84bd7453e91 | button | Check equipment panel external earthing connections are securely fitted and properly terminated on the cabinet protective earth bar. | Yes,N/A
| 8d8c72e4-db15-5815-8f44-631183e7accd | button | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar. | Yes,N/A
| 3965c715-368b-5cb6-9c83-e7321182ef1b | button | Ensure any AC power connection(s) is securely fitted and cabled to the appropriate Power Distribution Panel circuit breaker(s). | Yes,N/A
| d333b1ec-2e7a-5d7b-95d5-372777ed2d2f | button | Check sealing of all cable penetration (where applicable). | Yes,N/A
| 150224d8-b182-53df-a3a6-02cde63a7af1 | button | Ensure all signal cables, including any RF co-axial cables, are correctly identified and securely fitted to the equipment panel. | Yes,N/A
| 7656134f-66d4-52ca-b5d6-0abf1e6db346 | button | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable). | Yes,N/A
| ad14b56a-31fa-55c8-9edd-9fb2ab2186c3 | button | Confirm panel is readily accessible for inspection and maintenance. | Yes,N/A
|  | checklist | ITR-I-13 Temperature Instrument Installation |  | ITR-I-13 Temperature Instrument Installation |  |  | ad77c51c-5a40-4434-9fbf-f02c62010f12
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Temperature Instrument Installation
| fd0b9544-6069-5538-b6b4-703ee21e5fdb | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
| 2e83745a-0384-52ee-84d6-ab029cbf0dae | button | Temperature instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
| 03d1767a-0aec-50ed-b743-7fea6a07cb95 | dropdown | Type of thermowell installed | Flanged, Welded, Screwed, Other
| ee26a7ba-0f6a-5c50-b89e-de02ff8cfb8e | button | Thermowell details including flange size are correct in accordance with the specifications | Yes,N/A
| f2548ccd-2aef-5c45-8102-9cb5971c702c | button | Internal depth of thermowell checked and recorded | Yes,N/A
| 3d1e5e85-ef74-5af1-bc24-ce86e4120c34 | textbox | Depth:
| 53d28eab-69d2-5d8e-89ee-b9aa72ce40b9 | button | Bar material and tag number stamped on thermowell flange/exposed surface | Yes,N/A
| f8eb6715-05bd-5111-aedd-7193e8d1ac0a | button | Thermowell CE marked | YES,NO
| 5a49493f-98bc-5a47-94c2-fb034b4ebb12 | button | EOL resistor fitted and correctly rated where applicable | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-14 Flow Meter Installation |  | ITR-I-14 Flow Meter Installation |  |  | f5302184-516f-4723-a067-b81f152c18c2
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Flow Meter Installation
| f87e869d-c142-52cb-b7c0-3aae2a77c924 | button | Check instrument nameplate details are correct in accordance with the instrument index | Yes,N/A
| 1e434277-77d7-5393-9152-8bef58b8c3a1 | button | Flow meter calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
| 33935e3b-559c-5d24-b5e0-41bfcf541590 | button | Ensure location and tapping point is verified as per P&ID & location drawings | Yes,N/A
| afc06ac0-3a02-5f4e-bcc9-b10ffe87b8c1 | button | Ensure direction of flow is correct with respect to flow meter | Yes,N/A
| 185c702d-bfe6-54b0-b355-19b4a132e624 | button | Check mechanical clearance is adequate for installation of flow meter | Yes,N/A
| 0790c58e-f128-5b9f-b542-2f634616ee61 | button | Verify type and size of gasket is correct between process line and measuring unit flange | Yes,N/A
| cf1f916f-e92b-51e4-9b30-922d8cd6b113 | button | Ensure correct nut and bolt grade and material for connecting unit to process line | Yes,N/A
| 1a6bb310-9458-5042-b73f-47e9249b6d9e | button | Verify display/cover is oriented for ease of use for operators and access for technicians | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-15 Pressure Instrument Installation |  | ITR-I-15 Pressure Instrument Installation |  |  | 2175c743-90f1-4cd2-ad69-c230d09767be
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Pressure Instrument Installation
| 2631ab2a-0c77-5902-9f1f-ed22d93525fe | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
| 27098a9c-b9ac-5eb7-93fc-25e94c960982 | button | Pressure Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
| 79cb8320-6b5e-5cee-9eab-b27f09df8e25 | button | Instrument mounted as per hook-up drawings | Yes,N/A
| 48e55a55-0561-52a3-a7b3-f8ab1adbd073 | button | Air line/Impulse line are correct material to site specifications | Yes,N/A
| f1af2a64-0042-508b-b437-4d6d351a317f | button | Air line/Impulse line are routed tidily and as per hook-up drawings | Yes,N/A
| 4433f642-c751-585f-a2e3-6f220d279b03 | button | Correct bolt size and material/grade used | Yes,N/A
| e12ec30b-28ca-5fe0-a5e8-624de01d3ec6 | button | Local indicator is mounted and easy to read, easy access for technicians | Yes,N/A
| e203fc70-4033-5fa1-bc7e-0bda849aeaaa | button | Instrument and tubing are adequately supported as per drawings | Yes,N/A
| 916084dc-7799-58b3-aa41-eafe85e7d6ab | button | Isolation valve installed | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-16 Level Instrument Installation |  | ITR-I-16 Level Instrument Installation |  |  | fcc62f01-fd33-45e3-9992-718a0becfb67
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Level Instrument Installation
| e0c62c71-6e86-579c-a3c2-fb6d3eb9bb86 | button | Check Instrument Nameplate details are correct in accordance with the instrument index. | Yes,N/A
| b5472fcf-9d95-5ac7-9654-04a34eb8144e | button | Level Instrument calibrated before installation (ITR-CL-1-123 Instrument Calibration) | Yes,N/A
| b2964d43-e974-5267-8507-813d0824255b | button | Level instrument mounting equipment is adequately sturdy and correct materials used | Yes,N/A
| 0157f28e-3d95-5b4e-9284-9fe043d14dba | button | Bolts and studs are to site specification | Yes,N/A
| eed8f769-8084-5a79-8350-040b8d4ba5c2 | button | Ensure location and tapping point is verified per relevant drawings | Yes,N/A
| 241f3712-9ec0-54cc-8700-05a8eb19d664 | button | Ensure gasket and studs are used as per specifications | Yes,N/A
| 4be859d7-a63c-553a-a867-a30c40124d0d | button | Verify contact type sensor probes are installed without any resistance | Yes,N/A
| eb013389-4807-5a66-bfad-a652fd4e7b18 | button | Verify antenna/source are installed correctly | Yes,N/A
| 592b7207-03a5-50f4-b989-964519ce2f3b | button | Ensure display is easily readable by operations and access is easy for technicians | Yes,N/A
|  | signoff | All relevant signatures (Installed by, Approved by, Client Representative)
|  | checklist | ITR-I-21A - Instrument and COntrol Cables |  | ITR-I-21A - Instrument and COntrol Cables |  |  | 780c431e-648b-497b-b61f-ac740dd7c306
|  | checkpoint | Instrument and Control Cable
| 1d1be4a5-0430-5e99-850d-bcf42c1194c1 | button | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule. | Yes,N/A
| 8814a8f2-dab1-55d6-802e-14048a5cb82b | button | Check dressing / cleating, cable undamaged | Yes,N/A
| 88b4f85a-95d0-5b03-891c-a69079c9b8f0 | button | Cable mechanically protected | Yes,N/A
| 753520ad-bb9c-56a0-899a-34075f1019e4 | button | Cable terminated with correct lugs and crimped with the correct die. | Yes,N/A
| 2af625ee-50d3-550d-ab76-51bd6b56c9e1 | button | Screen correctly made off | Yes,N/A
| 5975fd09-5180-5bf0-a297-5fd8faa6668f | button | Glanding / Locknuts correctly installed. | Yes,N/A
| 85c8dabc-ed2a-59dc-8a7a-eee3e1d8c91e | textbox | Gland type - from: |  |  | Haz. Area Rating
| 31151933-a8f1-5e23-bc43-846a486e94c0 | textbox | Haz. Area Cert Details.
| 092bb3f3-190b-51e4-b3df-c6e0e5a41c6d | textbox | Gland type - to: |  |  | Haz. Area Rating
| e8616af8-b07d-5012-a51f-9d245c0ff169 | textbox | Haz. Area Cert Details.
| 19c166e0-2aa1-5578-9188-5aaef45cb686 | textbox | Confirm spare cores and shields are terminated and conform to drawings and client spec.
|  | checkpoint | Electrical Checks
| e5e3b755-2bc7-5682-accd-cf46de13030b | textbox | Record test results: Insulation Resistance, Continuity, Bonding, Other.
| 318d0cf5-d82e-51f7-ab9a-e86ae071d12f | textbox | Installed by:
|  | signoff | Client Representative:
|  | checklist | ITR-I-34A Instrument Installation PRV/PSV |  | ITR-I-34A Instrument Installation PRV/PSV |  |  | f124d4e7-3b4d-45c4-9526-8064d9b5193f
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint-no-value | Details
| 97a7e567-1414-5988-b564-f31e67504f15 | textbox | Make and Model:
| eaeabc79-4616-5adc-b156-6dfd748b6752 | textbox | Manufacturer:
| 568fc6f7-31e3-5b38-88bb-acf56ada0d02 | textbox | Type:
| 69f3ad75-17c9-5267-a781-dda72de8247c | textbox | Check equipment and nameplate details are correct in accordance with the instrument index
| 2e86613a-3062-5581-8af4-aca22cad7869 | button | Valve is installed correctly | Yes,N/A
| a37ed865-5928-5b49-8867-ff868f593690 | button | Valve is installed level and per P&ID | Yes,N/A
| c9ceefcb-f9e3-5e6b-9fdb-bcd992e15253 | button | All gaskets are correct specification and fitted | Yes,N/A
| f931fb78-6294-51f9-89d9-4ec95744b486 | button | All bolting is tight and to specification | Yes,N/A
| 92be7181-8c37-53be-926b-30114b5283b0 | textbox | Tagged by SGS/IVE, upload certification | Yes,N/A
| 6538c551-dc50-5cb2-b4ff-47039d4ba3fa | button | Correctly labelled as per drawings | Yes,N/A
|  | checklist | JHA - Job Hazard Analysis |  | JHA - Job Hazard Analysis |  |  | dfe7467e-6231-4264-a20d-1e13ece2605a
|  | section | Job details
|  | checkpoint-no-value | Job details
| 5e2b5a0a-ebea-5ef2-ba31-c6d8f1749ace | date | Date:
| d2eec14f-d345-5d26-b1ad-b715aa042c2f | textbox | Permit No.
| 6bbb017f-3de2-532f-ac5c-4018443cf25a | textbox | Job No.
| 6f8dd611-351e-5e98-9a2e-a317cccc405e | textbox | Site
| 73dbb284-80e6-5fd2-b031-36c02c27a304 | textbox | Activity Location
| f4a169d2-f7e1-554e-8166-d6fb66645ceb | textbox | Asset:
| 28a26cac-3139-5b60-a408-2b573120734d | textbox | Work Details:
|  | section | Prompts for Hazards - Mark all that apply.
|  | checkpoint-no-value | Prompts for Hazards - Mark all that apply.
| a65afbbd-ab46-5866-82e8-e5a2494f71e5 | tickbox | Sparks/Open flame
| 9c9e0951-136b-5579-8bfc-9ea8cb54a919 | tickbox | Disabled safety device(s)
| 5be00646-30d4-53b0-878f-03968bd89a5b | tickbox | Uneven surfaces
| 907e05b1-f3f8-5f0b-95de-d18e509be716 | tickbox | Fatigue, over-exertion
| 023842ab-a35a-55df-b61f-39f13987d7e6 | tickbox | Crane movements
| c3b59cd6-2e40-53b7-bfcc-a2599492575c | tickbox | Moving/Rotating parts
| e4811296-8b28-5c6b-b776-c35eb13bacfb | tickbox | Remote area, working alone
| e351d74e-2eef-5e18-bab8-402df388a475 | tickbox | Conflicting work/SIMOPS
| df7830ab-1021-56d1-b67d-0b2b84ddc266 | tickbox | Electrical arc flash
| a4fd4d14-b04f-5204-b16a-1afa55f33175 | tickbox | Sharp objects/materials
| ee70ca90-be26-58b7-8fe8-2e3a889f5fcd | tickbox | Restricted/Difficult Entry/Exit
| f6a8755a-13b1-5509-90c7-dd5a88fbb050 | tickbox | Overhead obstacles
| 6f36c55f-3df1-5b5f-8699-2a479fdcb98e | tickbox | Ignition sources (other)
| f96dd8c9-c3e8-500f-84f1-a8132cf4fa3e | tickbox | Access/Egress
| 1f484f0c-6ab9-57e1-9faa-eab8a4b86e79 | tickbox | Water body
| a796eddc-837c-581d-afa7-ccdf62c07d28 | tickbox | Live equipment
| dab35eba-3ac2-5006-bcda-d94035517276 | tickbox | Slippery surfaces
| a869361a-0abc-56df-ba6f-5a1f185ea61f | tickbox | Suspended loads
| 46281714-3f95-59f3-a75a-c7551f1707f8 | tickbox | Hazardous substances (chemicals)
| 0c71c6fa-c4aa-50fc-aad1-bb2ada686bae | tickbox | Use of non-intrinsically safe equipment
| bc1bcdcd-3196-57a9-b9f5-7b38012dda2a | tickbox | Weather extremes
| 6461377f-075a-5d0b-9be8-b482575dddef | tickbox | Moving vehicles
| 6c16d53c-3d8b-590c-a947-28707aff31a5 | tickbox | Task related noise
| 88425c20-6af8-5363-9f85-3e38f92ecaf6 | tickbox | Engulfment
| a2a1606f-7a2e-5584-ae35-a7d08552fcc7 | tickbox | General waste
| 94a1751c-c36d-5d4b-b960-80863a8730b8 | tickbox | Hazardous waste
| f3d9a879-6bea-5f34-a027-88e451874576 | tickbox | Hazardous/toxic substance, fumes, gas
| 2ed5ec41-c764-5322-894f-43cef3cadd52 | tickbox | Flammable materials - Gas, liquids, solids
| 0399710b-01b4-50e1-b917-59653585cfe3 | tickbox | Reduced visibility, lighting
| 8743eadf-87b6-5c4f-bec4-498e26e352bf | tickbox | Electricity
| 036da75a-d197-50f6-99a0-baa71f1d23a4 | tickbox | Static electricity
| 85b80620-fac6-5f77-980e-cdd689375cef | tickbox | Work at height
| ed077c10-2e2c-5996-ba17-cb716098c04b | tickbox | Underground services
| 4a3902cf-f186-5c75-a2d2-9f8b584cec35 | tickbox | O2 Deficiency/Excess
| d9946030-f9d0-5c9d-a3ea-b22813eea23a | tickbox | Temperature extremes
| 1c08a25b-fbd5-546b-902f-49f301b52f40 | tickbox | Heavy objects
| d4812bfc-4c9b-5544-ad25-56f567d2cdcd | tickbox | Radiation
| 2c8eadf5-6b45-541b-b952-d03c8d361f47 | tickbox | Potential energy - Tension/Compression
| 69c0479c-33e8-52ba-bc46-e2976bd374db | tickbox | Flying particles/Dust/Objects
| a71e667c-cbf4-54c8-9b8c-bc59d9e9bb3b | tickbox | Vehicle entry
| e791611b-16e7-5673-ab22-1d161508555d | tickbox | Exposure to process temperatures.
|  | section | Prompts for Initial Consequences - Mark all that apply
|  | checkpoint-no-value | Prompts for Initial Consequences - Mark all that apply
| bf873c34-9d4b-55f5-b052-24d60e90c17c | tickbox | Falling/Dropped objects
| d6c164a8-9282-532e-a45d-8843f33c646a | tickbox | Fall from height
| 31df14ab-0270-5b3a-a755-21618e606569 | tickbox | Trip/Slip/Fall
| d967af28-2ab3-55af-9099-6c178343cd42 | tickbox | Gas release
| 7c2a47b2-cdcb-5862-834e-d7eb794e7d54 | tickbox | Pressure release
| 5fb833df-a274-5f34-8160-7e437a3d5df8 | tickbox | Struck by object
| dd84d0c6-2be5-5ada-acfa-718b005cddc9 | tickbox | Exceeding tool limits
| c1e19ea0-e628-5782-984e-db82c7d1d744 | tickbox | Overloading people
| dee0d01f-0958-56d9-82d2-d06f1c47c7c4 | tickbox | Unplanned shutdown
| f6bc105b-442d-5820-b2aa-89b497ecadd0 | tickbox | Exposure to O2 deficiency/excess
| 3b77d9e5-5466-57ae-b82b-34d87af503e9 | tickbox | Exposure to hazardous substance
| d4d53505-3b55-5059-a075-914faa521c2e | tickbox | Entanglement
| 7d03fa48-0bb6-5433-affd-47ab741afd1d | tickbox | Flying objects
| 8889b7c7-28a4-50ea-990e-6c02237482e3 | tickbox | Loss of control
| d3b2a090-3334-5e2a-8a8d-a65091b8aacb | tickbox | Loss of containment
| bf47bbb4-2f5e-524a-a760-5e02a748724d | tickbox | Excess exposure to Emissions, dust, fumes, noise, fibres, heat
| e970ea5f-aa7f-5e22-baf3-43e8d7c125b7 | tickbox | Loss of structural integrity
| 60e1ac41-88c5-58f9-951e-adf44996c386 | tickbox | Equipment failure
| e36f210d-a526-5cab-9a79-0e586c9ac384 | tickbox | Uncontrolled ignition source
| 59b9a52f-660f-5dd4-b21c-7bce36412a12 | tickbox | Collision
| 56eace1d-eb60-5eb2-a662-2acbe44a48e6 | tickbox | Ignition/Fire
| e3b09fe0-48d0-5dc5-b9ec-e149a57a8227 | tickbox | Back strain/Injury
| 26ec0a23-00c6-5612-aa10-087cc79be1a7 | tickbox | Burns
| 2968c9e9-4ceb-521d-bd52-fea56fe848e2 | tickbox | Heat exhaustion
|  | section | Initial controls - Mark all that apply.
|  | checkpoint-no-value | Initial controls - Mark all that apply.
| 42cad66d-2f48-59fc-bdbc-a4899116b647 | note | People controls
| 2af4f081-c6a3-5ea7-8aa4-4c61e185c040 | tickbox | Safety/Fire watch person
| 0e0958ec-f586-5b40-91f4-2468376aeeb4 | tickbox | Barriers/Flagging
| 52e20385-4d53-5a5a-b5a2-63e9c76dbaec | tickbox | Warning signs
| 12d9b3a0-60b2-5d0c-88be-8e42d77e01b0 | note | Equipment controls
| 57311318-c4c1-5fad-a3c4-618731ab91bd | tickbox | Master tags and locks
| 83984315-0669-5317-90a0-59195580414b | tickbox | Scaffolding for access
| 0013af5a-f28f-5632-b7f8-41071b7e5eef | tickbox | Radio communication
| a71d663c-c81f-5b1b-8796-178e1412ea95 | note | Environmental controls
| c40dc098-b1f5-5043-be03-58c3c79f7672 | tickbox | Ventilation
| 48d60432-5643-562b-960d-7a98f8ee58bc | tickbox | Lighting
| 0518a857-3aae-51b9-b156-7015794d54c0 | tickbox | Gas Testing
| db4d6042-a72d-5317-a087-64a516a3ad8c | note | High risk controls
| 507a5b20-d86d-5851-9237-03437b51f1cf | tickbox | WSCS Work permit
| 82175306-5c2b-5b38-bf16-d8bcb857eceb | tickbox | WSCS Certificates
| 4f0f64f8-299c-54ca-8f65-700aac52ea92 | tickbox | Critical lift/Fall protection plan
| ba549199-0d05-5db3-9af4-a5bdfbee21fc | tickbox | Specialised PPE
| 276bc1a7-9086-50f8-aea6-0ed0e137191e | tickbox | Spill kit
| c8183da4-d4a0-530c-815c-198963cf8887 | tickbox | Fire extinguisher
|  | section | Signatures
|  | checkpoint-no-value | Signatures
|  | signoff | Applicant signature
|  | checklist | JHA - Job Step |  | JHA - Job Step |  |  | 99dfeae2-4934-4149-b121-d98403ee5a54
|  | section | Task Step - add task step for each individual task
|  | checkpoint-no-value | Task Step - add task step for each individual task
| de760b45-077c-5d33-a865-8203209941ab | date | Date:
| 5af8a12c-a856-5e8e-9a50-c3b114ef67d2 | textbox | Task step number (eg. Step 1, Step 2 etc):
| 9045a3aa-2ee3-5fac-86ae-a2e71654832c | textbox | Task details:
| bd9e4658-5f4e-52ca-a6c6-95235c4d9e07 | textbox | Hazards:
| 855ddb38-a1ad-58c4-8e99-41a0ba8435cc | dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
| a33cde4b-c8b9-5a55-b726-6589c2cd8911 | textbox | Potential consequence:
| 26f059e4-8ffa-53d6-9a83-3a06b83b6d21 | textbox | Controls:
| 87186b45-3e49-5075-a99d-624da0af48c5 | textbox | Recovery steps:
| 85282d46-5c1d-5f17-ba02-b45ca1b9e5ba | dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
|  | checklist | Record of Inspection (ROI) |  | Record of Inspection (ROI) |  |  | aebb5d4a-ebe7-4a8c-81a5-cedbd37f0f8f
|  | checkpoint | Please upload Record of Inspection here when complete (ROI)
|  | checklist | Sign Off |  | Sign Off |  |  | 42e817df-c63e-4b5d-b191-351cd47aa287
| 45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
|  | checkpoint | Add applicable signatures (e.g Electrician, Inspector, Client Representative)
|  | checklist | Test Equipment Details: |  | Test Equipment Details: |  |  | 8aee3121-953c-4376-8892-71ad106dd65d
|  | checkpoint-no-value | Details
| 6969f4e1-1250-5dce-94ca-225736132147 | textbox | Make
| 3dbf8f5c-fd86-5444-8bc9-b09c2afcea54 | textbox | Model
| e5406774-9890-58bb-83f0-6e149f1b2268 | textbox | Serial No
| 5c9ec93f-ae4a-541f-b021-f391f3c276fe | textbox | Calibration Expiry Date
|  | checklist | Toolbox Meeting |  | Toolbox Meeting |  |  | 4f0ec359-7e5a-4c71-816e-2567bbbd5875
|  | section | Toolbox meeting
|  | checkpoint-no-value | Toolbox meeting
| 5b46f868-e99f-53e7-8c14-aafd0ed4af0f | date | Date:
| 819ee9f5-86bf-575a-993a-b488f62017be | textbox | Meeting location:
| 86750fbf-4fc7-5317-99d8-b9e113c89592 | textbox | Meeting conducted by:
| 15296ca9-2f49-5891-9114-5f3ed53474e0 | textbox | Meeting attendees:
| fa1562a2-2acd-5d5a-959d-08f878654593 | textbox | Today's work scope/Hazards
| 46fd19b8-a84c-52e7-a905-a01a343624f7 | textbox | Hazard controls:
|  | signoff | PICWS Signoff