## Checklist Templates
Id | Type | Name | Values | Prompting Name | Resource Id
| checklist | FEL SM Weekly Site Checklist |  | FEL SM Weekly Site Checklist | 4406dc62-fb9b-4004-bdee-2789c1defa6e
| section | Monday
| checkpoint | Prestart Meeting with Team
| checkpoint | Health Check
| checkpoint | Review Tasks for the week
| checkpoint | Identify Targets Including Hours
| checkpoint | Approve hours by 9AM for previous week
| checkpoint | Sign off Subcontractor Hours & Submit
| checkpoint | Review SWMS
| checkpoint | Site Toolbox Meeting
| checkpoint | SSSP in Order
| section | Tuesday
| checkpoint | Follow up outstanding RFI's with PM
| section | Wednesday
| checkpoint | Review Roadblocks & Follow Up if still unresolved
| checkpoint | QAs up to date
| section | Thursday
| checkpoint | Weekly planner filled out for week ahead
| checkpoint | Roadblocks identified and actioned
| checkpoint | Materials organized for week ahead
| checkpoint | Plans printed with any relevant notes added
| section | Friday
| checkpoint | Submit Toolbox minutes to main contractor and FEL office
| checkpoint | Job Cards up to date and submitted
| checkpoint | Team tasks for week ahead filled out on whiteboard
| checklist | QA - Cable Tray |  | Cable Tray | 1d45ffb3-4fd7-4898-9c8b-ccb367fbe014
| checkpoint | Unistrutt Filed & Painted
| checkpoint | Hangers Spaced as Specified
| checkpoint | Correct Size Tray Installed
| checkpoint | Tray Joined Correctly
| checkpoint | Hangers Seismically Restrained as per Design
| checkpoint | Tray Fastened to Hangers
| checkpoint | Correct Anchors used fixing to Ceiling
| checkpoint | Cable Tray Bonded
| checkpoint | Photos
| checklist | QA - Catenary Wires |  | Catenary Wires | f54c3a97-afec-4c84-bd99-61cd1ed313bf
| checkpoint | 300mm Separation Between Power & Data
| checkpoint | Supported every 6 Meters or Adequately to avoid Sagging
| checkpoint | Correctly Secured at Each End
| checkpoint | Turn Buckle Installed and Accessible
| checkpoint | Photos
| checklist | QA - Completion |  | QA - Completion | 2c5c0560-1a87-4a6b-a844-bb98f8973d6f
| checkpoint | All Areas Defected by SM & Feisst Team prior to PC
| checkpoint | All DBs Tested, results uploaded to Drive on iPad and sent to Project Admin
| checkpoint | PS3 Completed & Signed for Emergency Lighting
| checkpoint | PS3 Completed & Signed for Seismic Bracing of Electrical Fixtures
| checkpoint | All COCs completed and Submitted to Julia
| checkpoint | "Clean" As Built Set of Drawings Completed and Submitted to Julia
| checkpoint | All excess material removed from site and returned to wholesalers
| checkpoint | All assets accounted for and removed from site
| checklist | QA - First Fix |  | QA - First Fix | 035bfade-da99-4f21-b17f-228d2c126893
| section | Flush Boxes
| checkpoint | Fire Rated or Acoustic
| checkpoint | Height as per plan
| checkpoint | Location as per plan
| checkpoint | Intumescent Pad In Place
| checkpoint | Flush Boxes Not back to back on Acoustic Walls
| section | Cabling
| checkpoint-no-value | Details
eb4f8ba9-a4a5-5b28-8713-d53348fd297e | textbox | Type
7b274a21-45c3-5097-9f9a-9ff8d64358f5 | textbox | Size
| checkpoint | Circuits clearly labelled
| checkpoint | No Horizontal cabling
| checkpoint | Separation between Data and Power at 300mm or as specified
| checkpoint | Light Control cabling Required
| section | Cat Wires
| checkpoint | 300mm Separation Between Power & Data
| checkpoint | Supported every 6 Meters or Adequately to avoid Sagging
| checkpoint | Correctly Secured at Each End
| checkpoint | Turn Buckle Installed and Accessible
| checkpoint | Number of cables per cat wire. 8 maximum or as per electrical spec
| checkpoint | Separation between services maintained
| checkpoint | All cables secured via cable ties with ends cut
| section | Cable Tray
| checkpoint | Minimum 25% spare capacity left on cable tray
| section | Lights
| checkpoint | Setout Correct
| checkpoint | Cabling in correct location
| checkpoint | Control Cabling installed
| checkpoint | PIR Sensors
| checkpoint | Occupancy Sensors
| checkpoint | Light Level Sensors
| checkpoint | Emergency/ Exit Lighting
| checkpoint | Nogging installed for Electrical Services
| section | Seismic Bracing
| checkpoint | For Lighting
| checkpoint | Cable Tray
| checkpoint | Switchboard
| section | Ducts and Conduits
| checkpoint | Correct size installed
| checkpoint | Location as per plan
| checkpoint | separation from other services
| checkpoint | Clean inside and in good condition
| checkpoint | Photos
| checklist | QA - Inground Services |  | Inground Services | e814a4c3-ab7f-4df1-992b-3348571f6526
| section | Ducts and Conduits
| checkpoint | Correct size installed
| checkpoint | Start and finish locations correct as per plan
| checkpoint | separation from other services
| checkpoint | Clean inside and in good condition
| section | Electrical Pits
| checkpoint | Set out correct
| checkpoint | Correct size installed
| checkpoint | Duct entry holes sealed / water proofed
| checkpoint | Pits installed to correct height and level
| checkpoint | Clean inside and in good condition
| section | Light Pole Foundations
| checkpoint | Set out correct
| checkpoint | Ducting in correct position - centre of cage
| checkpoint | Correct Cage Installed
| checkpoint | Cage installed to correct height / level
| checkpoint | Ground Plant pole installed to correct height / level
| section | Photos
| checkpoint-no-value | Photos
| checklist | QA - Second fix |  | QA - Second fix | 3563bea0-c420-4985-90e3-9a64cb75d1bc
| section | Power Outlets
| checkpoint | Weekly Toolbox
| checkpoint | Correctly installed with terminations all secured properly
| checkpoint | Outlet Installed level
| checkpoint | Intumescent Pad In Place
| checkpoint | Circuit Tested and results recorded
| checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
| section | Light Switches
| checkpoint | Correct type installed
| checkpoint | Correctly installed with terminations all secured properly
| checkpoint | Outlet Installed level
| checkpoint | Intumescent Pad In Place
| checkpoint | Circuit Tested and results recorded
| checkpoint | Description Labelled on the outlet face with vivid and with dymo labeller on cover plate and ensure label is level
| section | Light Fixtures
| checkpoint | Correct type installed
| checkpoint | Correctly installed with terminations all secured properly
| checkpoint | Seismic braces installed.
| checkpoint | Insulation removed from over downlights and drivers
| checkpoint | Tested for operation
| checkpoint | Photos
| checklist | Switchboard |  | Switchboard | b0c4f05f-eedc-4334-8e74-80cd1e8763aa
| checkpoint | Spatial certificate signed if required
| checkpoint | Fixings installed in wall correctly if board is wall mounted
| checkpoint | All clearances sighted to ensure location is compliant
| checkpoint | All cables correctly installed in protection device and earth and neutral bars and fully secured
| checkpoint | Cables neatly dressed
| checkpoint | Phase tabs on chassy covered
| checkpoint | All earths and neutrals labelled to match phase numbers
| checkpoint | Switchboard is clean on the inside and outside
| checkpoint | Masking blanks installed
| checkpoint | DB legend installed
| checkpoint | Feisst label on the door installed
| checkpoint | Photos