## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Seacliff Wastewater Treatment and Disposal Upgrade |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561469 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9776 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 6 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Storage Tanks |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | Seacliff Watewater Treatment Plant Upgrade |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | 310103025-01-001-C101 to C112 and C120 to C125 |  |  |  |  | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Sebastian Charlin |  | Date: | 2023-11-03 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
3.1 | Review all Drawings and Documents | Review all drawings and documentation provided to the Contractor. | Prior to the commencement of Works it must be ensure that all necessary documentation has been provided. | ITP | Prior to the commencement of Works | Visual | R | PM/QE
3.2 | Setting Out Levels and Alignment | All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4 | Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer | Compliance surveys or spot checks | Prior to the commencement of Works | Visual, Instrumental | H | SP/QE/SV
3.3 | Valves Delivery | Gate valves shall comply with AS/NZS 2638. Valves greater than DN50 shall be resilient seated sluice valves. DN50 shall be gate valves. Sluice valves shall be anti-clockwise closing. DN50 gate valves shall be clockwise closing. Valves shall be provided with a surface box according to the asset owner’s engineering standards. Specs 1131: 14.3.1 | The charasteritics of the valves delivered to site match the corresponding specifications, drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.4 | Joints and Fittings | All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2 | The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.5 | Pipe Bedding and Haunching Agregate | Pipe bedding should be AP20 and in accordance with AS/NZS 2566.2 or AS/NZA 3725. Maximum Dry Density (MDD) and Optimum Water Content (OWC) of the aggregate must be provided. Specs 1131: 14.9.1 | Visual Inspection, Engineer approval | Delivery Docket, Laboratory test results | Prior to the commencement of Works | Visual, Lab Test | H | QE/SP/MC
3.6 | Backfill Aggregate | Backfill aggregate should be GAP 65. Samples of backfill material should be tested in accordence of NZS 4402 to determine the MDD at OMC. The solid density of aggregate should be tested in accordance with NZS 4407. Specs 1131: 16.1.1 | Visual Inspection, Engineer approval | Delivery Docket, Laboratory test results | Prior to the commencement of Works | Visual, Lab Test | H | QE/SP/MC
3.7 | Concrete Manhole, Catchpits and Access Chambers | Precast concrete estructures shall comply with NZS 3106. Specs 1131: 14.5 | Manhole charasteritics Match NZS 3106 | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.8 | Material Storage | Storage for materiales must be arranged as it is described in: Specs 1131: 14.10 | Pipe stored according to specifications | Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.9 | Defective Materials | Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12 | Defective material detected and removed from site | Delivery docket, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
4.1 | Hazardous Waste and Contaminated soils | Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3 | Dumping site approval for contamiantion type | Dumping Docket | If constaminated soils are found | Document Check | C | QE/SP/CR
4.2 | Trench Excavation | Trenches for flexible pipes shall be excavated within tollerances in table from Specs 1131: 15.2.5 unless otherwise stated. | Trench width and pipe clearance to walls comply with requirements | Installation Check Sheet | During trench excavation | Visual, Measurement Check | C | QE/SP
4.3 | Pipe Bedding and Haunching | Bedding and Haunching for flexible pipes should be in accordance with AS/NZS 2556.2 and have minimum embedment zone as shown in table from Specs 1131: 15.2.8.2 | Bedding and haunching high and with comply width requirements | Installation Check Sheet | During bedding and haunching installation | Visual, Measurement Check | C | QE/SP
4.4 | Pipe Line and Level | Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12 | Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer | Grade Check sheet | During pipe installation | Visual, Instrumental | C | SP/QE/SV
4.5 | Precast Concrete Pipe Installation | Joints between precast pipe units shall be self-centering and shall be sealed with butyl mastic or similar approved to form a watertight joint. Concrete pipes shall be installed in accordance with AS/NZS 3725. Specs 1131: 15.3.6 | Precast concrete pipes Joints and Intallation comply with standard and specifications | Methodology. QA records | Per joint, and during pipe installation | Visual | C | QE/SP
4.6 | Aggregate Compaction | Compaction shall be as stated in Specs 1131: 15.4.4. For concrete pipes the verification testing of compaction shall use a method recommended in table 3 of the CPAA Technical Note on Installing Concrete Pipe and approved by the Engineer. Specs 1131: 15.3.6 | Compaction Value ≥ Specification Value | Depending of Pipe material or Aggregate: CBR Checksheet, Nuclear Density Meter (NDM) Results Sheet, Clegg Hamer test records | each layer | On site Test | H | QE/CR
4.7 | Backfill Compaction | Selected fill within 0.8m depth from finished surface shall be AP 65. Subgrade and subbase shall be compacted in layers no greater than 200 mm thick unless otherwise agreed with the Engineer. Under carriageway basecourse shall be compacted in layers no greater than 150mm thick unless otherwise aggred with the engineer. Specs 1131: 15.4.3.2, 15.4.3.3 | Dry Density ≥ 90% MDD | Nuclear Density Meter (NDM) Results Sheet or Clegg Hamer test records | each layer | On site Test | H | QE/CR
4.8 | Topsoiling and grassing | Topsoil shall be used to dress areas disturbed by the contrat works to a minimum thickness of 100mm. Grass seed shall be sown evenly over the prepared topsoil area. Specs 1131: 15.8.6 | Topsoil installed and grass seed spread in the specified rate and mixture. | QA records, Photos | After compaction of final layer of backfill | Visual | C | QE/SP
4.9 | PE pipes Welding | In accordance with manufactures specifications. Where unspecified butt welding in accordance with PIPA POP003 and electrofusion welding in accordance with PIPA POP001. All welds shall be marked with weld number and welder identification. Specs 1131: 15.3.2.1. | PE Welding ejectuded as specified | QA records, Weld records | Per weld | Visual | C | QE/SP/WS
4.10 | Welded Joints Inspections | Each butt-welded joint will be visually inspected by the engineer and Each electrofusion joint shall be visually inspected by the contractor according to Specs 1131: 16.3.2.1 | Welded Joints complies with visual inspection specified | QA records, Weld records, Photo | After welding each joint | Visual, Measurement Check | C | QE/SP/WS
4.11 | Pipes Connected to Structures | Where a pipe is built into an underground structure, the requirements stipulated in Specs 1131: 15.3.10 must be followed | Pipe is connected to the structures according to the specifications | Methodology, QA records, Photos | During installation | Visual, Measurement Check | C | QE/SP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
5.1 | As-built Drawings | Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2 | Engineer Approval | QA records | At completion | - | H | QE/CR
5.2 | Manholes | Manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. Testing shall be in the presence of the engineer. Specs 1131: 16.2.2.5 | A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. Engineer Approval | Test Records | For every manhole installed (24hr prior notice to the engineer before test) | Test | H | QE/CR
5.3 | CCTV Inspection | All pipelines shall pass a CCTV inspection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3 | A pipeline will fail its inspection if: - The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter. - The pipe has visible dips or ponding of water. - The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects. - There is evidence of infiltration at joints or laterals. | CCTV footage and log sheets | At every section of pipe installed. | Visual | H | QE/CR
5.4 | Surplus Materials and Refuse Disposal | All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2 | - | - | At completion | Visual | C | QE/SP/CR
5.5 | Cleaning | Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3 | - | - | At completion | Visual | C | QE/SP/CR
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: