## General
Modify template as required prior to use, e.g. to accommodate project or customer specific requirements, then delete this instructional text when complete.
SECTION 1 – GENERAL DETAILS
Project Name: | Seacliff Wastewater Treatment and Disposal Upgrade |  |  |  |  | Inspection Key Use in sections 3, 4 and 5. |  | Responsibilities Use in sections 3, 4 and 5.
Project Number: | 561469 |  |  |  |  | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Dunedin City Council |  |  |  |  | B | Report by Breach | CM | Construction Manager
Contract Number: | 9776 |  |  |  |  | C | Check | CR | Cust. Representative
Area/ Sub-System: |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[6 empty] | E | Examine | MC | Material Controller
ITP Number: | 7 |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager
ITP Description: | Sand Filters |  |  |  |  | I | Inspection | PM | Project Manager
Discipline: | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor
Specification: | Seacliff Watewater Treatment Plant Upgrade |  |  |  |  | O | Operation | QE | Quality Engineer
[6 empty] | R | Review | QM | QA Manager
Drawings: | 310103025-01-001-C101 to C112, C200 to C221 and C260 to C261 |  |  |  |  | S | Subcontractor | SP | Supervisor
[6 empty] | V | Visual Verification | ST | Superintendent
Prepared By: (Name) | Sebastian Charlin |  | Date: | 2023-11-06 |  | W | Witness Point | SV | Surveyor
Quality Specified: | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
3.1 | Review all Drawings and Documents | Review all drawings and documentation provided to the Contractor. | Prior to the commencement of Works it must be ensure that all necessary documentation has been provided. | ITP | Prior to the commencement of Works | Visual | R | PM/QE
3.2 | Setting Out Levels and Alignment | All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4 | Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer | Compliance surveys or spot checks | Prior to the commencement of Works | Visual, Instrumental | H | SP/QE/SV
3.3 | Pipes Delivery | Pipes and pipe fittings shall be of the material, pipe class and joint type nominated on the Drawings. Specs 1131: 14.1 and Drawings C260 - C261 | The charasteritics of the pipes delivered to site match the corresponding drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.4 | Joints and Fittings | All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2 | The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/CR
3.5 | Drainage Aggregate | Drainage aggregate shall be 19 mm uniformly graded, clean, durable aggregate having a crushing resistance of not less than 100 kN when tested in accordance with NZS 4407. Material used for backfilling the trench above any geotextile wrapping shall be free draining granular material. Specs 1131: 14.9.2 | Visual Inspection | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.6 | Material Storage | Storage for materiales must be arranged as it is described in: Specs 1131: 14.10 | Pipe stored according to specifications | Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.7 | Defective Materials | Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12 | Defective material detected and removed from site | Delivery docket, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.8 | PVC Pipes | PVC-U gravity pipes for sewer, drainage, ducting or venting shall comply with AS/NZS 1260. Shall have spigot and socket joints with rubber rings. Specs 1131: 14.2.1 and Drawings C260 - C261 | The charasteritics of the PVC pipes delivered to site comply with the standard and specifications | Delivery docket, Supplier certificate, Photo | Prior to the commencement of Works | Visual | C | QE/SP/MC
3.9 | Geotextile | Geotextile underlay bidim A37 or similar approved material. Drawings C260 - C261 | Procured Geotextile comply with specifications | Delivery docket, Photo, Engineer approval | Prior to the commencement of Works | Visual | C | QE/SP/MC

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
4.1 | Hazardous Waste and Contaminated soils | Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3, 1131: 13.5.3 | Dumping site approval for contamiantion type | Dumping Docket | Hazardous material identified is the filter media in the intermittent sand filters that are to be replaced. | Document Check | C | QE/SP/CR
4.2 | Existing Plastic Liner | To be kept if possible, take care not to damage when removing existing media. Drawing C261 | Existing filter media removed with minimum damage to the existing plastic liner | Methodology, QA records, Photos | During ISF media removal | Visual | C | QE/SP
4.3 | Pipe Line and Level | Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12 | Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer | Grade Check sheet | During pipe installation | Visual, Instrumental | C | SP/QE/SV
4.4 | PVC Pipe Installation | Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2, as applicable. Specs 1131: 15.3.1. | PVC Pipes Joints and Intallation comply with standard and specifications | Methodology, QA records, Photos | During pipe installation | Visual | C | QE/SP
4.5 | PVC Joints | All PVC-U shall be jointed by solvent cement weld. Drawing C260 | Joints are carried out as specified | Methodology, QA records, Photos | During pipe installation | Visual | C | QE/SP
4.6 | ISF PVC Laterals | DN40 PVC-U pipe with 6mm holes at 800mm centres facing upwards, positioned inside DN100 PVC-U pipe with 25mm holes in pipe invert at 150mm centers. Laterals to be positioned at 1.0m from centers in the horizontal. Drawing C260 | Laterals are installed as specified in drawings | Methodology, QA records, Photos | During pipe installation | Visual | C | QE/SP
4.7 | ISF PE Drains and Vents | 4xDN110 heavy dutty slotted PE drain pipe with air vents, to be positioned at 2.25m from centers in the horizontal. Drawing C261 | Drains are installed as specified in drawings | Methodology, QA records, Photos | During pipe installation | Visual | C | QE/SP
4.8 | Drainage Chip | Layers of 12mm and 20mm drainage chip as specified in Drawing C261 | Drainage chip layers installed as specified in drawings | Methodology, Delivery docket, QA records, Photos | During drainage chip installation | Visual | C | QE/SP
4.9 | Pea gravel | 4-7mm pea gravel layer above drainage chip layer and above coarse sand layer around drains as specified in Drawing C261 | Pea gravel layer installed as specified in drawings | Methodology, Delivery docket, QA records, Photos | During pea gravel installation | Visual | C | QE/SP
4.10 | Filter sand | Clean course sand: effective size 0.25 to 0.75mm, uniformity coefficient <4.0. Drawing C261 | Course sand layer installed as specified in drawings | Methodology, Delivery docket, QA records, Photos, Supplier certificate | During filter sand installation | Visual | C | QE/SP
4.11 | Cutting pipes | Where pipes need to be cut to form non-stardard lengths, pipes shall be cut by a method which complies with manufacturers recommendations and provides a clean square profile. Specs 1131: 15.3.7 | Pipe cutted up to the specifications | Methodology, Photos | During pipe installation | Visual | C | QE/SP

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER Insert additional or delete unused rows as required. Include reference to specification.
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type (Visual, other) | Inspection
[7 empty] | Key | By (Role Key) | Signature
5.1 | As-built Drawings | Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2 | Engineer Approval | QA records | At completion | - | H | QE/CR
5.2 | CCTV Inspection | All pipelines shall pass a CCTV inspection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3 | A pipeline will fail its inspection if: - The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter. - The pipe has visible dips or ponding of water. - The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects. - There is evidence of infiltration at joints or laterals. | CCTV footage and log sheets | At every section of pipe installed. | Visual | H | QE/CR
5.3 | Surplus Materials and Refuse Disposal | All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2 | - | - | At completion | Visual | C | QE/SP/CR
5.4 | Cleaning | Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3 | - | - | At completion | Visual | C | QE/SP/CR
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: