## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 561469-ITP-0006 - Storage Tank (DG-QA-TP018) | itp |  |  |  |  | 561469-ITP-0006 - Storage Tank (DG-QA-TP018)
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Review all Drawings and Documents
label | Inspection Point: Quality Control Activity - Review all drawings and documentation provided to the Contractor.
label | Acceptance Criteria - Prior to the commencement of Works it must be ensure that all necessary documentation has been provided.
label | Verifying Document - ITP
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - R
label | Inspection: By - PM/QE
checkpoint | 3.2 - Setting Out Levels and Alignment
label | Inspection Point: Quality Control Activity - All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4
label | Acceptance Criteria - Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Compliance surveys or spot checks
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
label | Inspection: By - SP/QE/SV
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Valves Delivery
label | Inspection Point: Quality Control Activity - Gate valves shall comply with AS/NZS 2638. Valves greater than DN50 shall be resilient seated sluice valves. DN50 shall be gate valves. Sluice valves shall be anti-clockwise closing. DN50 gate valves shall be clockwise closing. Valves shall be provided with a surface box according to the asset owner’s engineering standards. Specs 1131: 14.3.1
label | Acceptance Criteria - The charasteritics of the valves delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/CR
checkpoint | 3.4 - Joints and Fittings
label | Inspection Point: Quality Control Activity - All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2
label | Acceptance Criteria - The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/CR
checkpoint | 3.5 - Pipe Bedding and Haunching Agregate
label | Inspection Point: Quality Control Activity - Pipe bedding should be AP20 and in accordance with AS/NZS 2566.2 or AS/NZA 3725. Maximum Dry Density (MDD) and Optimum Water Content (OWC) of the aggregate must be provided. Specs 1131: 14.9.1
label | Acceptance Criteria - Visual Inspection, Engineer approval
label | Verifying Document - Delivery Docket, Laboratory test results
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Lab Test
label | Inspection: Key - H
label | Inspection: By - QE/SP/MC
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Backfill Aggregate
label | Inspection Point: Quality Control Activity - Backfill aggregate should be GAP 65. Samples of backfill material should be tested in accordence of NZS 4402 to determine the MDD at OMC. The solid density of aggregate should be tested in accordance with NZS 4407. Specs 1131: 16.1.1
label | Acceptance Criteria - Visual Inspection, Engineer approval
label | Verifying Document - Delivery Docket, Laboratory test results
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Lab Test
label | Inspection: Key - H
label | Inspection: By - QE/SP/MC
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Concrete Manhole, Catchpits and Access Chambers
label | Inspection Point: Quality Control Activity - Precast concrete estructures shall comply with NZS 3106. Specs 1131: 14.5
label | Acceptance Criteria - Manhole charasteritics Match NZS 3106
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.8 - Material Storage
label | Inspection Point: Quality Control Activity - Storage for materiales must be arranged as it is described in: Specs 1131: 14.10
label | Acceptance Criteria - Pipe stored according to specifications
label | Verifying Document - Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.9 - Defective Materials
label | Inspection Point: Quality Control Activity - Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12
label | Acceptance Criteria - Defective material detected and removed from site
label | Verifying Document - Delivery docket, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Hazardous Waste and Contaminated soils
label | Inspection Point: Quality Control Activity - Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3
label | Acceptance Criteria - Dumping site approval for contamiantion type
label | Verifying Document - Dumping Docket
label | Frequency - If constaminated soils are found
label | Inspection Type (Visual, other) - Document Check
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
checkpoint | 4.2 - Trench Excavation
label | Inspection Point: Quality Control Activity - Trenches for flexible pipes shall be excavated within tollerances in table from Specs 1131: 15.2.5 unless otherwise stated.
label | Acceptance Criteria - Trench width and pipe clearance to walls comply with requirements
label | Verifying Document - Installation Check Sheet
label | Frequency - During trench excavation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.3 - Pipe Bedding and Haunching
label | Inspection Point: Quality Control Activity - Bedding and Haunching for flexible pipes should be in accordance with AS/NZS 2556.2 and have minimum embedment zone as shown in table from Specs 1131: 15.2.8.2
label | Acceptance Criteria - Bedding and haunching high and with comply width requirements
label | Verifying Document - Installation Check Sheet
label | Frequency - During bedding and haunching installation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.4 - Pipe Line and Level
label | Inspection Point: Quality Control Activity - Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12
label | Acceptance Criteria - Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Grade Check sheet
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - C
label | Inspection: By - SP/QE/SV
checkpoint | 4.5 - Precast Concrete Pipe Installation
label | Inspection Point: Quality Control Activity - Joints between precast pipe units shall be self-centering and shall be sealed with butyl mastic or similar approved to form a watertight joint. Concrete pipes shall be installed in accordance with AS/NZS 3725. Specs 1131: 15.3.6
label | Acceptance Criteria - Precast concrete pipes Joints and Intallation comply with standard and specifications
label | Verifying Document - Methodology. QA records
label | Frequency - Per joint, and during pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.6 - Aggregate Compaction
label | Inspection Point: Quality Control Activity - Compaction shall be as stated in Specs 1131: 15.4.4. For concrete pipes the verification testing of compaction shall use a method recommended in table 3 of the CPAA Technical Note on Installing Concrete Pipe and approved by the Engineer. Specs 1131: 15.3.6
label | Acceptance Criteria - Compaction Value ≥ Specification Value
label | Verifying Document - Depending of Pipe material or Aggregate: CBR Checksheet, Nuclear Density Meter (NDM) Results Sheet, Clegg Hamer test records
label | Frequency - each layer
label | Inspection Type (Visual, other) - On site Test
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.7 - Backfill Compaction
label | Inspection Point: Quality Control Activity - Selected fill within 0.8m depth from finished surface shall be AP 65. Subgrade and subbase shall be compacted in layers no greater than 200 mm thick unless otherwise agreed with the Engineer. Under carriageway basecourse shall be compacted in layers no greater than 150mm thick unless otherwise aggred with the engineer. Specs 1131: 15.4.3.2, 15.4.3.3
label | Acceptance Criteria - Dry Density ≥ 90% MDD
label | Verifying Document - Nuclear Density Meter (NDM) Results Sheet or Clegg Hamer test records
label | Frequency - each layer
label | Inspection Type (Visual, other) - On site Test
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.8 - Topsoiling and grassing
label | Inspection Point: Quality Control Activity - Topsoil shall be used to dress areas disturbed by the contrat works to a minimum thickness of 100mm. Grass seed shall be sown evenly over the prepared topsoil area. Specs 1131: 15.8.6
label | Acceptance Criteria - Topsoil installed and grass seed spread in the specified rate and mixture.
label | Verifying Document - QA records, Photos
label | Frequency - After compaction of final layer of backfill
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.9 - PE pipes Welding
label | Inspection Point: Quality Control Activity - In accordance with manufactures specifications. Where unspecified butt welding in accordance with PIPA POP003 and electrofusion welding in accordance with PIPA POP001. All welds shall be marked with weld number and welder identification. Specs 1131: 15.3.2.1.
label | Acceptance Criteria - PE Welding ejectuded as specified
label | Verifying Document - QA records, Weld records
label | Frequency - Per weld
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/WS
checkpoint | 4.10 - Welded Joints Inspections
label | Inspection Point: Quality Control Activity - Each butt-welded joint will be visually inspected by the engineer and Each electrofusion joint shall be visually inspected by the contractor according to Specs 1131: 16.3.2.1
label | Acceptance Criteria - Welded Joints complies with visual inspection specified
label | Verifying Document - QA records, Weld records, Photo
label | Frequency - After welding each joint
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - QE/SP/WS
checkpoint | 4.11 - Pipes Connected to Structures
label | Inspection Point: Quality Control Activity - Where a pipe is built into an underground structure, the requirements stipulated in Specs 1131: 15.3.10 must be followed
label | Acceptance Criteria - Pipe is connected to the structures according to the specifications
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During installation
label | Inspection Type (Visual, other) - Visual, Measurement Check
label | Inspection: Key - C
label | Inspection: By - QE/SP
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As-built Drawings
label | Inspection Point: Quality Control Activity - Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Manholes
label | Inspection Point: Quality Control Activity - Manholes should be tested seperately to pipeline for water tightness up to lower rim of manhole cover frame. Testing shall be in the presence of the engineer. Specs 1131: 16.2.2.5
label | Acceptance Criteria - A maximum drop in water level over 30 min should not exceed 2mL/hr/mm of diameter/meter height of the manhole. Engineer Approval
label | Verifying Document - Test Records
label | Frequency - For every manhole installed (24hr prior notice to the engineer before test)
label | Inspection Type (Visual, other) - Test
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - CCTV Inspection
label | Inspection Point: Quality Control Activity - All pipelines shall pass a CCTV inspection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3
label | Acceptance Criteria - A pipeline will fail its inspection if:
label | – The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter.
label | – The pipe has visible dips or ponding of water.
label | – The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects.
label | – There is evidence of infiltration at joints or laterals.
label | Verifying Document - CCTV footage and log sheets
label | Frequency - At every section of pipe installed.
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.4 - Surplus Materials and Refuse Disposal
label | Inspection Point: Quality Control Activity - All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
checkpoint | 5.5 - Cleaning
label | Inspection Point: Quality Control Activity - Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date: