## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 561469-ITP-0007 - Sand Filter (DG-QA-TP018) | itp |  |  |  |  | 561469-ITP-0007 - Sand Filter (DG-QA-TP018)
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Review all Drawings and Documents
label | Inspection Point: Quality Control Activity - Review all drawings and documentation provided to the Contractor.
label | Acceptance Criteria - Prior to the commencement of Works it must be ensure that all necessary documentation has been provided.
label | Verifying Document - ITP
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - R
label | Inspection: By - PM/QE
checkpoint | 3.2 - Setting Out Levels and Alignment
label | Inspection Point: Quality Control Activity - All setting out shall be performed by or under the control of a licensed surveyor, who shall certify the accuracy of key dimensions of the as constructed works. Specs 1000: 3.2.4
label | Acceptance Criteria - Levels and allignment Set Out matches marks shown on the Drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Compliance surveys or spot checks
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - H
label | Inspection: By - SP/QE/SV
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Pipes Delivery
label | Inspection Point: Quality Control Activity - Pipes and pipe fittings shall be of the material, pipe class and joint type nominated on the Drawings. Specs 1131: 14.1 and Drawings C260 - C261
label | Acceptance Criteria - The charasteritics of the pipes delivered to site match the corresponding drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/CR
checkpoint | 3.4 - Joints and Fittings
label | Inspection Point: Quality Control Activity - All joints and fittings must comply with wath is estipulated on Specs 1131: 14.3.2
label | Acceptance Criteria - The charasteritics of the fittings delivered to site match the corresponding specifications, drawings details or approved equivalent
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/CR
checkpoint | 3.5 - Drainage Aggregate
label | Inspection Point: Quality Control Activity - Drainage aggregate shall be 19 mm uniformly graded, clean, durable aggregate having a crushing resistance of not less than 100 kN when tested in accordance with NZS 4407. Material used for backfilling the trench above any geotextile wrapping shall be free draining granular material. Specs 1131: 14.9.2
label | Acceptance Criteria - Visual Inspection
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.6 - Material Storage
label | Inspection Point: Quality Control Activity - Storage for materiales must be arranged as it is described in: Specs 1131: 14.10
label | Acceptance Criteria - Pipe stored according to specifications
label | Verifying Document - Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.7 - Defective Materials
label | Inspection Point: Quality Control Activity - Any materials that do not comply with this specification or that have been damaged as a result of the Contractor’s operations shall be removed from site and replaced at the Contractor’s expense. Repairs may be considered at the sole discretion of the Engineer. Specs 1131: 14.12
label | Acceptance Criteria - Defective material detected and removed from site
label | Verifying Document - Delivery docket, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.8 - PVC Pipes
label | Inspection Point: Quality Control Activity - PVC-U gravity pipes for sewer, drainage, ducting or venting shall comply with AS/NZS 1260. Shall have spigot and socket joints with rubber rings. Specs 1131: 14.2.1 and Drawings C260 - C261
label | Acceptance Criteria - The charasteritics of the PVC pipes delivered to site comply with the standard and specificationsDelivery docket, Supplier certificate, Photo
label | Verifying Document - Delivery docket, Supplier certificate, Photo
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
checkpoint | 3.9 - Geotextile
label | Inspection Point: Quality Control Activity - Geotextile underlay bidim A37 or similar approved material. Drawings C260 - C261
label | Acceptance Criteria - Procured Geotextile comply with specifications
label | Verifying Document - Delivery docket, Photo, Engineer approval
label | Frequency - Prior to the commencement of Works
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/MC
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Hazardous Waste and Contaminated soils
label | Inspection Point: Quality Control Activity - Contaminated soils (Type H materials) encountered shall be treated and/or disposed off site in accordance with statutory requirements. Specs 1110: 9.3, 1131: 13.5.3
label | Acceptance Criteria - Dumping site approval for contamiantion type
label | Verifying Document - Dumping Docket
label | Frequency - Hazardous material identified is the filter media in the intermittent sand filters that are to be replaced.
label | Inspection Type (Visual, other) - Document Check
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
checkpoint | 4.2 - Existing Plastic Liner
label | Inspection Point: Quality Control Activity - To be kept if possible, take care not to damage when removing existing media. Drawing C261
label | Acceptance Criteria - Existing filter media removed with minimum damage to the existing plastic liner
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During ISF media removal
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.3 - Pipe Line and Level
label | Inspection Point: Quality Control Activity - Pipes shall be laid true to the design line and level within the tolerances specified in Specs 1131: 15.9. Invert levels shall take precedence over depths. Specs 1131: 15.3.12
label | Acceptance Criteria - Pipe levels are within the tolerance and according to the drawings, 2D data and linework provided or agreed with the Engineer
label | Verifying Document - Grade Check sheet
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual, Instrumental
label | Inspection: Key - C
label | Inspection: By - SP/QE/SV
checkpoint | 4.4 - PVC Pipe Installation
label | Inspection Point: Quality Control Activity - Buried PVC pipes shall be installed in accordance with AS/NZS 2032 and AS/NZS 2566.2, as applicable. Specs 1131: 15.3.1.
label | Acceptance Criteria - PVC Pipes Joints and Intallation comply with standard and specifications
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.5 - PVC Joints
label | Inspection Point: Quality Control Activity - All PVC-U shall be jointed by solvent cement weld. Drawing C260
label | Acceptance Criteria - Joints are carried out as specified
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.6 - ISF PVC Laterals
label | Inspection Point: Quality Control Activity - DN40 PVC-U pipe with 6mm holes at 800mm centres facing upwards, positioned inside DN100 PVC-U pipe with 25mm holes in pipe invert at 150mm centers. Laterals to be positioned at 1.0m from centers in the horizontal. Drawing C260
label | Acceptance Criteria - Laterals are installed as specified in drawings
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.7 - ISF PE Drains and Vents
label | Inspection Point: Quality Control Activity - 4xDN110 heavy dutty slotted PE drain pipe with air vents, to be positioned at 2.25m from centers in the horizontal. Drawing C261
label | Acceptance Criteria - Drains are installed as specified in drawings
label | Verifying Document - Methodology, QA records, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.8 - Drainage Chip
label | Inspection Point: Quality Control Activity - Layers of 12mm and 20mm drainage chip as specified in Drawing C261
label | Acceptance Criteria - Drainage chip layers installed as specified in drawings
label | Verifying Document - Methodology, Delivery docket, QA records, Photos
label | Frequency - During drainage chip installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.9 - Pea gravel
label | Inspection Point: Quality Control Activity - 4-7mm pea gravel layer above drainage chip layer and above coarse sand layer around drains as specified in Drawing C261
label | Acceptance Criteria - Pea gravel layer installed as specified in drawings
label | Verifying Document - Methodology, Delivery docket, QA records, Photos
label | Frequency - During pea gravel installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.10 - Filter sand
label | Inspection Point: Quality Control Activity - Clean course sand: effective size 0.25 to 0.75mm, uniformity coefficient <4.0. Drawing C261
label | Acceptance Criteria - Course sand layer installed as specified in drawings
label | Verifying Document - Methodology, Delivery docket, QA records, Photos, Supplier certificate
label | Frequency - During filter sand installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
checkpoint | 4.11 - Cutting pipes
label | Inspection Point: Quality Control Activity - Where pipes need to be cut to form non-stardard lengths, pipes shall be cut by a method which complies with manufacturers recommendations and provides a clean square profile. Specs 1131: 15.3.7
label | Acceptance Criteria - Pipe cutted up to the specifications
label | Verifying Document - Methodology, Photos
label | Frequency - During pipe installation
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - As-built Drawings
label | Inspection Point: Quality Control Activity - Two hard copies and one electronic copy of As-built drawings shall be prepared in draft and final versions following Schedule 1D in NZS4404:2010. Specs 1000: 3.9.2
label | Acceptance Criteria - Engineer Approval
label | Verifying Document - QA records
label | Frequency - At completion
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - CCTV Inspection
label | Inspection Point: Quality Control Activity - All pipelines shall pass a CCTV inspection. All pipelines shall be free of debris and flushed 24hrs prior to inspection. Specs 1131: 16.2.3
label | Acceptance Criteria - A pipeline will fail its inspection if:
label | – The pipe is horizontally misaligned or deformed by more than 5 % of the pipe diameter.
label | – The pipe has visible dips or ponding of water.
label | – The pipe has visible defects, such as open or displaced joints, defective or protruding laterals, cracked barrels or similar defects.
label | – There is evidence of infiltration at joints or laterals.
label | Verifying Document - CCTV footage and log sheets
label | Frequency - At every section of pipe installed.
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - H
label | Inspection: By - QE/CR
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.3 - Surplus Materials and Refuse Disposal
label | Inspection Point: Quality Control Activity - All surplus, redundant and faulty materials must be removed from the Site and dispose of them in a safe and legal manner. Any demolition material or rubbish coming from the execution of the project must be removed as well. Specs 1000: 3.13.2
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
checkpoint | 5.4 - Cleaning
label | Inspection Point: Quality Control Activity - Completed items of construction about to be placed in service or occupied for their intended use must be properly and thoroughly cleaned of all foreign matter and other debris. Specs 1000: 3.13.3
label | Frequency - At completion
label | Inspection Type (Visual, other) - Visual
label | Inspection: Key - C
label | Inspection: By - QE/SP/CR
section | SECTION 6 - COMMENTS
checkpoint | Customer Release Granted
textbox | Certificate Number:
date | Date: