## ITP-xxx
|  |  | Inspection and Test Plan - Installation of Conduits & Pits | [7 empty] | Document # ITP-033
[11 empty] | Revision : 0 | Date : 24/01/24
Client: |  | VicRoads |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  | Latrobe & Swanston St |  | Installation of Conduit System – Trenching & Boring |  | Name: Jake Cardillo |  | Name: | Aaron Hatch |  | Name: Shaun Kent
Contract No: |  | 8B4400 |  | Specifications: VicRoads Specification Section 733
|  |  |  | Structure / Component: |  | Signed : |  | Signed : |  |  | Signed :
|  |  |  | Location: |  | Date : 24/01/24 |  | Date : 24/01/24 |  |  | Date : 24/01/24
Lot No: |  |  | Lot Details: | [5 empty] | Lot Size/ Quantity:
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check for correct documentation |  | Prior to commencing any activity | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings -all drawings are the latest revision | Drawings and drawing registers | Visual inspection | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
1.2 | Implementation of all measures and controls |  | Prior to commencing any activity | All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP | PSP, EMP, TMP, JSEA, SWMS, WP | Visual Inspection | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
1.3 | Materials |  | Per Batch | • Cable pits shall be VicRoads approved prefabricated polyethylene type • Electrical supply conduit to be Orange HDPE 100mm diameter • Cable pit lids shall be VicRoads type approved, impressed with 'VicRoads' and 'Electrical', 'Communication', 'Traffic signals" as appropriate as per VicRoads Standard Drawing TC-1220 • Bedding and backfill material: Materials used shall be free from perishable matter and shall conform with the appropriate grading and plasticity index requirements specified in Table 733.061 | 733.02 Table 733.061 | Verify | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
2 | Construction Works
2.1 | Survey set-out |  | As required | Work is set out in accordance with drawings. | Work procedure | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
2.2 | Excavation/Boring & Trenching |  | Prior to Backfill | • Saw cut edge of trench within road pavement as required for trenching works | 733.07 | Verify | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
2.3 | Bedding Material |  | Each Lot | • Bedding material shall be placed and compacted for the full width of the trench to a depth of not less than 80 mm on an earth foundation or 200 mm on a rock foundation. Bedding material must not be the same material excavated for the trench, it shall be clearly identifiable as introduced material. • Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by superintendent or representative. | 733.06 | Verify | This ITP signed | HP | Superintendent / FH Engineer | N/A |  | N/A
2.4 | Installation of Conduits |  | Each Lot | • All conduits to terminate in a pit in accordance with the arrangement in TC-1207 • All conduits shall be temporarily sealed prior to cabling to avoid blockage • Conduits for detector cables installed as per TC-1207 and TC-1320 • No bends in continuous sections of conduit shall be permitted. • Changes in conduit direction shall only occur at a pit. • Changes in conduit direction or depth are to be made by natural swept bends – no elbows or tees • Conduits shall be suitably aligned as they enter and leave pits to aid pulling cables | 733.04 Table 733.042 | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
2.5 | Minimum Conduit Cover |  | Each Lot | • Unless otherwise shown on the drawings or specified, trenches shall comply with the depth requirements in Table 733.031 which outline minimum conduit cover under tram tracks is to be 1200mm from top of conduit to top of track surface level. | Table 733.031 | Verify | This ITP signed | HP | Superintendent / FH Engineer | N/A |  | N/A
2.6 | Backfill Material |  | Each Lot | • Filling material unless otherwise specified or shown on the drawings, selected and common backfill shall be placed and compacted. Where the trench has been excavated from the design subgrade level or above, the trench shall be backfilled to design subgrade level with selected backfill material, and above that level with common backfill material or the specified pavement material. | 733.06 | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
2.7 | Installation of Draw Cords |  | Each Lot | • All conduits shall be provided with a draw string secured at the ends | 733.05 | Verify | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
2.8 | Installation of marker tape |  | Each Lot | Marker tape at 100mm wide is to be installed 300mm above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top. | TC-2204 | Verify | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
2.9 | Cable Pits & Pit Lids |  | Each Lot | • Cable pits are to be constructed and installed as per drawings • Cable pits for traffic signals constructed and installed as per TC-1210, TC-1220 and TC-1230 • Heavy duty pit lids shall be provided where the pit is located within a road pavement. • Pits shall be located in accessible locations for maintenance activities. • Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement | 733.07 | Verify | This ITP signed | HP* | Fulton Hogan Engineer | N/A |  | N/A
3 | Completion
3.1 | Cleaning of Site |  | Each Lot | • Surplus excavated material shall be removed from road reserve. All affected areas shall be restored to similar conditions that existed prior to work. | 733.09 | Visual inspection | This ITP signed | WP | Fulton Hogan Engineer | N/A |  | N/A
3.2 | Recording/As Built |  | Each Lot | Unless otherwise specified, the actual installed location and depth of conduits, and location of pits, shall be accurately recorded on as-constructed drawings in a format agreed by the Superintendent. | 733.1 | Verify | This ITP signed As Built Drawings | WP | Fulton Hogan Engineer | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: |  | Position: |  | Signature: |  |  |  |  | Date: / /
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
AP | Approval Point | Written or verbal approval given by the Superintendent
Note on K16: Rodrigo Anchico: Write "N/A" to disable the cell.