## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-033 - Vicroads Installation of Conduits & Pits | itp |  |  |  |  | ITP-033 - Vicroads Installation of Conduits & Pits
section | Preliminary Works
checkpoint | 1.1 Check for correct documentation
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: Ensure that all employees and subcontractors are:
label | – using the correct and complete set of drawings
label | – all drawings are the latest revision
label | REFERENCE DOCUMENTS: Drawings and drawing registers
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.2 Implementation of all measures and controls
label | FREQUENCY: Prior to commencing any activity
label | ACCEPTANCE CRITERIA: All necessary measures and controls are being implemented, that is: PSP, EMP, TMP, JSEA, SWMS & WP
label | REFERENCE DOCUMENTS: PSP, EMP, TMP, JSEA, SWMS, WP
label | INSPECTION/TEST METHOD: Visual Inspection
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 1.3 Materials
label | FREQUENCY: Per Batch
label | ACCEPTANCE CRITERIA: Cable pits shall be VicRoads approved prefabricated polyethylene type
label | ○ Electrical supply conduit to be Orange HDPE 100mm diameter
label | ○ Cable pit lids shall be VicRoads type approved, impressed with 'VicRoads' and 'Electrical', 'Communication', 'Traffic signals" as appropriate as per VicRoads Standard Drawing TC-1220
label | ○ Bedding and backfill material: Materials used shall be free from perishable matter and shall conform with the appropriate grading and plasticity index requirements specified in Table 733.061
label | REFERENCE DOCUMENTS: 733.02 Table 733.061
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Construction Works
checkpoint | 2.1 Survey set-out
label | FREQUENCY: As required
label | ACCEPTANCE CRITERIA: Work is set out in accordance with drawings.
label | REFERENCE DOCUMENTS: Work procedure
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.2 Excavation/Boring & Trenching
label | FREQUENCY: Prior to Backfill
label | ACCEPTANCE CRITERIA: Saw cut edge of trench within road pavement as required for trenching works
label | REFERENCE DOCUMENTS: 733.07
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.3 Bedding Material
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Bedding material shall be placed and compacted for the full width of the trench to a depth of not less than 80 mm on an earth foundation or 200 mm on a rock foundation. Bedding material must not be the same material excavated for the trench, it shall be clearly identifiable as introduced material.
label | ○ Once the bedding material has been laid and the conduits put in place, works shall not proceed prior to inspection by superintendent or representative.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Superintendent / FH Engineer
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.4 Installation of Conduits
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All conduits to terminate in a pit in accordance with the arrangement in TC-1207
label | ○ All conduits shall be temporarily sealed prior to cabling to avoid blockage
label | ○ Conduits for detector cables installed as per TC-1207 and TC-1320
label | ○ No bends in continuous sections of conduit shall be permitted.
label | ○ Changes in conduit direction shall only occur at a pit.
label | ○ Changes in conduit direction or depth are to be made by natural swept bends – no elbows or tees
label | ○ Conduits shall be suitably aligned as they enter and leave pits to aid pulling cables
label | REFERENCE DOCUMENTS: 733.04 Table 733.042
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.5 Minimum Conduit Cover
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Unless otherwise shown on the drawings or specified, trenches shall comply with the depth requirements in Table 733.031 which outline minimum conduit cover under tram tracks is to be 1200mm from top of conduit to top of track surface level.
label | REFERENCE DOCUMENTS: Table 733.031
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP
label | RESPONSIBILITY: Superintendent / FH Engineer
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.6 Backfill Material
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Filling material unless otherwise specified or shown on the drawings, selected and common backfill shall be placed and compacted. Where the trench has been excavated from the design subgrade level or above, the trench shall be backfilled to design subgrade level with selected backfill material, and above that level with common backfill material or the specified pavement material.
label | REFERENCE DOCUMENTS: 733.06
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.7 Installation of Draw Cords
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: All conduits shall be provided with a draw string secured at the ends
label | REFERENCE DOCUMENTS: 733.05
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.8 Installation of marker tape
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Marker tape at 100mm wide is to be installed 300mm above each line of conduits in all trenches where electrical and communications conduits are provided. When constructed in a shared trench, it must be ensured that the electrical warning tape is on top.
label | REFERENCE DOCUMENTS: TC-2204
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 2.9 Cable Pits & Pit Lids
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Cable pits are to be constructed and installed as per drawings
label | ○ Cable pits for traffic signals constructed and installed as per TC-1210, TC-1220 and TC-1230
label | ○ Heavy duty pit lids shall be provided where the pit is located within a road pavement.
label | ○ Pits shall be located in accessible locations for maintenance activities.
label | ○ Pits shall be constructed such that the level of the top of the pit lid matches surrounding finished surface level, top of pit wall is finished so that lid fits without movement
label | REFERENCE DOCUMENTS: 733.07
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed
label | HP*
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
section | Completion
checkpoint | 3.1 Cleaning of Site
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Surplus excavated material shall be removed from road reserve. All affected areas shall be restored to similar conditions that existed prior to work.
label | REFERENCE DOCUMENTS: 733.09
label | INSPECTION/TEST METHOD: Visual inspection
label | RECORD OF CONFORMITY: This ITP signed
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | 3.2 Recording/As Built
label | FREQUENCY: Each Lot
label | ACCEPTANCE CRITERIA: Unless otherwise specified, the actual installed location and depth of conduits, and location of pits, shall be accurately recorded on as-constructed drawings in a format agreed by the Superintendent.
label | REFERENCE DOCUMENTS: 733.1
label | INSPECTION/TEST METHOD: Verify
label | RECORD OF CONFORMITY: This ITP signed, As Built Drawings
label | WP
label | RESPONSIBILITY: Fulton Hogan Engineer
textbox | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: