## 1. Subsoil drainage
Inspection & Test Plan
Project Name : |  |  | Lot : | 6 | Lot Code : | DCnn | 6.1 | Date Issued :
Description : | Subsoil Drainage |  | Location : |  |  |  |  | Rev : | 0
Lot Code | Description |  |  |  | Spec Reference Special Conditions | Acceptance Criteria | Verifying Document | Verification / Witness - To Print and Sign |  |  |  | Date
[8 empty] | Contractor |  | Client's Rep.
[8 empty] | Print | Sign | Print | Sign
1 | Preliminary
1.1 | Ensure latest drawing revision is being used |  |  |  |  | CI | Drawing No:
1.2 | Use face of kerb set out to set out subsoil drainage |  |  |  | NZS4202 | WP
1.3 | Excavation to be set out according to survey marks and appropriate benchmark RLs |  |  |  |  | CI
2 | Excavation
2.1 | Excavation to be carried out using correct offsets based on FSL |  |  |  |  | CI | Drawing No:
HOLD - Continue only if the above is signed off.
3 | Subsoil Drainage installation
3.1 | Install Bidim and Subsoil drain and associated connections to Manholes/pipes/CP |  |  |  | TNZ F/2 | CI | Drawing No:
3.2 | Backfill with drainage metal |  |  |  |  | CI | Photos and mark-up drawings
3 | Backfill
3.1 | Backfill excavation using GAP65. Backfill to be placed and compacted in 150mm layers. |  |  |  | Civil Specifications | CI
4 | Handover to client
4.1 | Handover to client |  |  |  |  | HP
HOLD - Continue only if the above is signed off.
Rev. Status | Date | Reason for Rev. |  |  | HP - MANDATORY HOLD POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | WP - WITNESS POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | CI - CHECK ITEM |  |  | Signed by: |  | Leading Hand, Foreman Engineer (Contractor)
Comments / Required Actions :
| Contractors Representative | [5 empty] | Clients Representative |  |  |  |  | Revision 3
| Signature: | [5 empty] | Signature:
| Print: | [5 empty] | Print:
| Date: | [5 empty] | Date:

## 2. SW drainage
Inspection & Test Plan
Project Name : |  |  | Lot Number : | 13 | Lot Code : | Cunn | RSnn | Date Issued :
Description : | Stormwater Drainage |  | Location : |  |  |  |  | Rev : | 1
Lot Code | Description |  |  |  | Spec Reference Special Conditions | Acceptance Criteria | Verifying Document | Verification / Witness - To Print and Sign |  |  |  | Date
[8 empty] | Contractor |  | Client's Rep.
[8 empty] | Print | Sign | Print | Sign
SW1.0 | Set Out
1.1 | Ensure that the latest revision of the relevant drawing is being used. |  |  |  |  | CI | Drawing Register;
1.2 | Confirm existing and proposed drainage locations |  |  |  |  | CI | Survey Layout: Drawing ________________
HOLD - Continue only if the above is signed off.
SW2.0 | Stormwater Excavation
2.1 | Complete council Kick-off meeting |  |  |  |  | HP | Council inspection report
2.2 | All stormwater pipes and manholes shall be placed in accordance with surveyor's layout and locations given in design drawings. |  |  |  | NZA/AS 1260 | CI | M&P drainage long section sheet, M&P manhole sheet
2.3 | Stormwater trench should be excavated to design levels given in drawings. Tolerances given are -0mm, +50mm for line and -50mm, +0mm for level. Trench to be benched or battered when depth exceed 1.2m. Trench width to be dependant on pipe diameter and trench depth. |  |  |  | Drawing C-C401 and C-C402 | HP | M&P drainage long section sheet, M&P manhole sheet
2.4 | IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout. |  |  |  |  | HP | Geotech signoff
HOLD - Continue only if the above is signed off.
2.5 | Breakout to commence once Client issue site instruction |  |  |  |  | WP | Site Instruction
HOLD - Continue only if the above is signed off.
HOLD - Continue only if the above is signed off.
SW3.0 | Stormwater Installation
3.1 | All manholes shall be installed with accordance to locations shown on civil drawings. Any variations to be approved by Client prior to installation. |  |  |  | Drawing C-C401 and C-C402 | CI | Survey Layout
3.2 | Stormwater mains and downpipes to be laid out in accordance with design drawings. Any Variations to be approved by Client before installation. |  |  |  | Drawing C-C401 and C-C402 | HP | Survey Layout
3.3 | Pipes shall be laid true to alignment and with inverts true to grade. All manhole connections shall be in accordance with civil engineering specifications and Auckland Council standard drawings. |  |  |  | SWCoP DWG No. SW05 | CI | M&P Long Section Sheet, M&P Manhole Check Sheets
3.4 | Stormwater Detention tank and Orifice to be installed as per Civil and supplier specifications |  |  |  | Civil / Supplier specifications | CI | As build report and photo record
HOLD - Continue only if the above is signed off.
3.5 | M&P Drainage long section and Manhole sheets to be completed. |  |  |  |  | CI | M&P drainage long section sheet, M&P manhole sheet
3.6 | Pipes shall be bedded on 100mm minimum depth of approved fine granular material. |  |  |  | AS/NZS 2566 Part 2: 2002 | CI | M&P Long Section Sheet, M&P Manhole Check Sheets
3.7 | Lower surface to 1/4 of the pipe diameter shall be on the compacted material. From this point up to 300mm above the crown of the pipe, selected filling material (with 20mm maximum partial size) shall be rammed & tamped in layers of no more than 150mm depth. |  |  |  | AS/NZS 2566 Part 2: 2002 | CI
3.8 | All pipework to be inspected by clients engineer and Council inspector and signed off before trench can be backfilled |  |  |  |  | HP | Council & Engineer Approval Report
HOLD - Continue only if the above is signed off.
3.9 | If instructed by Client - Any pipe with less than 600mm cover must be concrete capped |  |  |  |  | CI | Ste instruction
3.1 | Trench to be backfilled with approved granular material and compacted sufficiently |  |  |  | AS/NZS 2566 Part 2: 2002 | CI
WW 4.0 | Handover to client with PS3
4.1 | Complete Council final drainage inspection |  |  |  |  | HP | Council inspection report
4.2 | Completed pipe sections to be CCTV'd |  |  |  |  | CI | CCTV Footage
4.3 | As build all pipe invert levels in manholes and CP and lid levels |  |  |  |  | HP | As build report
4.4 | Handover to client with PS3 |  |  |  | PS3 Drainage | HP | Hander documents
Rev. Status | Date | Reason for Rev. |  |  | HP - MANDATORY HOLD POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | WP - WITNESS POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | CI - CHECK ITEM |  |  | Signed by: |  | Leading Hand, Foreman Engineer (Contractor)
Comments / Required Actions :
| Contractors Representative | [5 empty] | Clients Representative |  |  |  |  | Revision 3
| Signature: | [5 empty] | Signature:
| Print: | [5 empty] | Print:
| Date: | [5 empty] | Date:

## 3. WW Drainage
Inspection & Test Plan
Project Name : |  |  | Lot Number : | 13 | Lot Code : | Cunn | RSnn | Date Issued :
Description : | Wastewater drainage |  | Location : |  |  |  |  | Rev : | 0
Lot Code | Description |  |  |  | Spec Reference Special Conditions | Acceptance Criteria | Verifying Document | Verification / Witness - To Print and Sign |  |  |  | Date
[8 empty] | Contractor |  | Client's Rep.
[8 empty] | Print | Sign | Print | Sign
WW 1.0 | Set Out
1.1 | Ensure that the latest revision of the relevant drawing is being used. |  |  |  | NZS 3107 | CI | Drawing Register ________________
1.2 | Confirm existing and proposed drainage locations |  |  |  |  | CI | Survey Layout; Drawing:__________
WW2.0 | Wastewater
2.1 | Complete council Kick-off meeting |  |  |  |  | HP | Council inspection report
2.2 | All wastewater pipes and manholes shall be placed in accordance with surveyor's layout and locations given in design drawings. |  |  |  | NZA/AS 1260 | CI | M&P drainage long section sheet, M&P manhole sheet
2.3 | Wastewater trench should be excavated to design levels given in drawings. Tolerances given are -0mm, +50mm for line and -50mm, +0mm for level. Trench to be benched or battered when depth exceed 1.2m. Trench width to be dependant on pipe diameter and trench depth. Use trench shield if battered cannot be achieve. |  |  |  | Drawing C-C401 and C-C402 | HP | M&P drainage long section sheet, M&P manhole sheet
2.4 | IF rock is encountered levels and photos are to be taken. Geotech must inspect rock prior to any break out. Levels and photos must be taken post-breakout. |  |  |  |  | HP | Geotech signoff
HOLD - Continue only if the above is signed off.
2.5 | Breakout to commence only once Client have issued a site instruction |  |  |  |  | WP | H&R Site Instruction
HOLD - Continue only if the above is signed off.
WW 3.0 | Wastewater Installation
3.1 | All manholes shall be installed with accordance to locations shown on civil drawings. Any variations to be approved by Client prior to installation. |  |  |  | Drawing C-C401 and C-C402 | CI | Survey Layout
3.2 | Wastewater mains and downpipes to be laid out in accordance with design drawings. Any Variations to be approved by Client before installation. |  |  |  | Drawing C-C401 and C-C402 | HP | Survey Layout
3.3 | Pipes shall be laid true to alignment and with inverts true to grade. All manhole connections shall be in accordance with civil engineering specifications and Auckland Council standard drawings. |  |  |  | WWCoP DWG No. | CI | M&P Long Section Sheet, M&P Manhole Check Sheets: Drawing: _______________
HOLD - Continue only if the above is signed off.
3.4 | M&P Drainage long section and Manhole sheets to be completed. |  |  |  |  | CI | M&P drainage long section sheet, M&P manhole sheet
3.5 | Pipes shall be bedded on 100mm minimum depth of approved fine granular material. |  |  |  | NZS 2566 Part 2: 2002 | CI | M&P Long Section Sheet, M&P Manhole Check Sheets
3.6 | Lower surface to 1/4 of the pipe diameter shall be on the compacted material. From this point up to 300mm above the crown of the pipe, selected filling material (with 20mm maximum partial size) shall be rammed & tamped in layers of no more than 150mm depth. |  |  |  | NZS 2566 Part 2: 2002 | CI
3.7 | All pipework to be inspected by clients engineer and Council inspector and signed off before trench can be backfilled |  |  |  |  | HP | Council & Engineer inspection and/or Approval report
HOLD - Continue only if the above is signed off.
3.8 | Any pipe with less than 600mm cover must be noted to the client and wait approval to proceed |  |  |  |  | CI | Site Instruction
3.9 | Trench to be backfilled with approved granular material and compacted sufficiently |  |  |  | NZS 2566 Part 2: 2002 | CI
3.1 | Backfill materials must be compacted correctly and tested in 150mm - 300mm lifts |  |  |  |  | CI | Council & Engineer inspection and/or Approval report
WW 4.0 | Handover to client with PS3
4.1 | Complete Council final drainage inspection |  |  |  |  | HP | Council inspection report
4.2 | Completed pipe sections to be CCTV'd |  |  |  |  | CI | CCTV Footage
4.3 | As build all pipe invert levels in manholes and CP and lid levels |  |  |  |  | HP | As build report
4.4 | Handover to client with CS3 |  |  |  | CS3 Drainage | HP | Hander documents
Rev. Status | Date | Reason for Rev. |  |  | HP - MANDATORY HOLD POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | WP - WITNESS POINT |  |  | Signed by: |  | Engineer (Contractor) Engineer Rep (Principal)
[5 empty] | CI - CHECK ITEM |  |  | Signed by: |  | Leading Hand, Foreman Engineer (Contractor)
Comments / Required Actions :
| Contractors Representative | [5 empty] | Clients Representative |  |  |  |  | Revision 3
| Signature: | [5 empty] | Signature:
| Print: | [5 empty] | Print:
| Date: | [5 empty] | Date: