## Checklists
Type | Name | Values | Prefix | Postfix | Usage Count | User Addable | Template Name
checklist-flat | JHA - Job Hazard Analysis
section | Job details
date | Date:
textbox | Permit No.
textbox | Job No.
textbox | Site
textbox | Activity Location
textbox | Asset:
textbox | Work Details:
section | Prompts for Hazards - Mark all that apply.
button | Sparks/Open flame | YES,NO
button | Disabled safety device(s) | YES,NO
button | Uneven surfaces | YES,NO
button | Fatigue, over-exertion | YES,NO
button | Crane movements | YES,NO
button | Moving/Rotating parts | YES,NO
button | Remote area, working alone | YES,NO
button | Conflicting work/SIMOPS | YES,NO
button | Electrical arc flash | YES,NO
button | Sharp objects/materials | YES,NO
button | Restricted/Difficult Entry/Exit | YES,NO
button | Overhead obstacles | YES,NO
button | Ignition sources (other) | YES,NO
button | Access/Egress | YES,NO
button | Water body | YES,NO
button | Live equipment | YES,NO
button | Slippery surfaces | YES,NO
button | Suspended loads | YES,NO
button | Hazardous substances (chemicals) | YES,NO
button | Use of non-intrinsically safe equipment | YES,NO
button | Weather extremes | YES,NO
button | Moving vehicles | YES,NO
button | Task related noise | YES,NO
button | Engulfment | YES,NO
button | General waste | YES,NO
button | Hazardous waste | YES,NO
button | Hazardous/toxic substance, fumes, gas | YES,NO
button | Flammable materials - Gas, liquids, solids | YES,NO
button | Reduced visibility, lighting | YES,NO
button | Electricity | YES,NO
button | Static electricity | YES,NO
button | Work at height | YES,NO
button | Underground services | YES,NO
button | O2 Deficiency/Excess | YES,NO
button | Temperature extremes | YES,NO
button | Heavy objects | YES,NO
button | Radiation | YES,NO
button | Potential energy - Tension/Compression | YES,NO
button | Flying particles/Dust/Objects | YES,NO
button | Vehicle entry | YES,NO
button | Exposure to process temperatures. | YES,NO
section | Prompts for Initial Consequences - Mark all that apply | YES,NO
button | Falling/Dropped objects | YES,NO
button | Fall from height | YES,NO
button | Trip/Slip/Fall | YES,NO
button | Gas release | YES,NO
button | Pressure release | YES,NO
button | Struck by object | YES,NO
button | Exceeding tool limits | YES,NO
button | Overloading people | YES,NO
button | Unplanned shutdown | YES,NO
button | Exposure to O2 deficiency/excess | YES,NO
button | Exposure to hazardous substance | YES,NO
button | Entanglement | YES,NO
button | Flying objects | YES,NO
button | Loss of control | YES,NO
button | Loss of containment | YES,NO
button | Excess exposure to Emissions, dust, fumes, noise, fibres, heat | YES,NO
button | Loss of structural integrity | YES,NO
button | Equipment failure | YES,NO
button | Uncontrolled ignition source | YES,NO
button | Collision | YES,NO
button | Ignition/Fire | YES,NO
button | Back strain/Injury | YES,NO
button | Burns | YES,NO
button | Heat exhaustion | YES,NO
section | Initial controls - Mark all that apply. | YES,NO
note | People controls | YES,NO
button | Safety/Fire watch person | YES,NO
button | Barriers/Flagging | YES,NO
button | Warning signs | YES,NO
note | Equipment controls | YES,NO
button | Master tags and locks | YES,NO
button | Scaffolding for access | YES,NO
button | Radio communication | YES,NO
note | Environmental controls | YES,NO
button | Ventilation | YES,NO
button | Lighting | YES,NO
button | Gas Testing | YES,NO
note | High risk controls | YES,NO
button | WSCS Work permit | YES,NO
button | WSCS Certificates | YES,NO
button | Critical lift/Fall protection plan | YES,NO
button | Specialised PPE | YES,NO
button | Spill kit | YES,NO
button | Fire extinguisher | YES,NO
section | Signatures
textbox | Applicant name
signoff | Signatures
checklist-flat | JHA - Job Step
section | Task Step - add task step for each individual task
date | Date:
textbox | Task step number (eg. Step 1, Step 2 etc):
textbox | Task details:
textbox | Hazards:
dropdown | Initial score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
textbox | Potential consequence:
textbox | Controls:
textbox | Recovery steps:
dropdown | Residual score (Likelihood x Severity 1 - 25) - Refer to risk matrix | 1, 2, 3, 4, 5, 6, 8, 9, 10, 12, 15, 16, 20, 25
checklist-flat | Toolbox Meeting
section | Toolbox meeting
date | Date:
textbox | Meeting location:
textbox | Meeting conducted by:
textbox | Meeting attendees:
textbox | Today's work scope/Hazards
textbox | Hazard controls:
signoff | Signatures
checklist-flat | Safe/Unsafe Observation Card
section | Basic Details
button | Safe or Unsafe observation? | SAFE,UNSAFE
date | Date:
textbox | Observers Name
textbox | Site
textbox | Task Observed
section | Hazard Observation (select all that apply)
button | Mobile Equipment | YES,NO
button | Hoisting & Lifting | YES,NO
button | Dropped Objects | YES,NO
button | PPE & Process | YES,NO
button | Pressurised equipment | YES,NO
button | Machinery & Tools | YES,NO
button | Electrical equipment | YES,NO
button | Housekeeping | YES,NO
button | Person fall risk | YES,NO
button | Manual handling | YES,NO
button | Exposure to process temperatures. | YES,NO
button | Confined space | YES,NO
textbox | What I saw
textbox | What I did
button | Is further action required? | YES,NO
checkpoint | Observation reported?
textbox | Reported to:
textbox | Other comments
checklist | Isolation
section | Isolation details
date | Date:
dropdown | Type of Isolation | Electrical, Mechanical, Digital
textbox | Duration of isolation:
note | All isolations must be done in accordance with the Entec Lockout - Tagout procedure H-P-1-037
section | Add Isolation
checkpoint | Isolation applied
textbox | Isolated by:
checkpoint | Isolation checked
textbox | Checked by:
textbox | Isolation description
textbos | Personal Padlock No.
date | Date applied
section | Remove Isolation
checkpoint | Isolated equipment has been tested and is confirmed safe to liven
note | Ensure there are no personnel working on equipment to be livened, do a full point-to-point test of the circuit to ensure the correct circuit is being re-livened.
checkpoint | Isolation removed
textbox | Removed by:
checkpoint | Removal checked
textbox | Checked by:
date | Date removed
signoff | Isolator and Checker signoff.
checklist-flat | Entec Daily Report
date | Date:
textbox | Site:
textbox | Work completed:
textbox | Issues:
textbox | Weather:
textbox: | Labour
textbox: | Plant & Equipment used:
signoff | Signed/Approved:
checklist-flat | As-Built Drawings
section | As-Built Drawings - attach scanned documents
textbox | Drawing no.
checklist | Civil Checklist - LV Pillar Foundation
section | Ground Conditions:
checkpoint | Verify ground conditions are as-per design assumption
section | NAL/Schneider LV Pillar foundation installation:
checkpoint | Correct location per drawings
checkpoint | Subgrade has been prepared per drawings (attach photo)
checkpoint | Check for level
section | Ensure the conduits between Pillar and EV Charger are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Ensure the conduits between Pillar and Site Lighting/Selector Switch are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Ensure the Fibre Optic/Earthing conduits between Pillar and Sales Store are:
checkpoint | Sized as indicated in drawing
checkpoint | Routed per drawings
checkpoint | Depth defined in drawing
section | Verify working space from front of LV Pillar
checkpoint | Ensure placement will allow for working area and emergency egress
section | As-built height of foundation
checkpoint | Verify protrusion above ground level is as per specification/drawing
section | LV Pillar Installation - if LF Pillar is installed ensure:
checkpoint | Ensure LV Pillar has been bolted down with the correct torque settings as per LV pillar specification
checkpoint | Water tightness/IP Specifications are being met
checkpoint | Record and photograph the serial number of the LV Pillar
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - NAL Solution/Monolithic Foundation
section | Ground Conditions:
checkpoint | Verify ground conditions are as per design assumptions
section | Verify STAKKAbox Installation is:
checkpoint | Subgrade prepared per drawings
checkpoint | STAKKAbox installed at location shown on drawing
checkpoint | Correct number of STAKKAbox installed
checkpoint | STAKKAbox are clear of any debris
checkpoint | STAKKAbox are installed at correct depth
checkpoint | Conduits enter at correct locations and verify depth
checkpoint | Protruding above the ground within the specified limits
section | Verify NAL EV Charger Socket is:
checkpoint | Installed per drawing
checkpoint | Correct depth as-per drawing
checkpoint | Verify level prior to EV charger placement
section | Verify NAL Bollard Sockets are:
checkpoint | Installed per drawing & Counts verified
checkpoint | Correct depth & spacing
checkpoint | Verify level
section | Verify NAL Flex-Bollards are:
checkpoint | Installed per drawing & counts verified
checkpoint | Correct height & spacing
checkpoint | Verify they are plumb
checkpoint | Pass pull-test/unable to be lifted out by hand
section | Verify Monolithic foundation (as required) is:
checkpoint | Installed as-per drawing
checkpoint | Pad/foundation is correct depth and dimensions
checkpoint | Rebar is proper size and correctly spaced (Photo)
checkpoint | Top of pad is free of defects, has an even surface with broom finish
checkpoint | Verify conduits are stubbed up in correct location
checkpoint | Protruding above the ground within the specified limits
section | Verify Anchor bolts:
checkpoint | In correct location as per drawing
checkpoint | Proper embedment depth
checkpoint | Pass pull-test/unable to be lifted out by hand
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Lighting Columns/Selector Switch/Fixture
section | Verify that lighting columns are:
checkpoint | As-per drawings
section | Verify lighting selector switch is:
checkpoint | Installed per manufacturers specification
checkpoint | As-per drawings
section | Light fixtures
checkpoint | Verify Lumens as per specification
checkpoint | Record serial numbers
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - EV Charging Parking Stalls
section | Verify dimensions match drawings
checkpoint | Depth, Length and Width are per drawings
section | Painted stripes are clean and correct colour
checkpoint | No over spray, colour is correct, lines are straight
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Miscellaneous Site Civil
section | New curb/gutter footpath per plans
checkpoint | Concrete is consistent and installed to match existing appearance and levels
section | Existing curb/gutter sidewalk undamaged
checkpoint | No damage to existing curb/gutters
section | Landscaping removed/damaged during construction is replaced to match
checkpoint | Replacements match what was damaged
section | New landscaping installed per plans. Ensure proper watering is in plans. Verify:
checkpoint | Correct species
checkpoint | height of plants is per plan
checkpoint | irrigation is provided
section | Irrigation system working properly. Irrigation that was disrupted during construction is:
checkpoint | Repaired and operation verified (Site host to provide signature)
checkpoint | Spray patterns are set correctly
section | Air & Water station relocation
checkpoint | Verify air & water station is functioning after relocation (Site host to provide signature)
section | Wheel stops are installed per drawings
checkpoint | Dimensions, height and width are per drawings
section | Parking stall signage complete per plans
checkpoint | Confirm the height of sign posts above grade is accurate and matches drawings
section | Site clean up
checkpoint | All debris removed by the time commissioning occurs. Site housekeeping must be kept up to minimize the disruption to the landlords
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Civil Checklist - Miscellaneous - Site Specific
section | Corrosion Protection
checkpoint | Ensure all corrosion prone surfaces are covered
section | Sharp objects
checkpoint | Ensure no sharp edges/protrusions are present following the completion of work
section | Concrete slump test
checkpoint | Concrete slump test to be conducted prior to all concrete pour. Refer to concrete specification in drawings
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat | Cable Test Record
checkpoint | Upload completed ITR scans
checklist | Tritium - Site Installation checklist
checkpoint | Complete Tritium online installation portal
note | https://tritium.formtitan.com/ftproject/tritium-checklists
checklist | Electrical checklist - LV Pillar
section | LV Pillar Setup/Installation
checkpoint | Confirm the switchboard is correctly located, aligned and foundation bolts and fixings are secure as-per switchroom layout drawings
checkpoint | Check that the final factory test and inspection record is enclosed with the LV Pillar delivered.
checkpoint | Check the LV pillar serial number matches the factory test and inspection record.
checkpoint | Check the LV Pillar is correctly installed and sealed on the foundation plinth, as per the IOM Manual
checkpoint | Visually inspect the LV pillar for external damage (including paintwork)
checkpoint | Verify nameplate details against data sheet. (LV Pillar type, compliance standard, rating in amps)
checkpoint | Check all cubicle doors can be fully opened without obstruction and that door hinges are installed correctly.
checkpoint | Check inside of the switchboard is clean and dry, check that all preservation (i.e. silica gel) has been removed (Pre-Energization)
checkpoint | Ensure all major components conform to vendor's design documentation and drawings.
checkpoint | Check all fuses/fuse carriers and link are correct to drawings
checkpoint | Check all equipment carries the correct circuit identification
checkpoint | Check busbar phase identifications are correct and phasing is maintained
checkpoint | Ensure all busbars are encapsulated as-per design requirements
checkpoint | Check the protective device(s) rating match the approved design
checkpoint | Check LV Cable terminations are completed correctly and are tight and secure
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Cables/Cable Entry Points/Cable Containment
section | Cables/Cable Entry Points/Cable Containment
checkpoint | Check all cable entries are correct to design requirements and spare enters are correctly plugged with Rayflates/Foam
checkpoint | Check that the depth of installation of the duct network matches the approved design. (To be witnessed by BP)
checkpoint | Check the number and type/size of ducts installed meets the approved design. (To be witnessed by BP)
checkpoint | Check the cable entry is at the correct depth (Minimum bending radius achieved)
checkpoint | Check the correct type of reinstatement material has been used to backfill the cable/duct network. (100mm of sand below and on top of ducts/cables.)
checkpoint | Check cable warning tape is laid prior to backfilling
checkpoint | Check the high level cable containment (Trays/Ladders) and cable cleats match the approved design.
checkpoint | Check all metal cable containments are bonded and connected to the main earthing system
checkpoint | Check that the tray/ladder is not damaged and is free of any sharp edges.
section | Cables
checkpoint | Check the cables installed are the correct type/size, as per the approved design.
checkpoint | Check the correct bending radius is being applied to the cable at the entry/exit points
checkpoint | Check the cable cleat and clamp screw are secure and tight
checkpoint | Check that the cables have been fully tested after installation and prior to terminating to the LV Pillar (Continuity, insulation resistance)
checkpoint | Check that the cable ends have been correctly capped after installation in ducts, to avoid water ingress in the cable (unless terminated straight after installation and testing)
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Earthing System
section | Earthing System
checkpoint | Check earth electrode system is installed at the correct depth and as per the approved design
checkpoint | Earth bosses installed correctly
checkpoint | Check all earth cables/electrodes are correctly sized
checkpoint | Check that the equipment is bonded to the main earth
checkpoint | Check all the earth cable lugs and cable idents are fitted correctly
checkpoint | Check earth cable mechanical protection is installed
checkpoint | Location of earth rod as per the location drawing
checkpoint | Check any metal doors and louvres are bonded to earth correctly
checkpoint | Earth pit installed properly according to finish ground level without any damages and connection facilities are installed
checkpoint | Earth pit tagging complete and is as-per the drawings
checkpoint | If the site is a hot site (EPR > 430V), check that the HV/LB earthing systems are fully segregated (HV/LV earth link removed in the LV Pillar)
checkpoint | Check the earthing system of the EV charger is as per the approved design.
section | Earthing System Test
checkpoint | Test certificate to be provided with a detailed SOW and test results
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Metering
section | DNO Cutout and Metering
checkpoint | Check that the metering unit matches the approved design
checkpoint | check sufficient space is available between the meter and incoming cutout
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - Lighting and Small Power
section | Lighting Columns
checkpoint | Verify the number as-per the drawing
checkpoint | Provide lighting cable test results
checkpoint | Check lighting operation
checkpoint | Check lux level of lighting meets design requirements
section | Power supply for Comsat unit
checkpoint | Verify the install is per the agreed design
checkpoint | Provide test results for the small power installation (separate test sheet)
checklist | Electrical checklist - EV Charger
section | EV Charger
checkpoint | Check the charger is free of any damage
checkpoint | Check the internal arts are free of any damages
checkpoint | Check the unit s correctly located as-per layout drawing
checkpoint | Check the unit is installed correctly and is level
checkpoint | Check the charger rating matches the purchase order
checkpoint | Check the type of sockets match the purchase order
checkpoint | Check the payment terminal matches the purchase order
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Electrical checklist - FO Install
section | FO Equipment
checkpoint | Verify the install is per the agreed design
checkpoint | Provide test results for the FO cable and associated equipment (separate test sheet)
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist-flat | Certificate of compliance (COC)
checkpoint | Please upload Certificate of Compliance here when complete (COC)
checklist-flat | Record of Inspection (ROI)
checkpoint | Please upload Record of Inspection here when complete (ROI)
checklist | Telecom DMC Checklist
section | LV Pillar Transceivers
checkpoint | Confirm the emergeny stop details match confirmed design
checkpoint | Confirm emergency stop transciever and shop closer modules match design
checkpoint | Confirm emergency stop is mointed and installed correctly
checkpoint | Check the shop closure transceiver is mounted and has been installed correctly
checkpoint | Check that the protection settings for the protective devices match approved design
checkpoint | Check the protective device(s) ratings match the approved design
checkpoint | Check all equipment carries the correct circuit identification
checkpoint | Check that the fibre optic cables are fitted with the correct plug connectors.
checkpoint | Check that the fibre optic cables are terminated correctly to transciever devices
checkpoint | Check the fibre optic cables are glanded correctly.
checkpoint | Check that the commissioning/lest records for the transceivers are available on site.
checkpoint | Check that the transceivers are earthed correctly
section | Transceivers in shop
checkpoint | Check that the transceiver enclosure is mounted to design requirements
checkpoint | Confirm the E-stop Comnet transceiver and shop closure transceiver model matches design
checkpoint | Confirm the emergency stop Comnet transceiver and shop closure transceiver module selection match the design
checkpoint | Confirm the E-stop Comnet transceiver and shop closure transceiver model matches design
checkpoint | Check all equipment carries the correct circuit identification
checkpoint | Check that the fibre optic cables are fitted with the correct plug connectors.
checkpoint | Check that the fibre optic cables are terminated correctly to transciever devices
checkpoint | Check the fibre optic cables are glanded correctly.
checkpoint | Check that the commissioning/test records for the trancievers are avilable on site
checkpoint | Check that the transceivers are earthed correctly
section | cables
checkpoint | check cables are right type and size as per design
checkpoint | Check that the cable ends have been correctly capped
checkpoint | Check that the cable test records are available on-site.
section | Cable Entry Points/Cable Containment
checkpoint | Check all cable entries are correct to design
checkpoint | If installed at high level, check that the cables are installed correctly on tray
section | CCTV network
checkpoint | Check that the CCTV hardware model and spec matches designs
checkpoint | Check that the wiring of the CCTV network matches the design
checkpoint | Check that the wiring is terminated correctly at the transceiver module
checkpoint | Check that the wiring is glanded correctly.
checkpoint | Check that all the commissioning documents are present on site
signoff | Acceptance signatures: Subcontractor/Global Contractor/BP
checklist | Mud Map
checkpoint | Please upload scan of Mud Map
checklist | SSSP - Site Specific Safety Plan
checkpoint | Please upload scan of SSSP
checklist | Underground services locator report
checkpoint | Please upload underground services locator report
checklist | Ground Disturbance Certificate
checkpoint | Please upload Ground Disturbance Report
checklist | Safety Audit
checkpoint | Please upload independent safety auditors report
checkpoint | Please upload Entec internal safety audit report
checklist | Dial Before You Dig
checkpoint | Please upload relevant Before You Dig information