## Foundations
INSPECTION & TEST PLAN
|  | Contract Name: | [6 empty] | Rev: | Originator | Date | Approved | Date
|  | TE MIHI POWER STATION |  |  | Hold Point (H) | Verify (V) |  |  | 0 | Carlos | 2024-07-25
ITP - 003 Concrete Foundations |  |  |  |  | Submit (S) | Review (R) |  |  | 1
[5 empty] | Approve(A) | Witness (W)
Surveillance (SU)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA | UCCL Signature | Client Signature | UCCL | Client | DATE | COMMENTS
Materials
Concrete Mix Design | Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 5.1.4 | Test certificates | UCCL, WCL | Each Mix Design used prior to use | Cement shall be ordinary Portland Cement, complying with NZS 3122. All aggregates shall comply with NZS 3121, is not derived from Andesite rock and does not exceed 20mm. Chloride content shall not exceed 0.8kg/m3 as per NZS3109. Mix designs shall comply with the table located on page 37 of the specification |  |  | H | R
Reinforcement | Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 6.1.7 | Test Certificates | UCCL, WCL | Prior to manufacturing of reinforcing | Reinforcement shall be hot rolled steel bars, Class E complying with AS/NZS 4671 . Reinforcing shall be manufactured by micro alloy techniques. Reinforcing shall be indentified along its length with its strength grades, ductility class, steel producer and method of manufacture. |  |  | H | R
Cast in Items - Nuts, Bolts and Studs | Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 16.2.4 | Supplier Documentation | UCCL | Prior to Ordering | Bolts, Nuts and Washers shall comply with NZS3404. All bolts, Nuts and wahsers shall be hot dip galvanised complying with AS 1214. |  |  | H | R
Pre Construction Site works
Trim Subgrade | THIG-MTL-S-000-STR-SPC-0001_0_StructuralSpec | Survey | UCCL | Prior to placing site concrete | Subgrade to be trimmed within +10/-50mm of the bottom of site concrete level. |  |  | V | Su
Site Concrete |  | Survey | UCCL | Each Foundation | Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm |  |  | V | Su
Setout |  | Survey | UCCL | Each Foundation | Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing. |  |  | V | Su
Prepour Inspection
Pre pour inspection |  | Pre pour inspection sheet | UCCL | Prior to placing structural concrete | Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete. |  |  | H | W
Postpour Inspection
Post pour inspection |  | Post pour inspection sheet | UCCL | Following placement of concrete | Post pour inspection sheet to be completed following each pour. |  |  | A | Su
Post Construction
As Built & Final Design Documentation |  | Surveying | UCCL | For Each Foundation | Confirmation From Engineer on as built records & redline mark ups |  |  | H | R
Completion Inspection inc. Construction Defects Report |  | Completion inspection on each foundation by CEL | CEL/ UCCL | For Each Foundation | Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out |  |  | H | R