## Piling
INSPECTION & TEST PLAN
|  | Contract Name: | [5 empty] | Rev: | Originator | Date | Approved | Date
|  | TE MIHI POWER STATION |  |  | Hold Point (H) | Verify (V) |  | 0 | Carlos Manuel | 2024-07-17
ITP No: 002 PILING |  |  |  |  | Submit (S) | Review (R)
Approve(A)
TASK | SPECIFICATION REFERENCE | TEST REQUIRED | INSPECTION BY | TASK TIMING OR TASK FREQUENCY | ACCEPTANCE CRITERIA |  | UCCL | Client | DATE | COMMENTS
Preliminary
Acceptable Method Statement | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes |  |  | Once Prior to commencement of piling | Approved Method statement document |  | H | R/A
Concrete Design Mix Verification | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes |  |  | Once Prior to commencement of piling | Approved by Engineer |  | H | R/A
Supply of Reinforcement - Steel reinforcement compliance records | THIG-MTL-S-000-STR-SPC-0001_0_StructuralSpec | Schedules shall be prepared by the supplier and reviewed | Engineer | Prior to manufacturing any reinforcement | Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet |  | H | R
Pile Boring
Pile Location | THIG-WOR-S-00-STR-DET- IFC Drawings | Survey record | Surveyor | Every Pile | Hz +/-75mm Vt +/- 25mm |  | H/V | R
Drill Tool Diameter | Visual | Pile Card | UCCL | Start of project | Design |  | H | R
Verticality | THIG-WOR-S-00-STR-DET-0008 IFC Drawings | Pile Card | UCCL | As per QAC requirements | Vertical alignment <1:75 from design |  | R | R
Casing Inspection |  | Pile Card | UCCL | Start of project | Visual |  | H | R
Bore size | THIG-WOR-S-00-STR-DET-0008 IFC Drawings | Pile Card | UCCL |  | ≥ specified diameter |  | H | R
Pre pour Inspection Check
Required depth reached | THIG-WOR-S-00-STR-DET-0008 IFC Drawings | Visual Inspection | UCCL | Every Pile | Weighted tape |  | H | W
Clean with no unsuitable material | THIG-WOR-S-00-STR-DET-0008 IFC Drawings | Visual inspection | UCCL | Every Pile | Weighted tape |  | H | H
Reinforcement Cage inspection | THIG-WOR-S-00-STR-DET-0008 IFC Drawings | Visual/ Delivery Docket | UCCL | Every pile | Confirm Pile cage Type 1 or 2 is used in correct location per design drawings |  | H | W
Concrete Placement
Verify Concrete Mix | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Concrete Docket | UCCL | Each delivery | Approved Mix Design - 40MPa |  | H | W
Concrete level | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Pile Card | UCCL | Every Pile, United Civil at commencement of project on the first pile/piles | Projection into pile cap to be +75mm |  | H | W
Concrete pouring | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Pile Card | UCCL | Every Pile, United Civil at commencement of project on the first pile/piles | Concrete pump or Truck Chute |  |  | R
Compressive Strength Sampling | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Lab.Test Record | BATCH PLANT | Undertaken at Batch plant | 28 day - 40MPa |  | R | R
| THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Lab. Test Record | BATCH PLANT | Undertaken at Batch plant | 28 Day - 40MPa |  | H | R
Slump/spread test | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Pile Card | BATCH PLANT | Undertaken at Batch plant | TBC |  | H | R
Concrete Finish | THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes | Pile Card | UCCL | Following Pile concrete pour | Apply surface retarder, pressure blast to 'Type B' CJ (Following day). |  | H | R
Post-Construction Testing
Pile Dynamic Analysis | N/A |  |  | TBC
Pile Integrity Testing | N/A |  |  | TBC
Post Construction
As Built & Final Design Documentation |  | Surveying | UCCL | For each Pour | Confirmation From Engineer on as built records & redline mark ups |  |  | R
Completion Inspection inc. Construction Defects Report |  | Completion inspection on the structure by CEL | CEL/ UCCL | For each structure | Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out