## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-003 - Concrete Foundations | itp |  |  |  |  | ITP-003 - Concrete Foundations
section | Materials
checkpoint | Concrete Mix Design
label | SPECIFICATION REFERENCE - Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 5.1.4
label | TEST REQUIRED - Test certificates
label | INSPECTION BY - UCCL, WCL
label | TASK TIMING OR TASK FREQUENCY - Each Mix Design used prior to use
label | ACCEPTANCE CRITERIA - Cement shall be ordinary Portland Cement, complying with NZS 3122. All aggregates shall comply with NZS 3121, is not derived from Andesite rock and does not exceed 20mm. Chloride content shall not exceed 0.8kg/m3 as per NZS3109. Mix designs shall comply with the table located on page 37 of the specification
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Reinforcement
label | SPECIFICATION REFERENCE - Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 6.1.7
label | TEST REQUIRED - Test Certificates
label | INSPECTION BY - UCCL, WCL
label | TASK TIMING OR TASK FREQUENCY - Prior to manufacturing of reinforcing
label | ACCEPTANCE CRITERIA - Reinforcement shall be hot rolled steel bars, Class E complying with AS/NZS 4671 . Reinforcing shall be manufactured by micro alloy techniques. Reinforcing shall be indentified along its length with its strength grades, ductility class, steel producer and method of manufacture.
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Cast in Items - Nuts, Bolts and Studs
label | SPECIFICATION REFERENCE - Geofuture Te Mihi Unit 3 Steamfield. Structural Specifications - 16.2.4
label | TEST REQUIRED - Supplier Documentation
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to Ordering
label | ACCEPTANCE CRITERIA - Bolts, Nuts and Washers shall comply with NZS3404. All bolts, Nuts and wahsers shall be hot dip galvanised complying with AS 1214.
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
section | Pre Construction Site works
checkpoint | Trim Subgrade
label | SPECIFICATION REFERENCE - THIG-MTL-S-000-STR-SPC-0001_0_StructuralSpec
label | TEST REQUIRED - Survey
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing site concrete
label | ACCEPTANCE CRITERIA - Subgrade to be trimmed within +10/-50mm of the bottom of site concrete level.
label | UCCL - V
label | CLIENT - Su
checkpoint | Site Concrete
label | TEST REQUIRED - Survey
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | UCCL - V
label | CLIENT - Su
checkpoint | Setout
label | TEST REQUIRED - Survey
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each Foundation
label | ACCEPTANCE CRITERIA - Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing.
label | UCCL - V
label | CLIENT - Su
section | Prepour Inspection
checkpoint | Pre pour inspection
label | TEST REQUIRED - Pre pour inspection sheet
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Prior to placing structural concrete
label | ACCEPTANCE CRITERIA - Pre pour inspection sheet to be completed prior to placing concrete. WCL to be notified of pours for inspection at least 24 hours prior to placing concrete.
label | UCCL - H
label | CLIENT - W
holdpoint | AUTHORITY HOLDPOINT
section | Postpour Inspection
checkpoint | Post pour inspection
label | TEST REQUIRED - Post pour inspection sheet
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following placement of concrete
label | ACCEPTANCE CRITERIA - Post pour inspection sheet to be completed following each pour.
label | UCCL - A
label | CLIENT - Su
section | Post Construction
checkpoint | As Built & Final Design Documentation
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - For Each Foundation
label | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Completion Inspection inc. Construction Defects Report
label | TEST REQUIRED - Completion inspection on each foundation by CEL
label | INSPECTION BY - CEL/UCCL
label | TASK TIMING OR TASK FREQUENCY - For Each Foundation
label | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checklist | ITP-002 - Piling | itp |  |  |  |  | ITP-002 - Piling
section | Preliminary
checkpoint | Acceptable Method Statement
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TASK TIMING OR TASK FREQUENCY - Once Prior to commencement of piling
label | ACCEPTANCE CRITERIA - Approved Method statement document
label | UCCL - H
label | CLIENT - R/A
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Concrete Design Mix Verification
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TASK TIMING OR TASK FREQUENCY - Once Prior to commencement of piling
label | ACCEPTANCE CRITERIA - Approved by Engineer
label | UCCL - H
label | CLIENT - R/A
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Supply of Reinforcement - Steel reinforcement compliance records
label | SPECIFICATION REFERENCE - THIG-MTL-S-000-STR-SPC-0001_0_StructuralSpec
label | TEST REQUIRED - Schedules shall be prepared by the supplier and reviewed
label | INSPECTION BY - Engineer
label | TASK TIMING OR TASK FREQUENCY - Prior to manufacturing any reinforcement
label | ACCEPTANCE CRITERIA - Manufacturer´s Mill Certificate/Rebar schedule/Rebar summary sheet
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
section | Pile Boring
checkpoint | Pile Location
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET- IFC Drawings
label | TEST REQUIRED - Survey record
label | INSPECTION BY - Surveyor
label | TASK TIMING OR TASK FREQUENCY - Every Pile
label | ACCEPTANCE CRITERIA - Hz +/-75mm Vt +/- 25mm
label | UCCL - H/V
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Drill Tool Diameter
label | SPECIFICATION REFERENCE - Visual
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Start of project
label | ACCEPTANCE CRITERIA - Design
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Verticality
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET-0008 IFC Drawings
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - As per QAC requirements
label | ACCEPTANCE CRITERIA - Vertical alignment <1:75 from design
label | UCCL - R
label | CLIENT - R
checkpoint | Casing Inspection
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Start of project
label | ACCEPTANCE CRITERIA - Visual
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Bore size
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET-0008 IFC Drawings
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | ACCEPTANCE CRITERIA - ≥ specified diameter
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
section | Pre pour Inspection Check
checkpoint | Required depth reached
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET-0008 IFC Drawings
label | TEST REQUIRED - Visual Inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Every Pile
label | ACCEPTANCE CRITERIA - Weighted tape
label | UCCL - H
label | CLIENT - W
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Clean with no unsuitable material
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET-0008 IFC Drawings
label | TEST REQUIRED - Visual inspection
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Every Pile
label | ACCEPTANCE CRITERIA - Weighted tape
label | UCCL - H
label | CLIENT - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Reinforcement Cage inspection
label | SPECIFICATION REFERENCE - THIG-WOR-S-00-STR-DET-0008 IFC Drawings
label | TEST REQUIRED - Visual/ Delivery Docket
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Every pile
label | ACCEPTANCE CRITERIA - Confirm Pile cage Type 1 or 2 is used in correct location per design drawings
label | UCCL - H
label | CLIENT - W
holdpoint | AUTHORITY HOLDPOINT
section | Concrete Placement
checkpoint | Verify Concrete Mix
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Concrete Docket
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Each delivery
label | ACCEPTANCE CRITERIA - Approved Mix Design - 40MPa
label | UCCL - H
label | CLIENT - W
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Concrete level
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Every Pile, United Civil at commencement of project on the first pile/piles
label | ACCEPTANCE CRITERIA - Projection into pile cap to be +75mm
label | UCCL - H
label | CLIENT - W
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Concrete pouring
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Every Pile, United Civil at commencement of project on the first pile/piles
label | ACCEPTANCE CRITERIA - Concrete pump or Truck Chute
label | CLIENT - R
checkpoint | Compressive Strength Sampling (1)
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Lab.Test Record
label | INSPECTION BY - BATCH PLANT
label | TASK TIMING OR TASK FREQUENCY - Undertaken at Batch plant
label | ACCEPTANCE CRITERIA - 28 day - 40MPa
label | UCCL - R
label | CLIENT - R
checkpoint | Compressive Strength Sampling (2)
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Lab. Test Record
label | INSPECTION BY - BATCH PLANT
label | TASK TIMING OR TASK FREQUENCY - Undertaken at Batch plant
label | ACCEPTANCE CRITERIA - 28 Day - 40MPa
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Slump/spread test
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - BATCH PLANT
label | TASK TIMING OR TASK FREQUENCY - Undertaken at Batch plant
label | ACCEPTANCE CRITERIA - TBC
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
checkpoint | Concrete Finish
label | SPECIFICATION REFERENCE - THIG-WOR-S-000-STR-DET-0001_A_Tie-Ins Standard Details General Civil Notes
label | TEST REQUIRED - Pile Card
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - Following Pile concrete pour
label | ACCEPTANCE CRITERIA - Apply surface retarder, pressure blast to 'Type B' CJ (Following day).
label | UCCL - H
label | CLIENT - R
holdpoint | AUTHORITY HOLDPOINT
section | Post-Construction Testing
checkpoint | Pile Dynamic Analysis
label | SPECIFICATION REFERENCE - N/A
label | TASK TIMING OR TASK FREQUENCY - TBC
checkpoint | Pile Integrity Testing
label | SPECIFICATION REFERENCE - N/A
label | TASK TIMING OR TASK FREQUENCY - TBC
section | Post Construction
checkpoint | As Built & Final Design Documentation
label | TEST REQUIRED - Surveying
label | INSPECTION BY - UCCL
label | TASK TIMING OR TASK FREQUENCY - For each Pour
label | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | CLIENT - R
checkpoint | Completion Inspection inc. Construction Defects Report
label | TEST REQUIRED - Completion inspection on the structure by CEL
label | INSPECTION BY - CEL/UCCL
label | TASK TIMING OR TASK FREQUENCY - For each structure
label | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measure taken, snag lists closed out