## PROJECT STRUCTURE
Folder Structure |  |  |  | Checklists
FLAT BUSH SCHOOL | TAMAKI HEALTH | PROJECT:TLA
INTERIOR FITOUT
ISOLATION
|  |  | ELECTRICAL ISOLATION | ISOLATION AND DISCONNECTION
|  | ELECTRICAL AND DATA | ELECTRICAL AND DATA | 1ST FIX
2ND FIX
DISTRIBUTION
|  |  | DISTRIBUTION BOARD DB1 | DISTRIBUTION BOARD
COMMISSIONING
|  |  | COMMISSIONING - SWITCHBOARD MSB | COMMISSIONING - DISTRIBUTION BOARD
|  |  | DATA | COMMS CABINET

## CHECKPOINTS
TYPE | NAME
CHECKLIST | ISOLATION AND DISCONNECTION
CHECKPOINT | SAFELY ISOLATE AND LOCK OUT ALL CIRCUITS BEING WORKED ON
CHECKPOINT | REMOVAL OF EXISTING LIGHTING WHERE REQUIRED
CHECKPOINT | REMOVAL OF EXISTING POWER WHERE REQUIRED
CHECKPOINT | CHECK EXISTING CABLING FOR COMPLIANCE
CHECKPOINT | REMOVE ALL REDUNDNANT AND NON COMPLIANT CABLING
CHECKLIST | 1ST FIX OFFICE
CHECKLIST | SETTING OUT
CHECKPOINT | INSTALLATION OF CATENARY WIRES
CHECKPOINT | VOLT DROP CALCULATIONS WORKED OUT PRIOR TO COMMENCEMENT OF CABLING
CHECKPOINT | LIGHTING CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | LIGHTING CONTROL CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | EMERGENCY LIGHTING CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | POWER CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | BONDING CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | DATA CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | AV CABLING INSTALLED AND LABELLED AS PER PLANS
CHECKPOINT | DATA CABLES ARE RUN ON A SEPARATE CAT WIRE, VELCRO TIED IN 24 DATA CABLES PER BUNDLE
CHECKPOINT | FLUSH BOXES MOUNTED AS PER ARCHITECTURAL ELEVATION
CHECKPOINT | FLUSH BOXES FOR ISOLATORS INSTALLED ABOVE BENCH OR AT ACCESSIABLE LOCATION TO APPLIANCE
CHECKPOINT | FEED AND SWITCH WIRES INSTALLED AND CONFIMRED FOR LIGHTING
CHECKPOINT | FIRE RATED FLUSH BOXES INSTALLED WHERE APPLICABLE
CHECKPOINT | ACCOUSTIC BOXES INSTALLED WHERE APPLICABLE
CHECKPOINT | DEEP MOUNTING BLOCKS INSTALLED ON TRUNKING FOR COMPLIANCE WITH DATA WARRANTY
CHECKPOINT | HOTWATER CABLE INSTALLED AND LOCATION CONFIMRED WITH PLUMBER
CHECKPOINT | APPLIANCE ISOLATORS INSTALLED A/B OR AT ACCESSIBLE LOCATION
CHECKPOINT | SWITCH LOCATIONS CONFIRMED AND IS ACCESSIABLE UPON ENTRY TO ROOM
CHECKPOINT | ALL CABLES ARE CABLE TIED NEATLY ON CATENARY WIRES AND MEETS SPECIFICATION
CHECKPOINT | FEATURE LIGHTING NOG MARKED AND INSTALLED
CHECKPOINT | FLOORBOXES MARKED AND PENETRATIONS COMPLETE
CHECKPOINT | BOOK DATA WARRANTY SITE VISIT
CHECKLIST | 2ND FIX
CHECKPOINT | LIGHT SWITCHES INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | LCP PANEL IS FITTED OFF AND LIGHTS ARE SWITCHING CORRECTLY.
CHECKPOINT | SENSORS INSTALLED
CHECKPOINT | DALI REALYS INSTALLED
CHECKPOINT | DALI POWER SUPPLIES INSTALLED
CHECKPOINT | ALL DALI CONNECTION COMPLETE
CHECKPOINT | SURFACE SOCKETS FITTED OFF FOR PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS
CHECKPOINT | SURFACE SOCKETS ARE LABELLED TO ALLOCATED CIRCUITS CORRECTLY
CHECKPOINT | PAN FITTINGS, DOWNLIGHTS AND EMERGENCY LIGHTS ARE INSTALLED IN CORRECT LOCATIONS.
CHECKPOINT | EMERGENCY LIGHTS INSTALLED, LABELLED, LIVE AND WORKING CORRECTLY.
CHECKPOINT | FEATURE LIGHTS INSTALLED SECURLY SUSPENDED OR SURFACE MOUNT ONTO PLY BEHINF CEILING GRID
CHECKPOINT | POWER OUTLETS INSTALLED, LEVELLED, LABELLED AND LIVE
CHECKPOINT | ISOLATION SWITCHES INSTALLED LEVELLED, LABELLED AND LIVE
CHECKPOINT | APPLIANCES CONNECTED
CHECKPOINT | DATA OUTLETS INSTALLED, LEVELLED, LABELLED AND TESTED.
CHECKPOINT | TRUNKING INSTALLED PLUMMBED AND LEVEL TO MOUNTING BLOCK FOR OUTLETS WHERE REUIRED.
CHECKPOINT | CEILING GRID/SINKS/ BUILDING STRUCTURE IS BONDED AND TEST RESULTS < 0.5 OHMS TO DB
CHECKPOINT | INSTALLATION OF FLOOR BOXES
CHECKLIST | DISTRIBUTION BOARD
CHECKPOINT | CABLE TRAY/TRUNKING INSTALLED ABOVE DB FOR SUB CIRCUITS AND NEW SUB MAINS.
CHECKPOINT | SUB CIRCUITS TIED AND DRESSSED NEATLY ON CAT WIRE/CABLE TRAY/TRUNKING
CHECKPOINT | SUBCIRCUITS TERMINATED INCLUDING LABELLING/FERRULES TO ALL CORES
CHECKPOINT | EARTHING/BONDING TERMINATED
CHECKPOINT | STRUCTURAL BONDING CABLE TERMINATED AT SWITCHBOARD.
CHECKPOINT | DB SCHEDULE COMPLETED
CHECKPOINT | DISTRIBUTION BOARD TEST SHEET COMPLETED
CHECKPOINT | DB SCHEDULE INSTALLED
CHECKPOINT | CLEAN OF ALL DEBRI AND MARKS
CHECKLIST | COMMISSIONING - DISTRIBUTION BOARD
CHECKPOINT | SWITCHBOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DB SCHEDULE COMPLETED, INSTALLED INTO DB AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | DISTRIBUTION BOARD CHECK SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EARTHING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | TIMECLOCK TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | BOARD FREE FROM DEBRI, NO MARKS, ALL ACCESSORIES INSTALLED
CHECKPOINT | LABELLING COMPLETED ON ALL FIELD OUTLETS, SWITCHES AND ISOLATORS ETC
CHECKPOINT | EMERGENCY LIGHTING TEST SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | SUBCIRCUIT COMMISSIONING RESULTS SHEET COMPLETED AND ADDED TO DROPBOX
CHECKPOINT | TEST - CONTINUITY OF CIRCUIT PROTECTIVE CONDUCTOR
CHECKPOINT | TEST - CONTINUIT OF BONDING
CHECKPOINT | TEST - INSULATION RESISTANCE
CHECKPOINT | TEST - POLARITY
CHECKPOINT | TEST - EARTH FAULT LOOP IMPEDANCE
CHECKPOINT | TEST - PFC
CHECKPOINT | TEST - RCD
CHECKLIST | COMMS CABINET
CHECKPOINT | COMMS CABINET MOUNTED AT AGREED LOCATION
CHECKPOINT | ALL DATA OUTLETS ARE FITTED OFF AND LABELLED.
CHECKPOINT | ALL CAT6A CABLES TERMINATED INTO PATCH PANEL
CHECKPOINT | ALL CAT6A CABLES ARE TESTED AND LABELLED CORRECTLY
CHECKPOINT | FRONT OF PATCH PANELS ARE LABELLED CORRECTLY TO FIELD OUTELTS AND CONFIRMED
CHECKPOINT | BOOK WARRANTY INSPECTION