## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
612ebf96-b2b9-4e49-a615-8a1d4645b1bf | checklist | EFPQF03 - Wet Pipe Sprinkler Install |  | EFPQF03 - Wet Pipe Sprinkler Install
c0826ba6-ffb7-4082-9204-682c72d5651e | section | Documentation
c5be5a33-9beb-4032-afd3-c8b7a9a10282 | checkpoint | Confirm correct construction drawings approved for use.
3032fe9e-3e4f-4a31-a20e-073567ca1772 | section | Incoming Inspection
5ffbbb0d-c07e-4cdb-9327-07f4bf90204f | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
e36a8f12-9787-5ee7-a11d-bbbbfe843e01 | tickbox | Fabricated pipework.
b263ab8c-3e60-5022-ad5d-db5d6a2b46fa | tickbox | Fittings.
061ff252-8eaf-58f8-b005-8d127132897e | tickbox | Hangers.
28fc77fc-f0a9-5c1b-92ef-729cab22f4cf | tickbox | Sprinklers.
5e96dd45-4831-568c-99ba-e2b667dc373c | tickbox | Valves.
dc7e9f29-d897-4711-b0af-c9f1ea0cce07 | section | Installation Rough In / Fit Off
8ee915de-c5d0-4332-9b34-29e73565c077 | checkpoint | Confirm hanger spacing.
a2b8291d-8809-531d-878f-9f8b4964c56f | note | 25mm - max 4m spacing.
5e438ede-0789-56d3-a77f-71dcfe43ddd0 | note | 32 – 100mm - max 5m spacing.
2c9fb0e3-f526-5cea-96ad-558de7bf3396 | note | ≥ 150mm - max 6m spacing.
7866570c-f405-430d-9db7-e85687e726e8 | checkpoint | Confirm support at change of direction at 1m max.
ec89ec4f-d93b-4a21-9e59-bd30dd6b8495 | checkpoint | Confirm support of pipework no more than 1m from end.
7161fd6e-ddd6-4089-bfec-21d115ba59ea | checkpoint | Confirm support of armpiece exceeding 500mm.
caa3aaea-ed20-44a9-924b-89b8424bcf5e | checkpoint | Confirm first support of range pipe within 2m of mains.
ce9cc500-4a51-4fed-a40f-0f0bb897d1d9 | checkpoint | Confirm pipework installed as per drawing.
36ea3974-0028-4c09-9af2-90b682d2cacc | checkpoint | Confirm sprinklers installed/Fit Off
db338dad-6b37-46a6-afdf-dbeb6856d1db | checkpoint | Confirm sprinkler guards installed.
ffac3c8f-89c6-431b-8dd0-3600b3fdbb98 | section | Pressure Testing
62d2d1a3-b5c3-47e6-8ae7-51498648fdd4 | checkpoint | Confirm all open ends plugged.
752bf445-d3f6-446d-ade7-3525e7fbb95a | checkpoint | Confirm isolation and drain valves are closed.
ffd8e062-157b-40c4-a3c9-d9ad379c75ad | checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
0aee12fc-553f-4dc7-8238-7f8270c8ae36 | checkpoint | Record pressure test results on Pressure Test Form.
b151fd97-076c-47e6-90b6-3e375717c619 | section | Pressure Test Report Sheet
bab64755-517e-49e5-aeb1-066e596392d6 | checkpoint | Test Details & Results
a9a67229-9154-5460-a46a-e56465b37fb8 | textbox | Test number
4aed9f64-000e-5576-8735-812df626a1b6 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
8476b282-ba65-58c4-b84d-29495e11915e | textbox | Start Date
708cf71a-0dd3-5773-9172-29a1a0590ac7 | textbox | Start Time
acae8c76-b69b-5518-8c1f-243436218656 | textbox | Start Pressure
9fb4aedc-f173-58e2-9f20-b4188afe1a57 | textbox | Finish Time
b265e5fc-9b41-5296-9fa2-aa1f63d5b4c0 | textbox | Finish Pressure
b22612fb-ad91-5aa1-b67e-bebee49650b3 | textbox | Gauge Reference
42810cd8-6dbc-48aa-87e7-60e381cf7359 | checkpoint | Test completed to specification/drawings & Area left clean/tidy
281c82f9-a1cb-593e-b5f1-844ff54c2439 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
235745ed-5077-4c50-9e04-69eae6ff6102 | checkpoint | Entire Fire Sign-Off (attach signature)
ac9844bd-5054-4565-b432-48c14a90e16c | checklist | EFPQF04 - Wet Pipe Sprinkler Control Valve |  | EFPQF04 - Wet Pipe Sprinkler Control Valve
65852163-0b30-4880-ad45-f04952c45901 | section | Documentation
6ef35839-a19f-4345-8154-549cabdd6792 | checkpoint | Confirm correct construction drawings approved for use.
ceedd3c7-27d8-46d4-b0a6-9f5670be4a66 | section | Incoming Inspection
a8743cb0-212f-4524-8cc7-84c897242e6f | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
17ea7014-524d-51a4-95c5-9403653bf20e | tickbox | Isolation valves.
7ec8be23-bdba-5e79-9cc4-7e3102695bc4 | tickbox | Alarm valves.
b6b6de42-4045-51b0-a972-13e68373fe9f | tickbox | Pressure switches.
594b31bc-e6d6-54ed-b75d-a94cf31ce8fb | tickbox | Jacking pump
fb416ea1-9e40-44a2-a825-ea7d6c5421b7 | section | Installation
82dec096-99f7-4dd7-a30f-3d0e3bcc51b3 | checkpoint | Main stop valve installed
fed7d342-53fd-4d1d-a900-dd58c4d0fa1e | checkpoint | Alarm valve installed
17c9a524-1a5c-4ebd-b62a-a3e751835323 | checkpoint | Drain valve installed
11cb99a3-24d4-4e60-b71c-22db039b9563 | checkpoint | Alarm pressure switches installed
7f6a7003-e89f-41d4-a62e-8839a339023e | checkpoint | Water motor alarm installed
16a3954a-d4f7-47a2-ad03-877078dfdec0 | checkpoint | Pressure gauges installed
9575f435-42fc-4121-aeeb-cecb18283f9f | checkpoint | Jacking pump installed
05f44d31-5e07-4718-9473-8e630e03f12e | section | Sign-Off
8d3aae1c-4822-4756-b90e-aa55195f7c91 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
d4419294-9398-49db-88f6-cc23f5d1e2a3 | checklist | EFPQF05 - Pre Action - Sprinkler |  | EFPQF05 - Pre Action - Sprinkler
3007b120-5684-4bbd-b122-f169b1a8d6b2 | section | Documentation
adbbc248-fd12-4ae4-967d-403d1ef09800 | checkpoint | Confirm correct construction drawings approved for use.
abd3c6ef-d551-44f1-9be2-60a83ce85aa5 | section | Incoming Inspection
2cf40c2e-2e82-4dd5-800b-7a7ce4c282f2 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
46bf603b-4c10-5542-aaf4-201d38319caf | tickbox | Fabricated pipework - All pipe galvanised.
858961e9-42a3-559c-b9c8-9bc05ffec407 | tickbox | Fittings - All fittings galvanised.
522628e0-44ee-5b19-a883-1c059fef7bc2 | tickbox | Hangers - All hangers galvanised.
3b6bd716-54e4-5be1-a814-428b7500bbc5 | tickbox | Sprinklers.
4d7aec57-97a3-5968-bb7b-5f9de034490a | tickbox | Valves.
690ab3a7-ea3c-4e09-aaa4-ce71e621b452 | section | Installation Rough In / Fit Off
1b610228-13bb-467f-9ff6-36017b7b4b59 | checkpoint | Confirm hanger spacing
4f76e003-e621-5f9b-bb2b-0b643d509f35 | note | 25mm - max 4m spacing.
eb26df27-5284-5fd5-94f3-56682acccc1a | note | 32 – 100mm - max 5m spacing.
b36d2e57-dc37-514a-aca7-cf0a9d7f9619 | note | ≥ 150mm - max 6m spacing.
d0dbbaf3-8997-45a2-b45a-ee8b6be7f5a3 | checkpoint | Confirm support at change of direction at 1m max.
bf541788-02dc-441c-a694-ea6cc1af8644 | checkpoint | Confirm support of pipework no more than 1m from end.
b2e7ec09-a03f-412b-919d-316c8faca058 | checkpoint | Confirm support of armpiece exceeding 500mm.
97f69135-0cfb-4c06-b417-853a9ef9f2a0 | checkpoint | Confirm first support of range pipe within 2m of mains.
136f2ec2-38f7-4528-8b21-e66f3165093f | checkpoint | Confirm pipework installed as per drawing.
7ba5b7d5-fb58-499e-8fe9-c3ada6b6aec7 | checkpoint | Confirm pipework installed fall back to drain
2f29c49f-9fbd-4754-96db-5dd24ab32a72 | checkpoint | Mains minimum 2mm per 1m.
8026e174-b5a6-4503-b326-8ca81212ca3f | checkpoint | Ranges minimum 4mm per 1m.
ffe9b246-7e89-4601-9421-7e71f1d7bd92 | checkpoint | Confirm sprinklers installed.
368a3cc4-6966-4257-917b-457f03b12c3c | checkpoint | Confirm sprinkler guards installed.
b3199f23-6668-46e4-a363-d7cd28fb6ab8 | section | Pressure Testing
23c4733a-9086-484e-909b-13e061bcaa1a | checkpoint | Confirm all open ends plugged.
2bda3cbd-e824-45ba-88f2-1324bce2bc7e | checkpoint | Confirm isolation and drain valves are closed.
88c0b0e3-c607-498b-8e9a-98ca0b39d0b9 | checkpoint | Fill pipework with air to 50kpa to confirm no open ends.
3c73c024-67d6-47d4-85ae-fd1723ffd24e | checkpoint | Fill pipework with water to 1600kpa. Hold 2 hours. No pressure loss permitted.
e3706cf9-ade5-40f5-bebd-86d17596286c | checkpoint | Fill pipework with air to 300kpa. Hold for 30 minutes. Pressure loss of 10% (60kpa) permitted.
8d86c965-5c48-49a2-9e83-eddb48441d16 | checkpoint | Record pressure test results on Pressure Test Form.
df1d7d4b-f799-49b5-94ba-3f4c4eacc204 | section | Pressure Test Report Sheet
98c3f7e4-145a-426e-9221-129154df4644 | checkpoint | Test Details & Results
2c9b5cc0-445b-5d05-88e7-d50066c8356b | textbox | Test number
693b79bd-2ef3-53d4-9c13-445693de0133 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
85f34997-21a7-5d7b-89d3-4827e437737f | textbox | Start Date
ef247145-2f12-53e6-98ee-bd642166054b | textbox | Start Time
51941312-a0f7-5d7a-9605-248ef4c383cb | textbox | Start Pressure
d578d386-ad19-5077-90e4-87a4cf276fec | textbox | Finish Time
20d687fa-08fc-5656-9aa8-976ceea43b46 | textbox | Finish Pressure
71e00f93-0fae-5b97-9dc1-3af2b00cd1c1 | textbox | Gauge Reference
6f8ff135-fdb9-4fbd-a4ea-c33e82c387d5 | checkpoint | Test completed to specification/drawings & Area left clean/tidy
e48e9088-dc7f-5746-a08c-8e30fc0e69a7 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
810f5544-91a0-4852-acf1-162ef93d42f7 | checkpoint | Entire Fire Sign-Off (attach signature)
ce6dbe12-0612-4343-8319-c4179e20ced7 | checklist | EFPQF06 - Pre Action - Sprinkler Control Valve |  | EFPQF06 - Pre Action - Sprinkler Control Valve
da9b916f-4c16-4fcd-a052-45e61e483d98 | section | Documentation
4076683e-0a14-4de9-9bce-8f60857e9b42 | checkpoint | Confirm construction drawings approved for use.
5dfba30e-88ea-49bc-95dd-d36d78276062 | section | Incoming Inspection
aae1757d-a778-4125-9eee-8750cf7f74dc | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
63c771ba-1863-5c97-ae49-967fcbc2995e | tickbox | Isolation valves.
cfbe1a05-9419-5b43-9039-139965fabebb | tickbox | Alarm valves.
38813808-9a89-5955-9941-8bde3030737b | tickbox | Pressure switches.
a71eb5f5-286d-5ab8-8828-07f219a0d7f8 | tickbox | Nitrogen generator/Air compressor
f6330529-7994-4c34-b75d-6cadf6436f07 | section | Installation
857e813b-1816-4c41-a29e-3d25e7b986c9 | checkpoint | Main stop valve installed
a56308dd-9966-48ef-96f8-66038d709095 | checkpoint | Alarm valve installed
84d848c3-d912-4ecf-a93e-cae649dd78dd | checkpoint | Drain valve installed
8cb6188c-a39a-41ad-81d0-d1be5211bb2d | checkpoint | Alarm pressure switches installed
8b34a069-5bdd-4ce7-a3a5-bba305cac3d1 | checkpoint | Water motor alarm installed
7d78fb96-0340-465a-be5c-2105a7ca0a22 | checkpoint | Pressure gauges installed
816dd0d8-d578-4064-89de-96be2a62149d | checkpoint | Nitrogen generator/air compressor installed
d4194960-acc4-4bc2-b28d-48d7bd5c0ea3 | checklist | EFPQF07 - Pressure Test Report Sheet |  | EFPQF07 - Pressure Test Report Sheet
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
a7976d38-0ea2-4c60-8328-84889eb6f056 | checkpoint | Test Details & Results
e66e3813-b801-520e-96d7-4313629778fe | textbox | Test number
632f4abe-7804-5251-a823-9e0efe797548 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa)
f1c92c1c-5b2e-52be-9137-fe05eb5ccafb | textbox | Start Date
ed825325-eed4-542c-8e3a-62e65347e4e3 | textbox | Start Time
bf8cf807-3f3a-5c6f-a269-ecddbc61a286 | textbox | Start Pressure
0ebdd96c-e8c6-5be0-8d1d-7e0a7a37aaa8 | textbox | Finish Time
ac705336-0b0d-505b-a8ab-787395063854 | textbox | Finish Pressure
433fa3ea-a1f3-54a0-9a79-6e638489dae6 | textbox | Gauge Reference
e0fcf168-53e1-4ee8-a61e-bc94a75d6f15 | checkpoint | Test completed to specification/drawings & Area left clean/tidy
f3a86841-e1fe-5b85-b347-fe0cb12607d6 | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
c51341e5-a52f-4ee7-9355-1eaf50b41014 | checkpoint | Entire Fire Sign-Off (attach signature)
2499d102-4b32-4245-8e99-fd6f6d90c275 | checklist | EFPQF08 - Fire Alarms Install |  | EFPQF08 - Fire Alarms Install
82a16cc2-a7e9-49e4-b123-53ed36ba796d | section | Documentation
c852b4d7-9bd7-4e08-934c-76a1b191c96a | checkpoint | Confirm construction drawings approved for use.
e28f4329-9efe-49f0-b77c-e1631af9d7d6 | section | Incoming Inspection
9d32b5ea-d12a-462c-a648-56c335456c4e | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
a7595205-aa28-52ab-adfc-94252f5872bc | tickbox | Fire rated cable
e434fe42-538a-5bd7-a8f7-d89c1a32e18d | tickbox | TPS cable
01ee030c-0c5b-52b8-8f19-64cf41930f51 | tickbox | Detectors
89a38ad1-8b9b-50f5-ab10-5173dffa860c | tickbox | Strobes
ae529c22-8517-560b-aa6b-832d2758df63 | tickbox | Speakers
fe0e997d-1929-41e3-bbea-3a8e0f9abbb2 | section | Installation Rough In / Fit Off
a0fd7fbc-56e9-4d8d-bd60-6fcb6d1f1618 | checkpoint | Confirm correct cable type run
508beed6-f907-4391-a846-12dacb23cca4 | checkpoint | Confirm cable support/conduit fixings and spacings
5eca0742-0601-477b-b1a2-c8d689fa98e3 | checkpoint | Confirm segregation from other electrical services
f3d0eb54-7de1-4b7a-8d46-3d6c3fdaf459 | checkpoint | Confirm detector fit off locations
b7100b31-d2aa-494d-9c08-4c66e8bf5e54 | checkpoint | Confirm speaker fit off locations
08588fa7-1b41-4025-bf68-cb85fe88d2a3 | checkpoint | Confirm strobe fit off locations
b8589da3-09a8-441d-bb60-4cbc93b86c05 | checkpoint | Confirm fire interfaces connected to sprinkler installation
01cbe4a4-01e3-44d0-a332-dc68a77d1567 | checkpoint | Confirm fire interfaces connected to security
adef7bae-d3e6-4aba-ab0c-2a1c92833b7a | checkpoint | Confirm fire interfaces connected to mechanical
4faab784-fdc2-4002-9114-3d3e6e8a9862 | checkpoint | Confirm fire interfaces connected to BMS
fe01dde8-84ff-4509-844c-8ba8fe7b7db9 | section | Sign-Off
9c0ef81c-2c1c-4630-80c8-b1a356f54ed1 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
884cffab-153f-4efa-aa10-2cb583fbfe5e | checklist | EFPQF09 - MASDS Install |  | EFPQF09 - MASDS Install
0007a541-9066-4f2a-a50a-db2d770a3ef6 | section | Documentation
da1556af-c65a-4b43-b417-1c6f0a365fa3 | checkpoint | Confirm construction drawings approved for use.
1cc7fb39-f368-4ff0-a355-fe7b49841458 | section | Incoming Inspection
6912f894-ac6b-4edd-8598-69a75e006d1b | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
76c77f71-245c-5fcb-8d45-ce2375bae22b | tickbox | Fire rated cable
d5fc5427-ef30-55c3-a25d-d1db9eb7e314 | tickbox | TPS cable
21eef353-5646-569f-b927-56aa44bf1fcc | tickbox | MASDS units
872d5c54-19b2-5713-8865-6e03f748c99f | tickbox | MASDS pipework
1d030e35-13e9-5a87-892c-a21652650c1b | tickbox | MASDS Power supplies
2d32de7c-8319-4a80-874a-501da9816e0e | section | Installation Rough In / Fit Off
8d4884ad-a8e6-4ad3-9361-b06549f2717b | checkpoint | Confirm correct cable type run
321a5668-1c6e-471c-843b-6c5be04c2ab8 | checkpoint | Confirm cable support/conduit fixings and spacings
0eaf0fa5-bfe0-48b7-9428-0ea9e079d711 | checkpoint | Confirm segregation from other electrical services
ceb5cdfe-de84-4c4d-84fe-52fb8f4c49b5 | checkpoint | Confirm MASDS pipework installed as per drawing
db7576b1-4b14-4f44-b581-03463abec4b8 | checkpoint | Confirm MASDS sampling points size & spacing
40c4dfe9-7d2b-4c72-8178-35e7f78a4d77 | checkpoint | Confirm MASDS unit fit off locations
9d2ee37c-f98a-44c6-83bb-a29dbcccb55e | checkpoint | Confirm MASDS power supply fit off locations
05c9953b-f73a-48d6-88c2-05accb65b958 | section | Sign-Off
ca58930c-6c73-4609-a17a-64e643c85d16 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
f67c92ec-beee-40ec-b549-8376839dc53b | checklist | EFPQF10 - FDCIE Install |  | EFPQF10 - FDCIE Install
2f01fe87-d728-4c7d-a5a9-06433b5cbc30 | section | Documentation
bc3e7ecd-20c8-4ff9-bd43-99a20825bfad | checkpoint | Confirm construction drawings approved for use.
741e6031-d953-44a8-84f2-ba7ff08d594b | section | Incoming Inspection
ab22032e-8da4-436e-a00b-7653b58745ba | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
12d6db18-7b12-5f03-885f-f7a871065893 | tickbox | Fire rated cable
f28bcd32-6c8d-565d-b355-94590863cee3 | tickbox | TPS cable
1c89253a-c3bd-50b9-906c-aa62ffe41758 | tickbox | FDCIE Panel
ba86a3a2-589d-4a2d-b460-b3fac852748f | section | Installation Rough In / Fit Off
a1ca623d-ed64-4e2d-b81d-ad7c11a6d2b8 | checkpoint | Confirm correct cable type run
64b7da38-dbf0-4e11-b4c0-aea6502078ac | checkpoint | Confirm cable support/conduit fixings and spacings
95b66e2c-1c66-4793-9b8f-0ca2107ed862 | checkpoint | Confirm segregation from other electrical services
441547c2-917b-46c5-a525-c8e54d8f922f | checkpoint | Confirm FDCIE mounted in correct location
97493874-6735-461a-a7d0-0eaee9ed3f57 | checkpoint | Loop cables terminated to correct output
1feff06d-6cdf-413d-a3be-52314a4bee12 | checkpoint | Confirm OWS cables terminated to correct output.
272d415f-8086-4ea7-a54d-f21805e64123 | section | Sign-Off
720e86e4-0686-4889-aa67-aa17a3f1ab7a | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
a5c2cb54-c68a-4129-8fed-a0ab042be500 | checklist | EFPQF11 - Fire Hydrant & Hosereel Install |  | EFPQF11 - Fire Hydrant & Hosereel Install
2d9d5f4c-0731-45bc-9ba4-918ef3f6b69d | section | Documentation
5ef089a5-df08-489c-983a-d24070cf2097 | checkpoint | Confirm construction drawings approved for use.
316e5110-f776-4b1d-9fe3-fa2b174bb278 | section | Incoming Inspection
a61f22e3-d8ca-4100-a945-4e669507c2e8 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
e3926c0b-3f62-582f-98e1-0fa61b7b4d78 | tickbox | Pipework.
1bd29893-005d-581e-b18f-a4cb25c269b5 | tickbox | Fittings.
49214c52-2c8e-5266-9edc-00f84a896629 | tickbox | Hangers.
1ec787d3-9e32-5d9f-bbac-63d370e9b697 | tickbox | Isolation valves.
a131e473-2f75-5bf6-8056-cd7469c86be2 | tickbox | Hydrant valves.
48bf6eda-b03c-5ac2-ac93-4f5e5e74e5c1 | tickbox | Hosereels
162e6afd-137b-4cb7-9ffb-9c385723bce3 | section | Installation Rough In / Fit Off
a128025a-49e5-4a39-abce-88ae2b820bec | checkpoint | Confirm hanger spacing.
f521fa73-555a-53ce-ab6e-2587d583f7fe | note | 100mm - max 5m spacing.
aa86af95-75cb-5724-9ca7-f13e29a7961f | note | ≥ 150mm - max 6m spacing.
3a78e2a3-8c6c-459b-9ce7-c2bf5d0a726c | checkpoint | Confirm support at change of direction at 1m max.
5658f73b-3caa-4546-82c1-78d44dc42b0e | checkpoint | Confirm support of pipework no more than 1m from end.
e29100cc-0574-4a65-9ffd-b6d429a9ae3c | checkpoint | Confirm support of horizontal branch from vertical riser no more than 300mm from riser
d01b395f-6bf3-4c35-96b6-f92ee789c324 | checkpoint | Confirm pipework installed as per drawing.
e116ead8-7e96-4850-b2b3-7fe16b3283b9 | checkpoint | Confirm hydrant height at handle between 750mm and 1200mm
a2482fdb-5fd2-44f6-b55a-58fe0c5e01ce | checkpoint | Confirm minimum clearance around hydrant handle 100mm
4ed1b835-b64f-4451-9c1b-213f7b80e66b | checkpoint | Confirm hydrant valve outlet not inclined more than 35° from horizontal
40ceae92-1043-41e7-a465-820596e31103 | checkpoint | Confirm outlet has 300mm clearance for a minimum 225 degrees
36819500-eb38-409d-98e7-9f3bf453b956 | checkpoint | Confirm hosereel mounting height 1400- 2400mm to centre of barrel
52e43776-0f8e-4064-a81e-8abbdcf6d6e4 | checkpoint | Isolation valve height is 900 – 1100mm
d1c849db-2402-41b1-aa2c-cb454eeef624 | checkpoint | Maintain 100mm clearance around barrel
354e29d4-4666-4666-95c9-479bd6fd02e2 | checkpoint | Confirm hydrant cap and chain installed
68f78131-15c7-4f33-958b-0c2d74ada60a | checkpoint | Confirm installation pressure gauge installed at top of most remote hydrant
b1d99ab1-6d91-4b1f-9158-2f995ed457c7 | checkpoint | Confirm pipe identification labels installed
751ba019-5fdb-4edb-9a26-fcf46d307ada | section | Sign-Off
6b604b32-680a-4fa5-a74d-864dc89faab1 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
3e00a85a-ea19-4f20-b68f-c8a45ff6ba86 | checklist | EFPQF13 - Fire Booster Assembly Install |  | EFPQF13 - Fire Booster Assembly Install
a091b63a-1492-44b9-b15a-79802e5f69c9 | section | Documentation
2348100f-7880-4a10-9fc7-28f3e957d9c9 | checkpoint | Confirm construction drawings approved for use.
bbc98efa-57ee-4d56-95be-b270fd417f40 | section | Incoming Inspection
0978b40e-3179-4f1e-9223-7da6206a045a | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
0d722f22-6396-50e2-bbba-510f270e26d4 | tickbox | Fire Boosters
d3aa9ec5-18fc-5fa9-9411-41dd00d84bde | tickbox | Suction Connections
6bed86c7-3efc-5358-b3b7-bdcf3344d8b5 | tickbox | Feed Hydrants
8b563c86-9854-5c8a-a479-5ac488887657 | tickbox | Isolation valves
64038cef-eb9a-434a-9b6f-64180e326215 | section | Installation
c8139923-06e3-4ba7-9224-f758d88642a6 | checkpoint | Confirm height of booster outlets between 750mm and 1200mm above standing surface in front of booster
c7b13230-c396-47dc-a044-5ea0aa82db08 | checkpoint | Confirm height of feed hydrant outlets between 750mm and 1200mm above standing surface in front of booster
e20b8afe-9998-474c-9949-50bb9c772366 | checkpoint | Confirm height of large bore suction connection between 450mm and 600mm above standing surface in front of booster
9c73e3ae-23e4-4cad-b10d-77024fa7f35b | checkpoint | Confirm height of small bore suction connection minimum of 400mm above large bore suction connection
b22bed20-86a1-4342-b26b-4aa1a602bf5e | checkpoint | Maintain minimum 450mm centre to centre clearance between outlets
5be56698-c74e-49fa-9161-45e8d5076a35 | checkpoint | Confirm front face of all connections within 150mm of the front of cabinet
724404de-3b7f-446a-b9b3-a29e8bfa6f1e | checkpoint | Confirm caps and chains installed
9fa2d35b-bb56-4ff6-8bb0-fd4861f4fa6e | checkpoint | Confirm isolation valves chained and locked
c0b5d0f7-93b7-4107-8862-812aa4fd3514 | section | Sign-Off
cd037236-cf7d-4f5e-a20f-88d4ffd98430 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
cb735854-1cbc-49fb-868a-ca87e5b9f564 | checklist | EFPQF14 - Gas Suppression Install |  | EFPQF14 - Gas Suppression Install
558b287b-cfe8-4698-af7d-48b3a2c23d17 | section | Documentation
5ce222fc-e7a9-4d14-bd2a-abbb90b8abe7 | checkpoint | Confirm construction drawings approved for use.
597e2d7c-fa08-4d4e-bfd0-72a30189ded2 | section | Incoming Inspection
98f91322-79b6-4e7b-b13f-0751f00b8faf | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
c3c18e92-5056-57c8-80d4-a2ca57d30c91 | tickbox | Fabricated pipework.
e9d7a03a-3f76-5691-aea0-1e14c8ff9ac3 | tickbox | Fittings.
aad5023c-3cc6-5e09-b862-65f040de1d6b | tickbox | Hangers.
8aed7505-87d7-5a96-ba3d-b5fd083ed473 | tickbox | Nozzles
105f168f-c2af-507b-a5f1-4f50060fa126 | tickbox | Cylinders
5dc04b71-8065-51f3-965b-ea02ca825a6d | tickbox | Actuators
32aa1abb-c937-58ee-9d3d-be2d4f60b41f | tickbox | Hoses
763541fb-7392-5ee1-9744-dfccc969bdb9 | tickbox | Gauges
508bfe08-05c1-4fb5-9fbc-1548e0f6733d | section | Installation Rough In / Fit Off
e0d024b4-4e15-4f59-b82d-f46263fe1739 | checkpoint | Confirm maximum hanger spacing.
6ee5c196-9501-53a0-bd50-9b20d68181b2 | note | 25mm - max 4m spacing.
1f877667-d521-5870-9164-b34486129d59 | note | 32 – 100mm - max 5m spacing.
1517dfa2-4783-5218-91c5-ce555ebc3e6d | note | ≥ 150mm - max 6m spacing.
0ceadb3f-ed8d-5c83-92e5-7d61924499aa | note | Acceptance Criteria - AS:2414
c4ed6eb3-10ba-45fd-b9c6-d855902e1aa8 | checkpoint | Confirm support at change of direction at 1m max.
b2c86516-961d-5814-8c7c-f909bc4d5284 | note | Acceptance Criteria - AS:2414
f300b31c-f746-48eb-9dfa-2f77c8b68684 | checkpoint | Confirm support of pipework no more than 1m from end.
e46b0bc8-6113-5d9b-8134-c41322ac4c91 | note | Acceptance Criteria - AS:2414
f0921575-7a6b-4bcb-bda3-ba4657b4207c | checkpoint | Confirm support of armpiece exceeding 500mm.
50f3dba1-d155-5818-8ddb-babc9096ca2a | note | Acceptance Criteria - AS:2414
6fb1f23e-372d-4f34-bd62-a0b32e26572d | checkpoint | Confirm first support of range pipe within 2m of mains.
bb0ea2f1-48e7-5f41-aeb2-7f0803c532ca | note | Acceptance Criteria - AS:2414
8303f01f-a30d-4f0e-a9fd-c37f43e6a391 | checkpoint | Confirm pipework installed as per drawing.
a9c380a5-ba19-4cc0-bd1d-7ee8bd95058f | checkpoint | Cap installation and perform pressure test
67321ae9-099f-5cfa-83c2-00b7131f242b | note | Acceptance Criteria - AS:2414
6a1bd738-8b69-48ee-86ff-b0a588322378 | checkpoint | Confirm discharge nozzles installed.
1668a94e-9fd8-4bd7-99c7-18c67f6055e3 | checkpoint | Confirm gas cylinder mounting as per manufacturer instruction
d2925f82-8c88-404e-8f53-fa2f79cd8bb7 | checkpoint | Confirm cylinder hoses fitted to discharge manifolds
5616ddba-b636-4bb6-ab11-cb1e3ba593b4 | checkpoint | Confirm cylinder pressure gauges fitted and indicating correctly
771950cc-e790-433b-b2b2-0c0a9f4b5fd8 | checkpoint | Confirm discharge actuators fitted
88a87beb-9db7-4ac1-8e71-c30c4f60d69d | section | Sign-Off
a0df75ab-e740-47c7-92fc-30d017427ed7 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
e8f89045-6591-4076-8765-c681dc221b79 | section | Pressure Test Report Sheet
b35e4829-b08d-4361-8561-7d1ad3ecf720 | checkpoint | Test Details & Results
6d7aef8c-27a0-5b66-95cf-3d14569b7a69 | textbox | Test number
d765bce0-1701-502c-9df8-90e9696bd440 | dropdown | Select relevant Test Criteria | HYDRANTS - HYDROSTATIC TEST – 1700kpa 2 HOURS - NO LOSS, WET FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - HYDROSTATIC TEST – 1600kpa 2 HOURS - NO LOSS, PRE-ACTION FIRE SPRINKLERS - PNEUMATIC TEST – 300kpa 30 MINS - PERMITTED LOSS 10% (30kpa), PNEUMATIC TEST – 300kpa 10 MINS - PERMITTED LOSS 20% (60kpa)
c006f9fe-d3bf-5401-91b2-665a0b3033e7 | textbox | Start Date
352a4d2c-d667-5b9c-a7cc-5cbb32bc685e | textbox | Start Time
cfbaa047-1cb3-5133-9e2c-e932ab2089fe | textbox | Start Pressure
87c14f5b-35af-5b83-8d19-3a694b2f7663 | textbox | Finish Time
e19eb48e-e65f-5cab-a28b-dc0ca06c2c35 | textbox | Finish Pressure
f61fa1a5-b311-547a-b970-677669ef9de4 | textbox | Gauge Reference
410d9216-ebd0-4552-b58c-17ae4e1cffcf | checkpoint | Test completed to specification/drawings & Area left clean/tidy
fef9e4d3-494b-5e7e-80db-788d1231649b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
e57d5b8d-918e-43ca-8724-e22446e786e6 | checkpoint | Entire Fire Sign-Off (attach signature)
05535ba1-0826-4119-a7f0-2f30982c26a8 | checklist | EFPQF16 - Fire Extinguisher & Blanket Install |  | EFPQF16 - Fire Extinguisher & Blanket Install
7e0e82e5-62f8-4043-84c4-ec3e12c46c7d | section | Documentation
32ab58b0-d5b0-42e9-834a-2304c6ee3766 | checkpoint | Confirm construction drawings approved for use.
cbcac3f0-9edd-4268-b760-a15fe2071e21 | section | Incoming Inspection
4cb988bb-d8a4-44cf-9d8e-ed4b3706fc63 | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
a70c81c0-9eb5-58cf-93bc-aeb9dbcb61b0 | tickbox | Fire Extinguisher.
245371f8-9d98-55a0-ac03-5ecb85171bcb | tickbox | Fire Blanket.
13415f31-318c-5a2c-aaf1-e084f70d830d | tickbox | Signage.
f57c4b4e-50bd-4870-8b95-d434096414cc | section | Installation
c9c60270-c2e5-458a-bb3f-b5b8a3d07957 | checkpoint | Confirm top of extinguisher handle ≤1200mm above floor level
14b568a6-7bdd-5709-8908-227b4c1cea66 | note | Acceptance Criteria - AS:2444
f733298b-0a5b-4874-8138-70a89bb5b23a | checkpoint | Confirm extinguisher type signage located just above handle
c3d2c847-af28-5561-98aa-43fb63ee2aff | note | Acceptance Criteria - AS:4587
4245e06a-fa83-4fb9-911f-0960dc34cd35 | checkpoint | Confirm extinguisher location signage located at ≥2000mm above floor level
bc9c1cee-ed11-5e2a-bab9-4d472e7b9683 | note | Acceptance Criteria - AS:4587
0f098280-fdd1-499a-8faf-fc47ad87fbaf | checkpoint | Confirm fire blanket located in a readily accessible location
2139087d-bba7-53a4-a984-9fee82e5ef2c | note | Acceptance Criteria - AS:4587
494a8826-800d-42fd-9dad-d305583037e3 | checkpoint | Confirm fire blanket signage provided adjacent to the fire blanket
908a9a72-ce36-5566-ba97-7b72c56730b4 | note | Acceptance Criteria - AS:4587
0578365f-0891-40b3-89ac-62d6c5fc4b7c | checkpoint | Confirm fire blanket location signage located at ≥2000mm above floor level
e0b48e1b-7ad9-5f62-b874-be5e042ed4bc | note | Acceptance Criteria - AS:4587
4637c85e-e946-4e61-bc48-c73c20cab29f | section | Sign-Off
9283fd46-a094-4c95-b211-82e71f024250 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
ddb5bee1-83bb-41dc-bdee-c02c88645a84 | checklist | EFPQF17 - Fire Electrical Commissioning Test Report |  | EFPQF17 - Fire Electrical Commissioning Test Report
0141aa6a-ab28-4e7d-a939-78d9d7681a16 | section | Pre-Start
f9a01391-b48d-42cd-95f8-bfb68fd62b67 | checkpoint-no-value | Information
4121b323-4bb2-5e77-aa8a-6e04acdec21d | textbox | drawing reference
642639ab-1bae-594a-98e4-3b1039d0196c | textbox | level and area
0c3db7e1-7a83-422a-b71e-c03bcbf4fe07 | section | Installation
f6ba77de-0e5b-464b-92a0-1ca27b80dc01 | checkpoint | Secure cabinet
2f1aa976-d24e-5c41-b98e-7b485bbe2adf | note | Specification Ref: drawing
fab65b36-bd01-4709-b66f-162da5ac7d5c | checkpoint | Extinguishers installed
d1ce464a-d3ab-57e2-a8a6-8b22945a496b | note | Specification Ref: drawing & AS:2444
afacc35d-3de6-4681-b852-9e4e2cb8e7dd | checkpoint | Signage to meet code compliance
9a97e4cd-876f-594d-b483-5f3db068bce7 | note | Specification Ref: drawing & AS:2941
28db5e59-d6c6-46ee-ac76-3a19b544c42f | checkpoint | Hangers location and spacing
460f4e31-b39d-5f33-8f4b-46a886bab29b | note | Specification Ref: drawing & AS:2941
5d595ac6-52b6-4576-a40b-3df7a3bcd6bd | checkpoint | Fire blankets
75b0ec2f-1cce-5cff-b57e-d1a1b394f6bb | note | Specification Ref: AS:2444
c21d4883-4dbc-4ac6-a0d9-eb069e285f82 | section | Sign-Off
6ce38c01-0caa-4225-b138-2826a44269a8 | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
c3374aed-2771-5716-bcc7-f97c8e10b73b | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
5c2c3975-0f4c-5ffd-b397-70c639497f60 | button | Entire Fire Signature Sign-Off added below | Yes, No
cf7c8bba-704d-4752-a53b-c0d1c98bc467 | checklist | EFPQF18 - Fire Penetrations (x 10) |  | EFPQF18 - Fire Penetrations (x 10)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
0cf2468c-cd60-4e54-9862-01bf5fe2d9e1 | checkpoint | Fire Penetration details
e209cb5a-4e4f-5314-9d3a-8d6d9b3de72c | textbox | Location
fa3a938c-2868-5229-854a-ae1f51c2fe30 | textbox | Diameter
f84d76b8-e567-5248-945d-1c179d07b1dd | textbox | Wall/Slab Thickness
1efe42b9-1ad5-4e6b-9313-c26561ae0928 | checkpoint | Sleeve installed satisfactorily
152ddaeb-56d8-55fa-8b3b-e1f76b2092bb | textbox | Date
3fede153-598b-45ef-85e8-3fd6cadf5396 | checkpoint | Fire Penetration details
cec6f99f-45c4-561f-9836-979d6eac0252 | textbox | Location
96358dc4-1381-525f-aa3a-715d6bda9913 | textbox | Diameter
9ac7573d-7b59-5081-bd5a-ffd31f2a3b75 | textbox | Wall/Slab Thickness
51ba18cb-dc4d-44ab-aadd-3cf5efdd6c21 | checkpoint | Sleeve installed satisfactorily
4bb9f99d-15fe-59eb-be45-936d46f9f6b9 | textbox | Date
b7fbc4db-df83-49a8-a790-c03db1a3eabe | checkpoint | Fire Penetration details
f31ebd37-e24c-5717-929b-e060cede3924 | textbox | Location
63eac541-2f38-55d1-b0ce-77f93a5e63fd | textbox | Diameter
364b86ae-f489-50a4-9633-7bbdd6ca2363 | textbox | Wall/Slab Thickness
bafc23ce-bd68-4689-afbe-851b7ccdfed6 | checkpoint | Sleeve installed satisfactorily
11963160-b683-5dde-bab5-d123115c63a0 | textbox | Date
ea9711df-68b2-4174-aa14-ae7aaf5d9ef0 | checkpoint | Fire Penetration details
f7edbcf9-88c7-5006-a908-fef049f5d01e | textbox | Location
5d52ece4-10d1-5d6e-9eb5-5c62865e51a7 | textbox | Diameter
c82318ba-6f1b-5847-a2dc-511b392e6d82 | textbox | Wall/Slab Thickness
3a0dfbf2-a7dd-4c9b-884b-2217257602c7 | checkpoint | Sleeve installed satisfactorily
a312ce6c-6dde-55b4-ab33-74daae20b885 | textbox | Date
a9e88b07-a7af-4c38-93ae-cd6fb3f02da5 | checkpoint | Fire Penetration details
69f3d66d-35f8-56a4-8a5e-54411d787178 | textbox | Location
6ffbbb3b-7a1d-5188-a08b-21f413f20b1b | textbox | Diameter
ec2f0193-385e-5728-8ee0-73cea48eff7f | textbox | Wall/Slab Thickness
7a2f6842-dd87-4d4d-8fe5-dd6bbd8f1dfe | checkpoint | Sleeve installed satisfactorily
6c7b4055-5422-5d92-bc2a-6590a4620be3 | textbox | Date
db94ca8a-60c4-47f7-9e40-b616a02ff661 | checkpoint | Fire Penetration details
23967716-2e57-5804-ac59-957bf20e0e67 | textbox | Location
f3009d2a-b078-580e-ab58-38cf2d4176a6 | textbox | Diameter
415e416b-dc27-5372-9f6b-4bd4192118df | textbox | Wall/Slab Thickness
1aec3899-b615-4948-a3c1-09375813a14c | checkpoint | Sleeve installed satisfactorily
c7b96366-5bce-5725-a1af-45197cce9754 | textbox | Date
7af4ca93-1cbb-48df-aa9f-aa36203ed7e1 | checkpoint | Fire Penetration details
31e4c4ff-8265-5986-b0ca-67ddbc741f39 | textbox | Location
b01557b9-5e42-5be8-a1d4-e9a4dfc5e39e | textbox | Diameter
5ae6fe75-460c-511f-b0e6-75f8f93e43f1 | textbox | Wall/Slab Thickness
cfb692e9-3620-4546-a8a6-e3f5fc98e757 | checkpoint | Sleeve installed satisfactorily
fd1de7e9-8238-554e-885e-c9bd88a78ae0 | textbox | Date
6aa0da0a-1f0b-4aef-ac7c-4314e6912ed5 | checkpoint | Fire Penetration details
4ab36e3d-5be9-54ac-a750-44571f070bb6 | textbox | Location
0320c7b8-5aaf-5976-b91f-8d5dae7ab8dc | textbox | Diameter
1710f63c-f0ec-5e47-a781-cd0ec2b9fb64 | textbox | Wall/Slab Thickness
db9c9e4e-df89-49d1-808d-ca5779127aab | checkpoint | Sleeve installed satisfactorily
7efb801d-8798-5080-99b9-c2661e0f0308 | textbox | Date
4e9e3c8a-4c2c-4dd1-9460-2edeffe65eee | checkpoint | Fire Penetration details
b8ef13f8-2505-56ff-b94b-5a07a91b2e02 | textbox | Location
5973a74f-292e-594c-9fa5-59c932d4130b | textbox | Diameter
3c9be382-dc2f-5187-8bcc-1aec3b0ee141 | textbox | Wall/Slab Thickness
02b524e0-d121-47ce-8716-fafd97ddb21c | checkpoint | Sleeve installed satisfactorily
739bb3fc-20dc-5921-b294-d5b1b36896ea | textbox | Date
e1687960-2860-4970-aa28-9641fc959a4f | checkpoint | Fire Penetration details
a68ffd20-91c9-58a7-b8e6-45e0c662a1d1 | textbox | Location
d90fa9a9-75ab-5629-af58-09a920b49725 | textbox | Diameter
9efeea8b-19f0-58fd-a3ac-c522f1726090 | textbox | Wall/Slab Thickness
0bf3d914-b5fb-4928-ad13-1bab64f32c76 | checkpoint | Sleeve installed satisfactorily
a4c1f44e-476a-5f9a-8119-1b15b7ee82a3 | textbox | Date
f86b038d-8eb6-4704-844b-89ba51bcce0e | checklist | EFPQF19 - Occupant Warning System Install |  | EFPQF19 - Occupant Warning System Install
0fa9cc22-27a6-48a2-a549-4dad447637e1 | section | Documentation
44fef904-f798-4413-b55e-28d068bf8844 | checkpoint | Confirm construction drawings approved for use.
163883d5-8e2e-4893-ac09-fdd6cbf1e4f3 | section | Incoming Inspection
a568eb34-7729-4b94-b0cf-3939a7e932db | checkpoint | Incoming Inspection - PASS if received in good condition - If not FAIL & Attach Photos/Comments below
5b08a353-2e5c-54b4-8b4a-cc3362efdf09 | tickbox | Fire rated cable
b9c932a9-7be0-52ba-af73-7f4b9728fb26 | tickbox | TPS cable
db72c8cd-dc9a-55f5-8389-12e5ca20913f | tickbox | OWS Panel
f683e2c8-71a5-5c9b-a0e4-28bce300da6f | tickbox | Speakers
89fd219d-c3e7-5bea-a1bf-1045feb6b19a | tickbox | Strobes
883d4029-4220-5579-a520-307d14a5e819 | tickbox | VAD
7af4246b-ed45-4519-85af-c1486a3a792d | section | Installation Rough In / Fit Off
8b039c37-ea69-4d5a-b250-0852574fff6b | checkpoint | Confirm correct cable type run
7dfc6046-11b4-576e-8cfa-a5d2aa8f8d6e | note | Acceptance Criteria - AS:1670
706148a7-0b71-4d71-8761-412febb49e78 | checkpoint | Confirm cable support/conduit fixings and spacings
6c3a6805-935a-5ce0-87eb-3d69932ae988 | note | Acceptance Criteria - AS:3000
49a1502c-43e5-4881-8596-d04375389bc6 | checkpoint | Confirm segregation from other electrical services
b00d116f-ed0c-5018-bd6b-d7ac0d7811cd | note | Acceptance Criteria - AS:1670
4e0a764f-6181-4b49-ac90-6959ffc2e832 | checkpoint | Confirm OWS mounted in correct location
220949bc-9170-4d27-af8b-3e09c6c3e618 | checkpoint | Loop cables terminated to correct output
8aff832c-de60-48f8-8631-8ab297d40cf0 | checkpoint | Confirm FDCIE cables terminated to correct output.
4a9159fc-5407-41b9-bdf8-90542d4d0382 | section | Sign-Off
dabf50f9-1943-47c2-8ef3-321fe16c9444 | checkpoint | Work(s) completed to specification/drawings & area left clean/tidy - Builder final signature to be attached below if applicable
0584064c-0ca5-48a1-bbd8-d0cd7560df45 | checklist | EFPQF20 - Calibration Record (x5) |  | EFPQF20 - Calibration Record (x5)
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
de57d880-718c-4dbc-9658-5194aef957f6 | checkpoint | 1.Calibration Details - Pass once entered
07ae80ce-d251-50df-aca6-93483af1f7b2 | textbox | Equipment
e592886d-162a-5154-bfdb-923771d79895 | textbox | ID Number
7aa9ab1c-a32d-5599-8bf8-c7e88f0213e1 | textbox | Expiry (If applicable)
093d1b1f-8587-53cc-8b62-a5d206034c65 | textbox | Record Number
c82edff1-bca8-5e80-8dc8-f5d47233aee4 | textbox | Date Calibrated
0767814a-ada8-432f-b8b0-e333a53b4709 | checkpoint | 1.Calibration Details - Pass once entered
89348c24-47df-5ea2-b054-96fc520cdcab | textbox | Equipment
61437e6c-ed93-58e8-910c-7937af7005db | textbox | ID Number
dd86af24-82bc-5a18-9b86-bdf1a0afaafd | textbox | Expiry (If applicable)
9991e67e-ad42-537a-8eb0-61289b467597 | textbox | Record Number
8bf52f32-074b-5519-aa99-a5b928f39551 | textbox | Date Calibrated
15e7ae97-ec0a-4137-a2f5-3d8d13d24ba3 | checkpoint | 1.Calibration Details - Pass once entered
2e9b2a91-ac08-5e5e-96e4-df2859dea3cf | textbox | Equipment
7a2b97f4-24fc-588f-aeb1-c8b2dba24cb1 | textbox | ID Number
2cf4bddc-8549-51f7-990d-f1419a03cfae | textbox | Expiry (If applicable)
b43c71cb-90f5-53eb-9668-51f3fb6bf595 | textbox | Record Number
40976e86-a0e9-5774-af16-f3a24b5ebb36 | textbox | Date Calibrated
ab074954-5fbc-4b9a-b306-d7a3b0a41676 | checkpoint | 1.Calibration Details - Pass once entered
cc62e8dc-350f-5f23-bf37-25ff14fb1606 | textbox | Equipment
6fdcc582-2cb1-5f68-8e09-943e5a5e6ed7 | textbox | ID Number
532542cd-7867-58d5-865a-5a4a1786467d | textbox | Expiry (If applicable)
8160eb84-9859-5465-8730-aaf620f3676a | textbox | Record Number
efb62743-0b28-5585-9058-59fd6053496a | textbox | Date Calibrated
67e75da9-da8b-4a4b-8809-57654dc2b3e9 | checkpoint | 1.Calibration Details - Pass once entered
f5b515ca-ad98-577d-a212-1f6914f745e8 | textbox | Equipment
169dc631-99ef-55f0-8fb0-447b6e6bcedb | textbox | ID Number
5604a108-c5fd-5d27-8e1e-475d5c68bf21 | textbox | Expiry (If applicable)
606d05ae-e2d6-5af2-b2c6-539d7f4ecdee | textbox | Record Number
e26977af-4aac-599e-95f4-d56f027899f3 | textbox | Date Calibrated
abcd4cbb-1d77-4b43-8967-e264f4ef3bc7 | checkpoint | Sign-Off Records completed
44ec500a-7cf4-5200-9076-a596e99b7feb | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
9d9fc651-f61e-568d-85aa-c271a60e0a66 | button | Entire Fire Signature Sign-Off added below | Yes, No