## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Fire Detection And Alarms FC ITP | itp
section | 1. PRE-SOFTWARE WORKS
checkpoint | RECEIVED ANNUAL TEST RECORDS AND REPORTS FROM ACM
checkpoint | REVIEWED ANNUAL TEST RECORDS AND REPORTS AND CONFIRM COMPLIANCE
checkpoint | TEST SELECTION OF EXISTING AZF'S TO DEMONSTRATE ACCURACY OF REPORTS:
textbox | Fire Panel:
textbox | Location:
textbox | Address
textbox | AZF
textbox | Device Type
textbox | Point Type
textbox | Description
button | MFIP DESC. CORRECT | Yes,No
button | GRAPHICS CORRECT | Yes,No
button | ASE ACTIVATION | Yes,No
button | EWIS ACTIVATION* | Yes,No
button | GFA FUNCTIONS** | Yes,No
label | * No specific EWIS testing shall be required. Alarm testing to demonstrate appropriate signals are sent to EWIS panel only. DB levels and operation an exisitng condition not affected or related to our scope.
label | ** Test will confirm simple operation of existing GFA function only. i.e. exsiting door release. This test will not extensively audit full cause and effect of alarm activation.
label | *** Only one x GFA test performed due to impacts to the facility.
section | 2. SOFTWARE WORKS
checkpoint | SUPPLIED REQUIRED FIRE PANEL SOFTWARE CHANGES TO JCI
checkpoint | RECEIVED REQUIRED FIRE PANEL SOFTWARE CHANGES FROM JCI
checkpoint | JCI ADVISED NODES WITH REQUIRED FIRE PANEL SOFTWARE DOWNLOAD
checkpoint | CURRENT FIP FAULT STATUS RECORDED
checkpoint | CONNECT IN NEW NETWORK CABLING
checkpoint | SOFTWARE SUCESSSFULLY DOWNLOADED TO ALL NODES
checkpoint | FIP FAULTS CONSITENT WITH PRE-DOWNLOAD RECORD
checkpoint | PROVIDED COPY OF SOFTWARE TO LL/ACM
checkpoint | SUPPLIED REQUIRED EWIS PANEL SOFTWARE CHANGES TO JCI
checkpoint | RECEIVED REQUIRED EWIS PANEL SOFTWARE CHANGES CHIPS FROM JCI
checkpoint | JCI ADVISED NODES WITH REQUIRED EWIS CHIP CHANGES
checkpoint | CURRENT EWIS FAULT STATUS RECORDED
checkpoint | CONNECT IN NEW NETWORK CABLING
checkpoint | SOFTWARE CHIPS SUCESSSFULLY INSTALLED TO NODES
checkpoint | EWIS FAULTS CONSISTENT WITH PRE-CHANGE RECORD
checkpoint-no-status | BACK OUT PLAN
label | FIRE: DISCONNECT NETWORK CABLING AND RE-INSTATE PREVIOUS SOFTWARE REVISION
label | EWIS: DISCONNECT NETWORK CABLING AND RE-INSTATE PREVIOUS SOFTWARE CHIPS
label | Note: Connection of network cabling in existing panels presents a risk due to the congestion of existing cabling, cards and age of equipment. Extreme care to be taken to not disturb any cabling, terminations and cards. All works to be undertaken with the respective panel switched off. Spare parts to be procured and on stand by if available.
section | 3. POINT REMOVAL LIST
checkpoint | POINT REMOVAL LIST
textbox | Address
textbox | AZF
textbox | Device Type
textbox | Point Type
textbox | Description
button | MFIP DESC. CORRECT | Yes,No
button | GRAPHICS CORRECT | Yes,No
section | 4. TESTING AND COMMISSIONING
checkpoint | TEST SELECTION OF EXISTING AZF'S TO DEMONSTRATE ACCURACY OF REPORTS:
textbox | Fire Panel:
textbox | Location:
textbox | Address
textbox | AZF
textbox | Device Type
textbox | Point Type
textbox | Description
button | MFIP DESC. CORRECT | Yes,No
button | GRAPHICS CORRECT | Yes,No
button | ASE ACTIVATION | Yes,No
button | EWIS ACTIVATION | Yes,No
button | GFA FUNCTIONS | Yes,No
checkpoint | TESTING OF ALL REPLICATED AZF'S
label | Methodology:
label | 1. Test each AZF isolate function is transmitted and displayed accurately from MFIP to SFIP.
label | 2. Test each AZF isolate function is transmitted and displayed accurately from SFIP to MFIP.
label | 3. Test 6 x AZF's via field activation. Confirm both AZF's at MFIP and SFIP indicate correctly. This test must include AZF 29 & 30.
label | 4. Test remainder of required AZF's via panel activation. Confirm both AZF's at MFIP and SFIP indicate correctly.
date | DATE
textbox | AZF
textbox | Description
button | MFIP DESC. CORRECT | Yes,No
button | NEW FIP DESC. CORRECT | Yes,No
button | GRAPHICS CORRECT* | Yes,No
checkpoint | BOTH MECP AND NEW SECP CONTROLS ALIGN
label | Methodology:
label | 1. Test each ECP zone activates and control and indication aligns at both the MECP and new SECP.
label | 2. Test 6 x WIP’s at varying locations to demonstrate control and indication aligns at both MECP and new SECP. WIP’s shall be called form both MECP and SECP.
date | DATE
textbox | ECP ZONE
textbox | Description
button | PA ACTIVATION | Yes,No
button | ALERT ACTIVATION | Yes,No
button | EVAC ACTIVATION | Yes,No
button | WIP 1* | Yes,No
button | WIP 2* | Yes,No
button | WIP 3* | Yes,No
label | * 3 X WIPs not necessarily provided in each ECP zone. Only 6 to be selected for testing
section | 5. FINAL CONFIRMATION
checkpoint | I declare the above information is correct as at the date as signed below.
textbox | Name
textbox | Position
date | Date
holdpoint | Sign