## 121 - ITP
Utilities And Street Lighting Inspection and Test Plan
Project: Homer Tunnel Avalanche Shelter
DS2676-DOW-ITP-CV-0121
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 10 – CONSTRUCTION ACTIVITY – UTILITIES AND STREET LIGHTING
10.01 | Utilities and Spare Ducts
10.01.01 | ITS Equipment Protection | The Contractor shall protect any such equipment from damage during the works until relocated by the MRA. The Contractor shall liaise with the MRA to arrange relocation of such equipment so that it does not impede on the construction programme. | PS 19.1.1.2 | Comms | Prior to Works | R | PE
10.01.02 | Spare Ducts | Spare ducts shall be fitted with draw wires and caps to allow future installation of services. | PS 19.1.1.3 | Site Notes | During Install | I | SE

## 122 - ITP
Stormwater Overarching Inspection and Test Plan
Project: Homer Tunnel Avalanche Shelter
DS2676-DOW-ITP-CV-0001 - Rev 0A
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 6 – CONSTRUCTION ACTIVITY – STORMWATER DRAINAGE
6.01 | Stormwater General
6.01.01 | Setting Out Service Clashes | The Contractor shall advise any clashes at least 5 working days before works are proposed to proceed to allow sufficient time for a reply. | PS 16.4.1 PS 16.3.1 | Notice | At least 5 working days before works are proposed | HP | ENG
6.01.02 | Pipe Minimum Cover | Culverts / pipes under pavement or trafficable areas (berms, access roads) shall have a minimum of 1,000 mm of cover unless specifically stated otherwise on the drawings. If minimum cover requirements cannot be achieved the Engineers input is required before work can proceed. | PS 16.3.1 PS 16.8.4.1 | Notice | When Encountered | HP | ENG
6.01.03 | Pipe Alignment | A proposed change in pipe alignment the Engineers input is required before work can proceed | PS 16.3.1 | Notice | When Encountered | HP | ENG
6.01.04 | Unsuitable Founding Material | If unsuitable founding material is encountered the Engineers input is required before work can proceed | PS 16.3.1 | Notice | When Encountered | HP | ENG
6.01.05 | Dewatering | The Contractor shall provide for keeping the works free from water at all times and shall provide, operate and maintain all pumping equipment, drains, sumps and other measures necessary for this purpose | PS 16.5.1 | Site Notes | During Construction | S | SE
6.01.06 | Environmental Compliance | All works shall be undertaken using an appropriate construction methodology to minimise the release of silt, sediment or other pollutants into any watercourse. | PS 16.6.1 | Methodology | Prior to Works | HP | ENG
6.03.04 | Compaction trials | At commencement of pipelaying, compaction trials shall be undertaken to demonstrate the adequacy of the proposed compaction methods to achieve the compaction parameters specified (refer to Table 16.7, and Section 16.7.3 of this Specification). | PS 16.12.3.1 | Compaction Trail Test Results | At commencement of pipelaying | HP | ENG
6.03.10 | As-Builts | As-built details of all stormwater infrastructure shall be recorded by the Contractor and provided to the Engineer in AutoCAD and hard copy format. As-built details shall be provided not only for new infrastructure but also for modified, removed or abandoned existing infrastructure | PS 16.13.1 PS 16.13.2 | CAD Asbuilts | Prior to PC | HP | ENG

## 123 - ITP
Stormwater Pipline and Manhole Inspection and Test Plan
Project: Homer Tunnel Avalanche Shelter
DS2676-DOW-ITP-CV-0001 - Rev 0A
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 6 – CONSTRUCTION ACTIVITY – STORMWATER DRAINAGE
6.02 | Pipes Installation
6.02.01 | Geo-textiles and Filter Cloths Installation | All Geo-textiles and filter cloths shall be handled and installed in accordance with the manufacturer’s requirements and have a minimum lap of 500mm when placed above the final water level an1m when placed below the final water level. Further to that shown on the drawings, all geotextile laps shall be orientated to the direction of flow. | PS 16.11.2 | Site Records | When Installed | I | SE
6.02.02 | Pipe Support | Concrete pipe support shall be a minimum of H2 unless stated otherwise | 16.8.2.1 | Site Records | When Installed | I | SE
6.02.03 | Embedment Wrapping | Where the pipe bedding / haunching / embedment material is not compatible with the surrounding fill or in-situ material (i.e. there are voids, or low-fines fill material is used in in-situ silt material) the trench shall be wrapped in filter cloth or an equivalent grade non-woven needle-punched geotextile filter cloth product complying with TNZ F/7. | 16.8.2.2 | Site Records | When Embedment material is not compatible with the surrounding fill | I | SE
6.02.04 | Embedment Placement | Pipe embedment material (haunch and overlay) shall be placed and compacted in maximum 150 mm lifts | 16.8.2.3 | Site Records | Each Layer | I | SE
6.02.05 | Connections to Structures | PVC-U or RCRRJ pipes shall include a pipe short adjacent to the connection to any structure / headwall and at all sumps / manholes. The exception to this is larger diameter RCRRJ pipes (>DN675) where pipe shorts are not available or may be omitted due to diameter. | 16.8.2.4 | Site Records | Each Connection | I | SE
6.02.07 | Pipes on grades steeper than 10% | Pipes on grades steeper than 10% (or 1:10 (V:H)) are to have cement-stabilised bedding and haunching wrapped in filter cloth. | PS 16.8.6.1 | Site Records | Each Occurrence | R | PE
6.02.08 | DN375 and smaller pipes laid at grades of 20% | DN375 and smaller pipes laid at grades of 20% (or 1:5 (V:H)) or steeper are to be SN16 PVC-U DWV pipe or Series 1 pressure pipe with an equivalent stiffness rating. A concrete bulkhead shall be installed at each pipe socket as shown on the Contract Drawings, excluding the manhole starter or finisher when cast into a concrete corbel. | PS 16.8.6.1 | Site Records | Each Occurrence | R | PE
6.02.09 | Pipe Installation in or under an Embankment | Where pipes are installed within or under fill embankments, the pipe shall be laid in an ‘induced excavated trench’. | PS 16.8.7.1 | Site Records | Each Occurrence | R | PE
6.02.10 | Pipe installed deep under embankments | Where pipes are installed under a significant depth of embankment fill material (>5 m), great care shall be taken to ensure the surrounding embankment material is well compacted and that the pipe bedding and surround material is well compacted. Use HS3 support in accordance with AS/NZS3725 where cover exceeds 5 m. | PS 16.8.7.2 | Site Records | Each Occurrence | R | PE
6.03 | Inspection and Testing
6.03.01 | Sub-grade Visual inspection | Visual inspection of sub-grade material prior to placement of bedding material where any unsuitable material, hard spots or weak founding material has been replaced. | PS 16.12.1.1 | Site Notes | During Construction | S | SE
6.03.02 | Subgrade Testing - Scala | A minimum CBR of 5% or 3 blows per 100 mm using a Scala Penetrometer is considered an acceptable sub-grade strength. The Engineer shall be notified where this is not achieved. Testing of founding material for appropriate strength at 10 m intervals or as otherwise directed by the Engineer. | PS 16.12.1.1 PS 16.12.1.2 | Scala Results | At 10 m intervals | I | SE
6.03.03 | Low fines - Compaction Testing | No compaction testing is required for ‘low fines’ material (defined as having 0% passing a 2.36 mm sieve) subject to having a compaction fraction of 10% or less (refer to Section 16.7.3.5). | PS 16.12.2.2 | Compaction Fraction Test | Prior to Installation | R | SE
6.03.05 | Acceptable Compaction trials | Provided the material and method of placement and compaction remain the same as determined by the trial, regular testing is not required where the construction is periodically inspected or supervised by the Engineer or his representative. | PS 16.12.3.5 | Notice | At commencement of pipelaying | HP | ENG
6.03.06 | Unacceptable Compaction trials - Bedding Compaction | Where the Engineer has any concerns over the suitability of the bedding or haunching material, or the thickness of lifts being carried out, or an alternative means of installation is undertaken, testing of material compaction can be requested by the Engineer at any time. Testing shall consist of Clegg Hammers calibrated to the material at 20 m intervals for the bedding layer and every second lift of the haunch material. A minimum CIV of 12-15 shall be achieved for all embedment material. | PS 16.12.3.6 | Clegg and NDMs | NDM at start of Run, Calibrated Cleggs every 20m | I | SE
6.03.07 | Flexible Pile Embedment Compaction | Compacting approved material in 150mm lifts to a minimum compaction of 95% MDD | PS 16.12.3.2 | As per Trial | As per Trial | I | SE
6.03.08 | Concrete Pile Embedment Compaction | Compacting approved material in 150mm lifts to a minimum compaction of 95% MDD | PS 16.12.3.6 | As per Trial | As per Trial | I | SE
6.02.06 | Wide Trenches | Where insitu soil conditions are deemed unacceptable, the support zone needs to be increased in width. This would involve widening the trench to four times the pipe’s internal diameter and refilling with approved material in 150mm lifts to a minimum compaction of 95% MDD, or for cohesionless material a Density Index of 70%. | 16.8.2.5 | Site Records / NDMs | NDMS every 20m every lift | I | SE
6.04 | Conformace Testing
6.03.09 | CCTV | All pipes (excluding sub-soil drains) shall be filmed with CCTV once the surface above has been finished. The CCTV shall be reviewed for any visible defects in the pipes. | PS 16.12.4.1 | Footage and Logsheet | Each Pipeline (Excluding Subsoil) | I | PE
6.04 | Manholes
6.04.01 | Manhole cover slabs | Manhole cover slabs shall finish approximately 200 mm below the finished pavement to allow pavement construction or top-soiling above. A manhole access riser shall be included to make up the difference from the cover slab to the underside of the access cover frame. The total dimension from pavement level to the soffit of the cover slab must not exceed 500 mm. | PS 16.9.1.2 | Site Records | Each Manhole | I | SE
6.04.02 | Manhole Connections | When connecting the pipe to the manhole, neatly cut or core drill the concrete to match the outside diameter of the pipe to provide a gap of 10-50 mm. The gap shall then be sealed with epoxy mortar both inside and outside to seal the joint. Where the gap exceeds 50 mm or the concrete has spalled, a concrete corbel shall be constructed to seal the opening from soil ingress. | PS 16.9.1.4 | Site Records | Each Manhole Connection | I | SE
6.04.03 | Manhole access cover | The manhole access cover and frame shall be hinged, with the hinge position orientated towards the direction of on-coming traffic. The access cover, frame and access opening on the cover slab shall have a nominal internal dimension of 600 mm. | PS 16.9.1.6 | Site Records | Each Manhole | I | SE
6.04.04 | Manhole Benching | All manhole inverts shall be benched to form a smooth transition between the connected pipes unless stated otherwise. For pipes smaller than DN450 the manhole shall be fully benched. | PS 16.9.1.7 | Site Records | Each Manhole | I | SE
6.05 | Sump
6.05.01 | Kerb Inlet | All sumps located along a kerb shall include a pre-cast side entry lintel. The lintel shall be aligned to the face of the kerb. Where the lintel is proud of the adjacent kerb, the two shall be transitioned together smoothly over a minimum distance of 0.5 m. | PS 16.10.2 | Site Records | Each Sump | I | SE

## 124 - ITP
Landscaping Installation Inspection and Test Plan
Project: Homer Tunnel Avalanche Shelter
DS2676-DOW-ITP-CV-0124
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 18 – CONSTRUCTION ACTIVITY – LANDSCAPING
18.01 | Landscaping
18.01.01 | Work Plan | A detailed work plan shall be prepared for all landscape works, at least two weeks prior to the landscape works commencing on site. This shall be submitted to the Landscape Architect. | NZTA P39:2013 - B5.1 | work plan | At least two weeks prior to the landscape works commencing | HP | ENG
18.01.02 | Landscaping Notice | The Contractor shall provide written notice to the Engineer, at least two working days prior to carrying out all activities detailed in Section B, Table1 of NZTA P39:2013 to enable the Engineer to inspect key works. | PS 25.1.3 | Notice | At least two working days prior to carrying out Landscaping | HP | ENG
18.01.03 | Planting | Should the need for planting arise, the preparation of planting, supply of plants, planting, staking (of trees if required), fertilizing and mulching of all plant material shall fully comply with Section G of NZTA P39:2013. | PS 25.8.1 | Checksheet | Each Planting Area | R | PE
18.01.04 | Reporting | Throughout the implementation of the works the contractor shall monitor the progress and condition of the works and provide a 3 monthly report. | NZTA P39:2013 - B3 | Report | 3 monthly report. | R | PE
18.01.05 | Plant Quality Samples | Two samples of each area planted will be inspected. For planting areas less than 2,000 m2 , the sample area will be a minimum 5% of the entire area. For planting areas larger than 2,000 m2 , the sample area will be a minimum of 2% of the entire area. | NZTA P39:2013 - B6.1 | Inspection Result | Two samples of each area | HP | ENG
18.01.06 | Grassed Surfaces Quality | Grassed surfaces shall be deemed in an acceptable condition when No ponding of surface water occurs (excluding stormwater assets) and Grass covers 95% of the grassed areas. | NZTA P39:2013 - B7 | Checksheet | Each Planting Area | I | PE
18.01.07 | Hydro-seeding Quality | Hydro-seeded grass surfaces shall be deemed in an acceptable condition when No ponding of surface water occurs (excluding stormwater assets) and Grass covers 95% of the grassed areas | NZTA P39:2013 - B8 | Checksheet | Each Planting Area | I | PE
18.01.08 | Inspections | The Contractor shall notify the Landscape Architect for inspection of the works as specified in P39 Table 1. | NZTA P39:2013 - B4 | Table 1 Checksheet | Each Planting Area | HP | ENG