## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-flat | C3 Bund Compound Upgrade |  |  |  |  | Yes | ITP T04 T06 Tank Upgrade T039/C1 - C3 Bund Compound Upgrade
checkpoint | 1. Issued For Construction Drawings
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | Acceptance Criteria - IFC drawings issued. Clear scope of work
label | Leading Hand - N/A
label | Supervisor - N/A
label | Third Party (state) - P - Worley’s project engineer
checkpoint | 2. Change Details
label | Applicable Documents - Details of design changes, Details of approved scope changes
checkpoint | 3. Waste Management/Disposal
label | Applicable Documents - CTS General Civil Construction Specification, CTS Containment Environmental Ground Soil Management plan RW-231
label | Acceptance Criteria - Waste Management methodology produced by civil contractor and confirmed by CTS Environment Department. All excavated contaminated material and concrete to be taken off site. To be taken to landfill.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Environmental team/ Client Representative
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4. Site survey and set out of levels.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Existing services located, marked, and protected if required.
label | ○ All works to be accordance with CTS Excavation works Specification.
label | ○ CTS General civil construction Specification
label | Leading Hand - P - Surveyor
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5. Demolition scope and removal of bitumen/grass/concrete from compound bund walls and prepare and shape.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspection areas inspection.
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Structures footings are not undermined.
label | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6. Demolition scope and removal of bitumen and concrete away from tank annular
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas.
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Tank annular is not undermined.
label | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7. Demolition scope and removal of bitumen and concrete from compound floor
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Structures footings are not undermined.
label | ○ Inspection once the bitumen/concrete has been removed prior to sand blinding.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 8. Subbase preparation under liner compound bund walls
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas.
label | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Existing services located, marked and protected if required.
label | ○ All works to be accordance with CTS Excavation works Specification.
label | ○ 50mm sand/cement bedding clean and free of debris
label | ○ Sand/cement placed to line and level.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9. Subbase preparation under liner around annular
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ CTS General Civil Construction Specification
label | ○ Site plan with inspected areas.
label | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Existing services located, marked, and protected if required.
label | ○ All works to be accordance with CTS Excavation works Specification.
label | ○ 50mm sand/cement bedding clean and free of debris
label | ○ Sand/cement placed to line and level.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10. Subbase preparation under liner over compound floor
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ CTS General Civil Construction Specification
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Existing services located, marked, and protected if required.
label | ○ All works to be accordance with CTS Excavation works Specification.
label | ○ 50mm sand/cement bedding clean and free of debris
label | ○ Sand/cement placed to line and level.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 11. Install subsoil drainage.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ CTS General Civil Construction Specification
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All levels and set outs as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Existing services located, marked and protected if required.
label | ○ All works to be accordance with CTS Excavation works Specification.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12. Install 1.5mm PE liner on Bund Walls.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
label | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
label | ○ Review installers QC documentation before placing Bidim
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 13. Install 1.5mm PE liner on tank shoulder.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
label | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
label | ○ Review installers QC documentation before placing Bidim
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 14. Install 2mm PE liner on compound floor.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - PE liner installed with Bidim A64 cloth T&B
label | ○ PE liner installed as per installers QA-QC and Worley’s QC requirements as per Civil /Struct Design pack 310449/C1 Rev A drawing notes T3084782 on IFC drawings issued 05 May 2023
label | ○ Review installers QC documentation before placing Bidim
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 15. Concrete pre-pour inspection Bund Walls
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ All works in accordance with CTS General Civil Construction Specification
label | ○ Concrete pre-pour check sheet completed and filed with ITP.
label | ○ General Civil Construction Specification
label | ○ Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104.
label | ○ Delivery dockets retained.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 16. Concrete pre-pour inspection Tank Shoulder
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ All works in accordance with CTS General Civil Construction Specification
label | ○ Concrete pre-pour check sheet completed and filed with ITP
label | ○ General Civil Construction Specification
label | ○ Concrete shall be high or special grade certified “ready mixed concrete” manufactured at a currently certified plant and shall comply with NZS 3104.
label | ○ Delivery dockets retained.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 17. Replace 50mm sand on top of HDPE liner followed by recovered in situ aggregate then 75mm AP40 aggregate.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ CTS General Civil Construction Specification
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ All works in accordance with CTS General Civil Construction Specification
label | ○ 50mm sand/cement bedding clean and free of debris
label | ○ All layers placed to line and level.
label | ○ Compound floor to be graded to allow free draining to lowest point.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - W - Civil Inspector
checkpoint | 18. Compound Flood Test
label | Applicable Documents - UCCL Compound C3 Flood test methodology, HSWA COP 47 ‘Secondary Containment’
label | Acceptance Criteria - Timing of the flood test will be conducted as per the approved Compound C3 Flood test methodology.
label | ○ All items on Compound Pre-Flood Check Sheet to be completed by relevant parties.
label | ○ The infiltration test will be as detailed in HSWA COP 47 ‘Secondary Containment
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Worley’s PE/ Representative
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 19. Sealing construction/expansion joints on tank annular
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Product manufactures specifications
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Seal manufactures specifications followed.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 20. Install Denso steel coat base protection or approved equivalent (Viscotaq) around tank annular
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Product manufactures specifications
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Viscotaq installed in accordance with manufacturers recommendations.
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 21. Sealing construction/expansion joints on bund walls
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Product manufactures specifications
label | ○ Site plan with inspected areas
label | Acceptance Criteria - All works carried out as per Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | ○ Site plan of area inspected to be signed off by Civil inspector after each inspection.
label | Leading Hand - N/A - Leading Hand
label | Supervisor - W - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Civil Inspector
checkpoint | 22. Complete final Civil inspection and close off ITP.
label | Applicable Documents - Civil /Struct Design pack 310449/C1 Rev A IFC drawings issued 05 May 2023
label | Acceptance Criteria - ITP / QC has been completed; all steps & hold points signed by relevant party.
label | ○ All work scope completed as per design pack and any field instructions issued during construction.
label | ○ Job site has been left tidy.
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R/H - Worley’s project engineer
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 23. Non-Conformance reporting
label | Applicable Documents - UCC internal NCR and or CTS Lucidity event NCR, CTS QC Requirements for Civil Works
label | Acceptance Criteria - In accordance with the approved Work Pack, drawing, Field Instruction and agreed scope of work.
label | ○ CTS General Civil Construction Specification
label | ○ CTS QC Requirements for Civil Works
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - H - Civil Inspector / Worley QC Coordinator
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 24. “As- Built” Information/Drawing
label | Applicable Documents - Section 9 CTS QC Requirements for Civil Works
label | Acceptance Criteria - CTS General Civil Construction Specification
label | ○ CTS QC Requirements for Civil Works
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Worley Project engineer
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 25. Reference info, specifications etc
label | Applicable Documents - Relevant sections of Controlled doc’s, Material specs (Epcon, coatings etc)
checkpoint | 26. Punch listing
label | Applicable Documents - Section 10 CTS QC Requirements for Civil Works
label | Acceptance Criteria - CTS QC Requirements for Civil Works
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R - Worley Project engineer
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 27. Compilation of inspection and test record
label | Applicable Documents - Signed off ITP & work pack, Section 7 and 8 UCC Producer Compliance Statement. These documents will be compiled to form a complete MDR/QC Pack.
label | Acceptance Criteria - CTS General Civil Construction Specification
label | ○ CTS QC Requirements for Civil Works
label | Leading Hand - N/A
label | Supervisor - H - UCCL Supervisor or Project Engineer
label | Third Party (state) - R/H - Worley Project engineer / QC Coordinator
holdpoint | AUTHORITY HOLDPOINT