## General
SECTION 1 – GENERAL DETAILS
Project Name: | Ōtaki to Levin Saftey Improvements | [5 empty] | Inspection Key |  | Responsibilities
Project Number: | 558010 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | 345084-NZ Transport Agency | [5 empty] | B | Report by Breach | CM | Construction Manager | Chris Colman | CC
Contract Number: | NZTA 6581 | [5 empty] | C | Check | ER | Engineers Representative | Luke Cameron | LC
Area/ Sub-System: | Ōtaki to Levin State Highway 1 |  |  | Lot ID Number: |  |  | D | Dimension Inspection | IP | Inspection Personnel
[7 empty] | E | Examine | MC | Material Controller
ITP Number: | O2L ITP 5 |  |  | Version: | 1 |  | H | Hold Point | OP | Operations Manager | Glen Flint | GF
ITP Description: | Covers all inspection points pre, during and post construction of the street light installation. | [5 empty] | I | Inspection | PM | Project Manager | Sam Christensen | SC
Discipline: | Lighting | [5 empty] | M | Monitor on Random Basis | PS | Project Supervisor | Richard Wild | RW
Specification: | Consultants Standard Technical Specifications TS1 NZTA M26 NZTA M30 | [5 empty] | O | Operation | QE | Quality Engineer
[7 empty] | R | Review | QM | QA Manager
Drawings: | For construction drawings : | [5 empty] | S | Subcontractor | SP | Supervisor | Richard Wild | RW
[7 empty] | V | Visual Verification | ST | Superintendent
Prepared By: | Sam Christensen |  |  | Date: | 2023-05-10 |  | W | Witness Point | SV | Surveyor | Andre Wilkes | AW
Quality Specified: | Project Technical Specifications cross referencing relevant to Transit New Zealand (TNZ) & NZTA Z8:2022 | [7 empty] | WS | Welding Supervisor
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: |  |  |  | Signature: |  |  |  |  | Date:
Downer Approval |  | Name: | Matt Erard |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:

## Item
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency |  | Inspection Type | Inspection
[8 empty] | Key | By | Checked (PM Initial) | Date
5.0 | Lighting | Final Sign Off | All below requirements are met and approved by CR | Referenced Item numbers as below | Once post construction |  | Hold Point | H | ER
5.1 | Technical Requirements
5.1.1 | Electrical Installation undertaken by qualified & "approved" technician | To be confirmed with Subcontractor prior | Relevant qualification documentation provided by sub-contractor. | Qualifying Documents | Once Per Source/Supplier |  | Review | R | PM
| Information to be provided by supplier |  | Information to be provided by supplier The following information shall be supplied with the quotation, if requested: (a) Fully detailed drawings showing a general arrangement, mounting height, outreach arm length, and base plate details, together with material specifications (including protective coating(s) where relevant), welding, fixing details, and construction tolerances. (b) Method of assembly of the sections and base including lifting and installation procedures. (c) Installation procedure including torque setting for holding down bolts and the maximum and minimum torque tolerance applicable. (d) Maintenance requirements for breakaway devices. (e) Confirmation of specified intended life and details of any recommended maintenance to achieve this. (f) A suitable compliance certificate, e.g. Producer Statement Design (PS1). This information may be lighting column type or wind zone specific and cover the general supply of the lighting columns. This generic information must be submitted initially by the supplier to the NZTA.
5.1.2 | Earthing | Inspection Post Install | Each pole to be separate installation, earthed using driven earth rod & M.E.N link - NZS3000 | Site Inspection Form | Once per pole installation |  | Witness Point | W | ER
5.1.3 | Testing and Commissioning | Completed Post Install | To be carried out in accordance with NZS3000 & NZTA M30 - Electrical test certificates for each lighting pole - Electrical Certificate of Compliance for the complete installation - As Built information - Completion Certificate (refer Appendix VI I of NZTA M30) - Any particular maintenance requirements (e.g., shear base poles) - Contractor to enter Ramm data for all installations | Relevant Documentation | Once per pole installation |  | Review | R | ER
5.1.4 | Poles and Luminaries | Documentation provided Pre-Construction | All lighting poles and luminaries to compley with NZTA M30, M26 & project technical specifications. | Manufacturers Certificates | Once Per Source/Supplier |  | Review | R | ER
5.2 | Construction
5.2.1 | Ducting & Cable Installation | Trench Inspection | Ducting to be installed as below where open trenching is possible - Required minimum thickness of separation 150mm - Minimum cover depth from crown of ducting 700mm - Type of ducting required - Orange PVC 100mm duct - Warning tape required over ducting minimum 300mm above duct | Site Inspection Form | Once per tench installation |  | Witness Point | W | ER
5.2.2 | Asbuilt of ducts | Survey Asbuilt | As-built location of ducting prior to backfilling as per design. | Suvey Records | Once per tench installation |  | Review | R | ER
5.2.3 | Trench Backfill | Density | Material is visually compact and tightly bound, and passes proof roll during subgrade inspection under ITP 2 Item 2.2.3 | Site Inspection Form | Once prior to subase placement |  | Witness Point | W | ER
5.2.4 | Pole & Luminaire Positioning | Check setout prior to installation | Poles to be located a minimum of 1m behind kerb/edge of seal & at right angles (90°) to kerb lines and lane markings. When poles are set in place they shall be vertical to within 1°. When each luminaire is installed it shall have the required tilt to within 2° The axis of the luminaire beam shall be in a vertical plane to within 2°. Columns shall be installed within +/- 100mm of the approved marked location both longitudinally and laterally. Height above finished ground level to ± 50mm of the manufacturer’s level. | Site Inspection Form | Once per pole installation |  | Inspection | I | PM/PS/ER
| Add Identification Marking (NZTA M26 2.4) |  | Identification Marking (NZTA M26 2.4) All lighting columns and outreach arms shall be clearly and durably marked with the following information: • Name, identifying mark or symbol of the manufacturer • Year of manufacture (or at least the last two digits of the year in which the marking was affixed) • Manufacturers model number or identification reference • Impact classification and performance class (F if passively safe/frangible, blank otherwise).
5.2.5 | Concrete | Compressive Strength | As per NZS 3112 - Concrete surrounding base to be minimum 20MPa at 28 days Columns shall be installed as per the manufacturer’s recommendations. | Compressive Strength Report | Once per days production |  | Review | R | ER
COMMENTS
[6 empty] | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: