## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | F2LSIP - ITP 05 - Lighting | itp |  |  |  |  | F2LSIP - ITP 05 - Lighting | 9a5fbbdd-2c65-4329-9179-9e5adbd10060
section | 5.0 - Lighting
checkpoint | Lighting
label | Inspection Point: Quality Control Activity - Final Sign Off
label | Acceptance Criteria - All below requirements are met and approved by CR
label | Verifying Document - Referenced Item numbers as below
label | Frequency - Once post construction
label | Inspection Type - Hold Point
label | Inspection: Key - H
label | Inspection: By - ER
holdpoint | AUTHORITY HOLDPOINT
section | 5.1 - Technical Requirements
checkpoint | 5.1.1 - Electrical Installation undertaken by qualified & "approved" technician / Information to be provided by supplier
label | Inspection Point: Quality Control Activity - To be confirmed with Subcontractor prior
label | Acceptance Criteria - Relevant qualification documentation provided by sub-contractor.
label | ○ Information to be provided by supplier
label | The following information shall be supplied with the quotation, if requested:
label | (a) Fully detailed drawings showing a general arrangement, mounting height, outreach arm length, and base plate details, together with material specifications (including protective coating(s) where relevant), welding, fixing details, and construction tolerances.
label | (b) Method of assembly of the sections and base including lifting and installation procedures.
label | (c) Installation procedure including torque setting for holding down bolts and the maximum and minimum torque tolerance applicable.
label | (d) Maintenance requirements for breakaway devices.
label | (e) Confirmation of specified intended life and details of any recommended maintenance to achieve this.
label | (f) A suitable compliance certificate, e.g. Producer Statement Design (PS1).
label | This information may be lighting column type or wind zone specific and cover the general supply of the lighting columns. This generic information must be submitted initially by the supplier to the NZTA.
label | Verifying Document - Qualifying Documents
label | Frequency - Once Per Source/Supplier
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - PM
checkpoint | 5.1.2 - Earthing
label | Inspection Point: Quality Control Activity - Inspection Post Install
label | Acceptance Criteria - Each pole to be separate installation, earthed using driven earth rod & M.E.N link - NZS3000
label | Verifying Document - Site Inspection Form
label | Frequency - Once per pole installation
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.1.3 - Testing and Commissioning
label | Inspection Point: Quality Control Activity - Completed Post Install
label | Acceptance Criteria - To be carried out in accordance with NZS3000 & NZTA M30
label | ○ Electrical test certificates for each lighting pole
label | ○ Electrical Certificate of Compliance for the complete installation
label | ○ As Built information
label | ○ Completion Certificate (refer Appendix VI I of NZTA M30)
label | ○ Any particular maintenance requirements (e.g., shear base poles)
label | ○ Contractor to enter Ramm data for all installations
label | Verifying Document - Relevant Documentation
label | Frequency - Once per pole installation
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
checkpoint | 5.1.4 - Poles and Luminaries
label | Inspection Point: Quality Control Activity - Documentation provided Pre-Construction
label | Acceptance Criteria - All lighting poles and luminaries to compley with NZTA M30, M26 & project technical specifications.
label | Verifying Document - Manufacturers Certificates
label | Frequency - Once Per Source/Supplier
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
section | 5.2 - Construction
checkpoint | 5.2.1 - Ducting & Cable Installation
label | Inspection Point: Quality Control Activity - Trench Inspection
label | Acceptance Criteria - Ducting to be installed as below where open trenching is possible
label | ○ Required minimum thickness of separation 150mm
label | ○ Minimum cover depth from crown of ducting 700mm
label | ○ Type of ducting required - Orange PVC 100mm duct
label | ○ Warning tape required over ducting minimum 300mm above duct
label | Verifying Document - Site Inspection Form
label | Frequency - Once per tench installation
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.2.2 - Asbuilt of ducts
label | Inspection Point: Quality Control Activity - Survey Asbuilt
label | Acceptance Criteria - As-built location of ducting prior to backfilling as per design.
label | Verifying Document - Suvey Records
label | Frequency - Once per tench installation
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER
checkpoint | 5.2.3 - Trench Backfill
label | Inspection Point: Quality Control Activity - Density
label | Acceptance Criteria - Material is visually compact and tightly bound, and passes proof roll during subgrade inspection under ITP 2 Item 2.2.3
label | Verifying Document - Site Inspection Form
label | Frequency - Once prior to subase placement
label | Inspection Type - Witness Point
label | Inspection: Key - W
label | Inspection: By - ER
checkpoint | 5.2.4 - Pole & Luminaire Positioning / Add Identification Marking (NZTA M26 2.4)
label | Inspection Point: Quality Control Activity - Check setout prior to installation
label | Acceptance Criteria - Poles to be located a minimum of 1m behind kerb/edge of seal & at right angles (90°) to kerb lines and lane markings.
label | ○ When poles are set in place they shall be vertical to within 1°.
label | ○ When each luminaire is installed it shall have the required tilt to within 2°
label | ○ The axis of the luminaire beam shall be in a vertical plane to within 2°.
label | ○ Columns shall be installed within +/- 100mm of the approved marked location both longitudinally and laterally. Height above finished ground level to ± 50mm of the manufacturer’s level.
label | Identification Marking (NZTA M26 2.4)
label | All lighting columns and outreach arms shall be clearly and durably marked with the following information:
label | ○ Name, identifying mark or symbol of the manufacturer
label | ○ Year of manufacture (or at least the last two digits of the year in which the marking was affixed)
label | ○ Manufacturers model number or identification reference
label | ○ Impact classification and performance class (F if passively safe/frangible, blank otherwise).
label | Verifying Document - Site Inspection Form
label | Frequency - Once per pole installation
label | Inspection Type - Inspection
label | Inspection: Key - I
label | Inspection: By - PM/PS/ER
checkpoint | 5.2.5 - Concrete
label | Inspection Point: Quality Control Activity - Compressive Strength
label | Acceptance Criteria - As per NZS 3112 - Concrete surrounding base to be minimum 20MPa at 28 days. Columns shall be installed as per the manufacturer’s recommendations.
label | Verifying Document - Compressive Strength Report
label | Frequency - Once per days production
label | Inspection Type - Review
label | Inspection: Key - R
label | Inspection: By - ER