## 062 Construction MSBs
Main Switchboards on Construction Sites
Nominate Equipment or Works associated with this ITC | [13 empty] | Page 1 of 2
ITP No : |  |  |  | ITP Item No: |  | 3.49 |  | Job No: |  |  | Area:
Dwg No:
Function | [11 empty] | OK | N/A | NCR raised
No | Confirm following items comply with requirements | [12 empty] | Major | Minor
Check that the Switchboard:
1 | AS 3012:2019 - 2.3.1.1 - Switchboard is legibly and indelibly marked to identify the source of supply from which it originates. (min 6mm letters)
2 | AS 3012:2019 - 2.3.1.1 - The switchboard shall be readily accessible and protected from damage.
3 | AS 3012:2019 - 2.3.2.1 (a & b) - The switchboard shall be of robust construction with a minimum IP 23 rating.
4 | AS 3012:2019 - 2.3.2.1 (c) - Live parts are eﬀectively protected at all times against contact by personnel operating equipment located on the switchboard, including the connection or disconnection of plugs to socket-outlets.
5 | AS 3012:2019 - 2.3.2.1 (c) - All penetrations are closed oﬀ, with propriety fittings, i.e. bungs & lock rings for unused penetrations and pole fillers for unused circuit breaker poles.
6 | AS 3012:2019 - 2.3.2.1 (e) (i) - The door or lid requires the use of tool for removal.
7 | AS 3012:2019 - 2.3.2.1 (e) (ii) - The door or lid is fitted with a facility for locking.
8 | AS 3012:2019 - 2.3.2.1 (f) - Switchboard is clearly labelled to distinguish one board from another. (by means of numbers, letters or both)
9 | AS 3012:2019 - 2.3.2.1 (g) - Switchboards is marked in accordance with appendix C to indicate presence of live parts.
An electric shock risk sign is displayed in locations where additional attention is required in the removal of covers, e.g. covers for switchboards or cable junctions.
A danger sign with an additional message indicating the presence of live parts within, is conspicuously displayed on the enclosure.
10 | AS 3012:2019 - 2.3.3 - Switchboard is securely fixed in position, attached to a pole, post, wall, floor. (if it is not fixed down for any reason the board should not be in service)
11 | AS 3012:2019 - 2.4.1 - Switchboard has one isolation switch marked in accordance with clause 2.4.3. (6mm Text) ‘MAIN SWITCH’ and confirm switch interrupts supply to all downstream circuits.
12 | AS 3012:2019 - 2.4.2 - Isolating switches are lockable or located within a lockable enclosure
13 | Current single line drawing is readily available within the switchboard
Nominate Equipment or Works associated with this ITC | [13 empty] | Page 2 of 2
ITP No : |  | 0 |  | ITP Item No: |  | 3.49 |  | Job No: |  | 0 | Area: | 0
Dwg No: |  | 0
Function | [11 empty] | OK | N/A | NCR raised
No | Confirm following items comply with requirements | [12 empty] | Major | Minor
14 | Switchboards have signage attached with correct Q Electrical site contact details
15 | Switchboards have up to date schedules and are correctly labelled
16 | All conduit entries into Switchboard have adaptors fitted and glued
17 | All cables are correctly glanded into the switchboard
18 | All spare penetrations are eﬀectively sealed by use of a propriety fitting e.g. screwed bung and lock ring.
19 | Check cubicle has been cleaned of all rubbish, dust, filings, tools, etc.
20 | Check all cable terminations and Bus bar connections are secured correctly & tensioned. Refence Documents:
| Item or Part |  |  |  |  | Torque Setting |  |  |  | Initial
Record Serial No and Calibration Date of all IMTE used : |  |  |  |  | Model |  |  |  | Serial No. |  |  | Calibration Date
Associated documents:
Comments
Minor NCR's raised |  |  |  | YES | NO |  | N/A | Have all NCR's been finalised ?
[8 empty] | YES |  |  | NO |  |  | N/A
Major NCR's raised |  |  |  | YES | NO |  | N/A
Accepted By |  |  | Name (Print) |  | Signature |  |  |  | Position |  |  | Date
Q Electrical
PM Review
Client (If Applicable)