## 064 Construction Wiring
Wiring and Installation of Accessories (Sub-Circuits) on Construction Sites
Nominate Equipment or Works associated with this ITC
ITP No : |  |  | ITP Item No: |  | 3.46 |  | Job No: |  | Task Lot
Dwg No:
Function | [9 empty] | OK | NA | NCR raised
Confirm following items comply with requirements | [11 empty] | Major | Minor
No | Check that the accessories :
1 | Are the correct type :
Reference Document:
2 | Are located in the correct position :
Reference Document:
3 | Are securely fitted and field equipment and cabling is clearly labelled
4 | Are fitted in accordance with manufacturers recommendation :
5 | AS 3012:2019 - 2.5.2 - Check wiring is not tied, bundled or grouped with permanent wiring; nor attached to free-standing fencing.
6 | AS 3012:2019 - 2.5.3 - Check wiring is mechanically protected in accordance with previously conducted risk assessment. (QA_TEM_057_Construction Wiring Risk Assessment) Or not less than; (a) medium duty rigid or corrugated conduit of insulating material; (b) heavy-duty rigid or corrugated conduit of insulating material; (c) flexible electrical hose; (d) armoured cable; or (e) other means that provide equivalent protection against mechanical damage.
7 | AS 3012:2019 - 2.5.4 - Construction wiring is readily distinguishable from permanent wiring by using cable sheath of a diﬀerent colour or by attaching iridescent yellow tape spaced at intervals not exceeding 5m and marked with the words "CONSTRUCTION WIRING"
8 | AS 3012:2019 - 2.5.4 - If live permanent wiring is located where construction wiring is occurring, or its location, check that it be marked with the words "LIVE WIRING" at interval not exceeding 5m.
9 | Confirm all Field wiring to Isolators, Socket outlets and point off supply has been terminated correctly
Associated documents:
Comments
Minor NCR's raised |  |  | YES | NO |  | N/A | Have all NCR's been finalised ?
[7 empty] | YES |  | NO |  |  | N/A
Major NCR's raised |  |  | YES | NO |  | N/A
Accepted By |  | Name (Print) |  | Signature |  |  |  | Position |  | Date
Q Electrical
PM Review
Client (If Applicable)