## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | CRL-ITR-010 - Crack Unit Installation |  |  |  |  | Yes | CRL-ITR-010 - Crack Unit Installation | 1681b2f6-cc11-443d-919e-ddb5b4e71636
section | Crack Unit
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Unit Model
textbox | Model Number
textbox | Serial Number
checkpoint | Check for Damage
checkpoint | Verify Floor is Level
checkpoint | Confirm Fixings as per detail (Seismic)
textbox | Drawing Reference Number
section | Crack Second Fix QA
checkpoint | Potable Water connected (by others)
checkpoint | Filters Installed – Check Clearances
checkpoint | Door Clearance checked
checkpoint | Drains Installed – Run to Tundish by Others
checkpoint | Shipping mounts removed
checkpoint | Label to be installed
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist | CRL-ITR-002 - Fire Dampers |  |  |  |  | Yes | CRL-ITR-002 - Fire Dampers | 1e39f4ac-1012-4c63-80a6-cc0f230b32c7
section | First Fix QA
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Penetration formed correctly
checkpoint | Correct FD Installed & correct orientation
section | Second Fix QA
checkpoint | Access Panel installed
checkpoint | Drop Tested
checkpoint | Track is Clear
checkpoint | All angles correctly fixed
checkpoint | Label to be installed
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist-flat | CRL-ITR-021 - Metal Cladding |  |  |  |  | Yes | CRL-ITR-021 - Metal Cladding | 3985b1fb-aded-4b5b-8a99-10d38c1271e5
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Clad pipework as per drawing
checkpoint | Approved materials have been used
checkpoint | Pipework cladding installation complete and tidy. Check straps, sealant and removable sections
checkpoint | Penetraitons are sealed for gauges, instruments, and drain vents (silicone)
checkpoint | Confirm cladding is free of damages
checklist | CRL-ITR-005 - Fan Coil Units |  |  |  |  | Yes | CRL-ITR-005 - Fan Coil Units | 3b5b0c67-e589-4a84-956a-4494334b5791
section | Unit First Fix QA
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Unit Installed
textbox | Model Number
textbox | Serial Number
checkpoint | u/s of Unit at correct height
checkpoint | Correct mountings / Springs Installed
section | Unit Second Fix QA
checkpoint | Unit Plenum Boxes to be installed
checkpoint | Filters installed & clearence checked
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
checkpoint | P - trap installed if required
checkpoint | Driptray installed if required
checkpoint | Condensate Drains installed
checkpoint | Correct Fall to tundish , and water flow tested
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist-flat | CRL-ITR-009 - Chillers Installation |  |  |  |  | Yes | CRL-ITR-009 - Chillers Installation | 3f3fda41-8da8-47be-a79e-3d3ae14cf971
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed
textbox | Model Number
textbox | Serial Number
checkpoint | Setting out point correct
checkpoint | Corrrect Mounting Springs installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
checklist-flat | CRL-ITR-006 - Chilled Water Pipe Systems |  |  |  |  | Yes | CRL-ITR-006 - Chilled Water Pipe Systems | 479364f1-e9dc-4a4f-8c20-dd82f195c496
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Pipework installed as per Drawing
textbox | Installation done by
checkpoint | Valve arrangement installed as per schematic
checkpoint | Insulation blocks installed where required
checkpoint | Correct hanger spacing
checkpoint | Drains installed at low points
textbox | Air vents installed at all high points
checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint | The correct coupling has been used for the correct joint i.e flexible or rigid
checkpoint | Visual indicators verified - Positive overlap - Joint Square
checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint | Pipework Seismic to be installed
textbox | Drawing Reference Number
checklist-flat | CRL-ITR-003 - Mechanical Board (MSSB) |  |  |  |  | Yes | CRL-ITR-003 - Mechanical Board (MSSB) | 4991d906-3871-451c-bc64-40524ddaf55a
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Equipment / plant installed
checkpoint | Switch Board Mounted in correct position and level
checkpoint | Switch Board terminations complete
checkpoint | Board Tested
checkpoint | COC's Complete
checkpoint | Label to be installed
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist-flat | CRL-ITR-020 - Fire Rated Duct Insulation |  |  |  |  | Yes | CRL-ITR-020 - Fire Rated Duct Insulation | 4adf8ef0-0d22-4096-a20e-9fe3ba6f5e6f
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Insulate ducting as per drawing and specifications
checkpoint | Ensure all wraps are complete and no gaps ensure
checkpoint | Confirm all joints installed correctly with suitable overlaps
checkpoint | Pins and banding correctly applied
checkpoint | Maxilite board to wall complete and sealed.
checkpoint | Confirm second layer length has been installed as per specification from wall.
checkpoint | Access Panels installed correctly. Confirm fixings, sealant and alignment with internal panel.
checkpoint | Confirm insulation is free of damages
checklist | CRL-ITR-004 - Fans |  |  |  |  | Yes | CRL-ITR-004 - Fans | 4d627d76-e704-4600-befb-ee5c18078785
section | Fans
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Equipment / plant installed
textbox | Model Number
textbox | Serial Number
checkpoint | Correct mountings / springs installed
checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist | CRL-ITR-013 - Radiant Heaters |  |  |  |  | Yes | CRL-ITR-013 - Radiant Heaters | 6763602d-b449-40cd-8974-69fa2b41fe77
section | Radiant Heaters
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Equipment / plant installed
textbox | Model Number
textbox | Serial Number
checkpoint | U/S of Equipemnt heights correct as per Workshop Drawings.
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist-flat | CRL-ITR-017 - CHW Insulation |  |  |  |  | Yes | CRL-ITR-017 - CHW Insulation | 7299ea09-fcaa-4caf-9f3a-ee67be57a2fd
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint | Insulation is glued and taped correctly
checkpoint | Confirm insulation is free of damages
checklist-flat | CRL-ITR-018 - Condensate Insulation |  |  |  |  | Yes | CRL-ITR-018 - Condensate Insulation | 75cc0929-776c-4e1f-8e13-efde724dbbef
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint | Condensate pipework insulated correctly
checkpoint | Confirm insulation is free of damages
checklist-flat | CRL-ITR-015 - Cowls |  |  |  |  | Yes | CRL-ITR-015 - Cowls | 98da1882-c84a-4314-9e63-64008dc2b2b9
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Outside Air Roof Cowl Installed
checkpoint | Builder - Waterproof and Seal to be installed
checklist | CRL-ITR-008 - AHU Installation |  |  |  |  | Yes | CRL-ITR-008 - AHU Installation | a81305a7-b0d7-48a3-8806-457907e7267a
section | AHU's
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Check plinth size and location
checkpoint | Correct Unit Installed
textbox | Model Number
textbox | Serial Number
checkpoint | Condensate Piping installed
checkpoint | Unit correctly anchored
textbox | Drawing Reference Number
section | Unit Second Fix QA
checkpoint | Filters Installed
checkpoint | Label to be installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist | CRL-ITR-001 - Mechanical Duct |  |  |  |  | Yes | CRL-ITR-001 - Mechanical Duct | a9de3f00-764a-4d78-acaa-16e97654b8a6
section | First Fix QA
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint | Duct Hangers (is spacing correct, installed level , rods trimmed back etc)
checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint | Orientation of dampers and equipment to be installed correct way
checkpoint | Access Panels to be installed as per drawing
section | Second Fix QA
checkpoint | All volume control dampers set fully open.
checkpoint | Seismic bracing installed as per Drawing
textbox | Drawing Reference Number
checkpoint | Flexibles installed and supported correctly
section | Fit Off QA
checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checkpoint | Restrained correctly
checkpoint | Flexible connection fixed correctly to grill box
checklist-flat | CRL-ITR-011 - Pump Installation |  |  |  |  | Yes | CRL-ITR-011 - Pump Installation | d338dfb0-7fc5-49e9-8be7-e66350240a9b
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Check if plinth site is correct
checkpoint | Correct Unit Installed
checkpoint | Setting out point correct
checkpoint | Corrrect Mounting Springs installed
textbox | Drawing Reference Number
checkpoint | Label to be installed
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details
checklist-flat | CRL-ITR-019 - External Duct Work Insulation |  |  |  |  | Yes | CRL-ITR-019 - External Duct Work Insulation | f0b3b5e6-81f8-4d55-9043-bf22f3afbeb7
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Insulate ducting as per drawing and specifications
checkpoint | Provide 50mm over lapping at all joints.
checkpoint | Confirm pins are installed and spacing is correct
checkpoint | Confirm bands at 600mm centres.
checkpoint | Confirm all overlaps and joints are complete
checkpoint | Confirm insulation is free of damages
checklist | CRL-ITR-016 - DX Units |  |  |  |  | Yes | CRL-ITR-016 - DX Units | fae97e9a-2e24-410e-826d-a3dcad9a786f
section | DX Units
checkpoint | Pre-check equipment for damage prior to installation
checkpoint | Correct Unit Installed
textbox | Model Number
textbox | Serial Number
checkpoint | Out door Unit Installed
checkpoint | u/s of Unit at correct height
checkpoint | Refrigeration Pipework installed as per drawings
textbox | Installation done by
checkpoint | Pipework Installed from DX unit box to Outdoor unit
note | Schematic markups drawings
checkpoint | Condensate Piping installed
checkpoint | Pressure Tested
checkpoint | Signed off By AE Smith
textbox | Name of person
textbox | Date
checkpoint | Photo's of Pressure test
textbox | Start of Pressure test
textbox | Time / Date
textbox | Pressure test after recored Duration
textbox | Time / Date
checkpoint | Triple Evacuation procedure to be done.Final below 500 Microns
checkpoint | Refrigeration (Scale) charge unit completed - According to Calculation for Pipe Size & Length
checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint | Seismic Bracing Installed
textbox | Drawing Reference Number
section | Unit Second Fix QA
checkpoint | Filters Installed
section | E4M QA
checkpoint | Electrical Isolators installed in correct location
checkpoint | Units Terminated
checkpoint | Units Tested and Running
checkpoint | Location
textbox | Add details
checkpoint | Level
textbox | Add details
checkpoint | Room Number
textbox | Add details
checkpoint | BIM Tag ID #
textbox | Add details
checkpoint | Asset #
textbox | Add details
checkpoint | Serial #
textbox | Add details