## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Sprinkler Rough In | [5 empty] | ITC 301 - Sprinkler Installation - Rough In High Level
section | Details
checkpoint | 1. Drg No / Revision
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Supports spacing & fixing as per code
checkpoint | 3. Pipework installed as per drg
checkpoint | 4. Concealed space sprinklers installed
checkpoint | 5. All ends blanked off/plugged for testing
checkpoint | 6. Pipes left out as noted below
checkpoint | 7. Flexibles installed
checkpoint | 8. Seismic Bracing Installed if required.
checkpoint | 9. Charge hand Inspection
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Sprinkler | [5 empty] | ITC 302 - Sprinkler Installation - Below Ceiling Fit-off
section | Details
checkpoint | 1. Drg No / Revision
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Ceiling grid levelled
checkpoint | 3. Sprinklers installed as per drg
checkpoint | 4. All escutcheon plates installed
checkpoint | 5. Areas not fitted-off as noted below
checkpoint | 6. Pressure Tested (refer I&TR 401)
checkpoint | 7. Charge hand inspection
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Hydrant | [5 empty] | ITC 303 - Hydrant Installation - Hydrant / Hose Reel Install & Fit Off
section | Details
checkpoint | 1. Drg No / Revision
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Supports spacing & fixing as per code
checkpoint | 3. Pipework installed as per drg
checkpoint | 4. Seismic Bracing Installed if required.
checkpoint | 5. Pipes left out as notes & reason
checkpoint | 6. Hyd valve installed at correct height
checkpoint | 7. Hosereel installed at correct height
checkpoint | 8. Signage & labelling installed
checkpoint | 9. Hydrant valves locked open
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | SCV | [5 empty] | ITC 304 - Sprinkler Control Valve Installation
section | Details
checkpoint | Sprinkler Rough-In completed
checkpoint | 1. Monitored Alarm Valve Operated
checkpoint | 2. Solenoid Valve Operated
checkpoint | 3. Flow Switch Operated
checkpoint | 4. Run Remote Test Drain
checkpoint | 5. Installation Pressure Switch Operated
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Smoke Signals Sign Off
textbox | Checked By:
textbox | Date:
checklist | Test | [5 empty] | ITC 401 - Sprinkler Hydrostatic Pressure Test
section | Guidelines
checkpoint | Guidelines acknowledged
label | Air - 50Kpa for 30mins.
label | Water - “1400 kPa for 2 hours” with no pressure loss.
label | Note - 1400 kPa will be the maximum tested pressure
section | Air Test
checkpoint | First Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
checkpoint | Second Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
section | Rough In
checkpoint | First Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
checkpoint | Second Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
section | Fit Off
checkpoint | First Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
checkpoint | Second Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
checklist | Test | [5 empty] | ITC 402 - Hydrant Hydrostatic Pressure Test
section | Guidelines
checkpoint | Guidelines acknowledged
label | AIR - 50Kpa for 30mins
label | WATER - “1700 kPa for 2 hours” with no pressure loss.
label | # 1700 kPa will be the maximum tested pressure or
label | 1.5 TIMES THE HIGHEST HYDRANT IF GREATER – i.e 700Kpa + 350Kpa = 1050Kpa + RL DIFFERENCE GREATER THAN 65m (650Kpa) = <1700kPA
section | Air Test
checkpoint | First Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
checkpoint | Second Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
section | Water Test
checkpoint | First Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
checkpoint | Second Sighting
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
section | Water Test if Required
checkpoint | First Sighting if Required
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
checkpoint | Second Sighting if Required
date | Date:
textbox | Time:
textbox | Pressure:
textbox | Witness (Contractfire):
textbox | Witness (Lend Lease):
checklist | Extinguisher | [5 empty] | ITC 501 - Fire Extinguisher Installation
section | Details
checkpoint | 1. Drawing revision correct
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Installation locations as per drawing.
checkpoint | 3. Correct unit type
checkpoint | 4. Correct unit height & clearances
checkpoint | 5. Extinguisher tagged
checkpoint | 6. Extinguisher description type signage installed to AS.2444
checkpoint | 7. Location signage installed to AS.2444
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Diesel Pump Installation / Commissioning | [5 empty] | ITC 601 - Diesel Pump Installation / Commissioning
section | Details
checkpoint | 1. Pump room drawing revision correct
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Piping as per installation
checkpoint | 3. All Drains connected.
checkpoint | 4. Diesel fuel tank filled.
checkpoint | 5. Power available from electrical contractor & approved for use.
checkpoint | 6. Pump performance site test results Diesel S1
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | 7. Pump performance site test results Diesel S2
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | 8. Manufacturers site commissioning results attached as an appendix.
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Electric Pump Installation / Commissioning | [5 empty] | ITC 601 - Electric Pump Installation / Commissioning
section | Details
checkpoint | 1. Pump room drawing revision correct.
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Piping as per installation.
checkpoint | 3. All drains connected.
checkpoint | 4. Power available from electrical contractor & approved for use.
checkpoint | 5. Pump performance site test results Elec S1
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | 6. Pump performance site test results Elec S2
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | 7. Manufacturers site commissioning results attached as an appendix.
label | * Flow Test & Commissioning results attached as an appendix.
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Tank Installation / Commissioning | [5 empty] | ITC 602 - Tank Installation / Commissioning
section | Details
checkpoint | 1. Approved shop drawing revision.
textbox | Drawing No.
textbox | Revision No.
checkpoint | 2. Visual Inspection of installation confirming correct location.
checkpoint | 3. Access ladder and Hatch Installed and accessible.
checkpoint | 4. Level Indicators Installed.
checkpoint | 5. Tank Drain installed in correct location and is sized correctly.
checkpoint | 8. Tank Overflow installed in correct location and is sized correctly.
checkpoint | 9. Tank Suction installed in correct location and is sized correctly.
checkpoint | 10. Tank Infill installed in correct location and is sized correctly.
checkpoint | 11. Tank Top up installed in correct location and is sized correctly.
checkpoint | 12. Tank Man Hole installed in correct location and is sized correctly.
checkpoint | 13. All relevant pipework has been connected to the tank.
checkpoint | 14. Tank Number and Capacity labeling installed.
checkpoint | 15. Ensure Drains have been connected by Hydraulics contractor and capable of taking the volume of water if tank needs to be drained.
checkpoint | 16. Fill Tank to a level just above the tank drain and wait 2hrs before continuing if no leaks.
checkpoint | 17. Fill Tank to a level just above the Suction line and wait 2hrs before continuing if no leaks.
checkpoint | 18. Visual Inspection of installation confirming no leaks, movement or distortion before next filling.
checkpoint | 19. Fill Tank to a level just above the top of the first panel and wait 2hrs before continuing if no leaks.
checkpoint | 20. Fill Tank to a level just above the top of the second panel and wait 2hrs before continuing if no leaks.
checkpoint | 21. Visual Inspection of installation confirming no leaks, movement or distortion before next filling.
checkpoint | 22. Fill Tank to the capacity level.
checkpoint | 23. Ensure Infill line ball float valve is adjusted correctly.
checkpoint | 24. Ensure Top up line ball float valve is adjusted correctly.
checkpoint | 25. Visual Inspection of installation confirming no leaks, movement or distortion.
checkpoint | 26. Inspect tank for each day for the next 2 days concurrently to ensure that there is no leaks, movement or distortion.
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Booster Installation | [5 empty] | ITC 701 - Booster Installation
section | Details
checkpoint | 1. Installed as per drawing
checkpoint | 2. Drawing revision
checkpoint | 3. MFB required clearance confirmed
checkpoint | 4. Labelling per stage & level provided
checkpoint | 5. Isolations valves closed & locked
checkpoint | 6. Pressure gauges at T.M pressure
checkpoint | 7. Storz couplings installed to suction points
checkpoint | 8. Hydrostatic Test Completed (1700 kpa)
checkpoint | 9. Independent Certification
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date:
checklist | Project Completion/Certification | [5 empty] | ITC 801 - Project Completion/Certification Checklist
section | Details
checkpoint | 1. Hydrant Independent Certification
checkpoint | 2. Sprinkler Independent Certification
checkpoint | 3. Contractfire Completion Statement
checkpoint | 4. Contractfire Warranty Statement
checkpoint | 5. Operation & Maintenance Manuals
checkpoint | 6. Quality Assurance Documentation
checkpoint | 7. As Installed Documentation
checkpoint | 8. Testing & Maintenance Commences
checkpoint | Contractfire Sign Off
textbox | Checked By:
textbox | Date:
checkpoint | Lend Lease Sign Off
textbox | Checked By:
textbox | Date: