## Cladding Template
INSPECTION AND TEST PLAN
SITE INSTALLTION | [7 empty] | ITP No. |  |  | Revision No. | REV02
ITP Name | Site Installation CLG-506 deflection head |  | Elevation or Area : Lower Ground patient drop off
Project | New Footscray Hospital |  | Module. No or Item : CLG-506 deflection head
Building Ref. | Building A/B lower ground patient drop off |  |  |  | Refer to O&M Manual for Project for maintneance and care proceedures for cladding types
Check / Inspection Required |  | Responsibility | Acceptance Criteria |  | Reference Document / IFC Shop Drawing Number AS1562.1-2018 | Frequency of Testing and Inspections | Client | Date | Facadex | Date | Comments
IFC Shop Drawings Approved |  | MPX | MPX / Architect Sign Off
Material Approval |  | MPX | MPX / Architect Sign Off
Materials (Deflection head/Bolts/Washers) delivered to site free of damage and deformation |  | Facadex | Facadex sign off.
Grid lines established and site set out complete |  | Facadex | Facadex sign off.
Deflection head installed as per shop details and location |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
Correct size of deflection head has been installed to allow enough depth to outcome the tolerance of the slab. |  | Facadex
Ensure the deflection head installed was not bended or deformed. |  | Facadex
Connections (bolts/washers/screws) checked for damages |  | Facadex | Facadex sign off.
HOLD POINT- All Criteria above must be signed off before proceeding
Client inspection of installed product with Facadex representative. Any sighted defects (incurred during installation) to be recorded and subcontractor to be notified within 24 hours of installation. |  | Facadex / Builder | Defect notification via email or chosen coorespondece
Evidence of close out / rectification
(SI / Photographic record & evidence of close out to be attached to this ITP for each wall type)
Sign of only once agreed that wall is defect free
AUTHORITY TO PROCEED
Foreman – Checklist Completed |  |  |  | Date / Time
Coordinator – Checklist Completed |  |  |  | Date / Time
In signing the above the Facadex Construction and Named parties are confirming that all works have been completed in accordance with all the relevant Design Documentation & Specifications.
Facadex Construction located at 13-14 Adams Court Sunshine West, VIC 3020