## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP - Stormwater (Structures) - 202 - Rev B | itp |  |  |  |  | ITP - Stormwater (Structures) - 202 - Rev B
section | 1.01 Stormwater Aggregate Materials
checkpoint | 1.01.1 - Controlled Low Strength Materials - CLSM
label | Acceptance / Conformance Criteria - The use of CLSM by the Contractor will require approval from the Engineer on a case-by-case basis.
label | Standard / Specification - PS 16.8.1, PS 16.37
label | Verifying Document - Engineers Approval
label | Frequency - An application submitted to the Engineer for approval, to use CLSM.
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.01.2 - AP65 Aggregate
label | Acceptance / Conformance Criteria - AP 65 Aggregate is to be a crushed product with a maximum granule size of 65mm and be a graded, clean durable aggregate which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
label | Standard / Specification - PS 16.8.2.1, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.01.3 - AP40 Aggregate
label | Acceptance / Conformance Criteria - AP 40 aggregate is to be a crushed product with a maximum granule size of 40mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requitements
label | Standard / Specification - PS 16.8.2.2, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.01.4 - AP20 Aggregate
label | Acceptance / Conformance Criteria - AP 20 aggregate is to be a crushed product with a maximum granule size of 20mm and be a graded, clean, durable aggregate and which meets Grading, Linear Shrinkage, Weathering Index, Crushing resistance, Maximum and Minimum Dry Densities requirements
label | Standard / Specification - PS 16.8.2.3, PS 16.9.1.2, PS 16.6, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.01.6 - Alternative Bedding
label | Acceptance / Conformance Criteria - If the Contractor wishes to propose a different material from that specified in this section, the Contractor shall submit to the Engineer
label | Standard / Specification - PS 16.9.2.1, PS 16.9.1.2, PS 16.37
label | Verifying Document - Statement from the concrete pipe supplier
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.01.7 - Overlay Zone Material (for concrete pipes)
label | Acceptance / Conformance Criteria - Materials for the overlay zone GAP 20 shall be used which has been tested for Grading, Weathering Index, Crushing Index
label | Standard / Specification - PS 16.9.2.2, PS 16.37
label | Verifying Document - IANZ Lab Reports
label | Frequency - Submitted to Engineer for approval
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 1.02 Stormwater Pipe Materials
checkpoint | 1.02.2 - Steel Work
label | Acceptance / Conformance Criteria - Unless otherwise specified, all steel work shall be fabricated from mild steel conforming to the requirements of AS/NZS 3679.1:2010 and AS/NZS 4680:2006. All cut surfaces shall be protected with a corrosion protection coating i.e., zinc rich paint.
label | Standard / Specification - PS 16.8.1, PS 16.8.4
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.02.4 - Steel Fitting Corrosion Protection
label | Acceptance / Conformance Criteria - Steel fittings shall be shop assembled as large as practicable before hot dip galvanising or zinc metal spray to AS/NZS 2312.2:2014 and AS/NZS 4680:2006, to minimise the number of field welds and bolted joints required.
label | Standard / Specification - PS 16.8.4.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.02.5 - Hot Dip Galvanised
label | Acceptance / Conformance Criteria - All ferrous metalwork except standard galvanised pipe shall be hot dip galvanised to HDG900 unless otherwise specified.
label | Standard / Specification - PS 16.8.4.1
label | Verifying Document - Datasheet / Cert
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.02.6 - Fastenings
label | Acceptance / Conformance Criteria - All fastenings associated with manholes or drainage structures shall be either hot dipped galvanised or stainless steel. Zinc Plated fastenings shall not be permitted
label | Standard / Specification - PS 16.8.4.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.02.7 - Concrete pipes and fittings
label | Acceptance / Conformance Criteria - Concrete pipes and fittings shall comply with the requirements of AS/NZS 4058:2007 for concrete pipes
label | Standard / Specification - PS 16.9.1.1, PS 16.37
label | Verifying Document - Datasheets
label | Frequency - Prior to use
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
checkpoint | 1.02.8 - Quality of Pipe and Precast Units
label | Acceptance / Conformance Criteria - IANZ Accredited Manufacturers certificate to NZTA F/3 (refer to Appendix F)
label | Standard / Specification - PS 16.34
label | Frequency - For every pipeline delivered (as soon as they are delivered)
section | 1.03 Stormwater Structure Materials
checkpoint | 1.03.1 - Precast Catchpits
label | Acceptance / Conformance Criteria - All catchpits shall be precast concrete suitable for HN-HO-72 traffic loading.
label | Standard / Specification - PS 16.10.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.2 - Catchpit Lids
label | Acceptance / Conformance Criteria - Non-Rock 510mm Class D Heavy Duty type lids or similarly approved shall be used unless otherwise specified on the drawings. Heavy Duty type lids to be suitable for HN-HO-72 traffic loadings that are cycle friendly.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.3 - Precast concrete manhole
label | Acceptance / Conformance Criteria - All precast concrete manholes shall be manufactured in accordance with NZS 3109:1997. All manholes shall be suitable for HN-HO-72 traffic loading.
label | Standard / Specification - 16.15.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.4 - Catchpit Grates and Frames
label | Acceptance / Conformance Criteria - Catchpits grates and frames shall be grey cast iron suitable for HN-HO-72 traffic loadings.
label | Standard / Specification - PS 16.10.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.5 - Scruffy domes lids
label | Acceptance / Conformance Criteria - Scruffy domes lids shall be galvanised steel Hynds Type 2 scruffy domes (unless noted otherwise in the drawings), or similar approved.
label | Standard / Specification - PS 16.16.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.6 - Cement Mortar
label | Acceptance / Conformance Criteria - Cement mortar shall be Durability Class M4 in accordance with NZS 4210:2001, with a minimum compressive strength of 12.5MPa.
label | Standard / Specification - PS 16.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.7 - Epoxy Mortar
label | Acceptance / Conformance Criteria - Epoxy mortar for use in manhole riser joining or repairing of damaged or cut concrete (to provide cover to reinforcing due to cutting of precast units) shall be Hynds (MSR) or Humes Hume bond (or similar approved), applied in accordance with the manufacturer’s recommendations.
label | Standard / Specification - PS 16.8.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.8 - Precast Headwalls and Wingwalls
label | Acceptance / Conformance Criteria - Precast concrete headwalls or wingwall units shall be manufactured in accordance with NZS 3109:1997.
label | Standard / Specification - PS 16.13.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.9 - Erosion protection matting
label | Acceptance / Conformance Criteria - Erosion protection matting (coir Blanket or similar approved) is to be 100% biodegradable.
label | Standard / Specification - PS 16.13.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.10 - Precast Soakage Pit
label | Acceptance / Conformance Criteria - All precast concrete Soakage Pit manholes shall be manufactured in accordance with NZS 3109:1997.
label | Standard / Specification - PS 16.12.2.1
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.12 - Manhole Sealant
label | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
label | Standard / Specification - PS 16.12.2.2
label | Verifying Document - Datasheet
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.13 - Head and Wing wall Insitu Concrete
label | Acceptance / Conformance Criteria - Headwall and wingwall insitu reinforcing shall be steel grade 500E.
label | Standard / Specification - PS 16.13.2
label | Verifying Document - Mill Certs
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.14 - Head and Wing wall Reinforcing
label | Acceptance / Conformance Criteria - The headwall and wingwall cast in-situ concrete shall be 40MPa
label | Standard / Specification - PS 16.13.2
label | Verifying Document - Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 1.03.16 - Benching Concrete
label | Acceptance / Conformance Criteria - Benching shall be 20MPa concrete
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Mix Design
label | Frequency - Prior to use
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
section | 2.01 Stormwater Drainage (Existing Assets)
checkpoint | 2.01.1 - Obsolete Stormwater Structures
label | Acceptance / Conformance Criteria - Obsolete catchpits, manholes, kerb and channel shall be demolished, uplifted and removed to an approved tip site.
label | Standard / Specification - PS 14.2.1
label | Verifying Document - Site Record
label | Frequency - Each Obsolete Structures
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 2.01.2 - Cutting Existing Pipes
label | Acceptance / Conformance Criteria - Where the catchpit will be replaced by a new drainage structure and/or constructed in a new location the existing stormwater pipe shall be neatly cut perpendicular to the line of the pipe to allow it to be easily extended.
label | Standard / Specification - PS 14.2.2
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 2.01.3 - Debris Removal and Void Filling
label | Acceptance / Conformance Criteria - All debris shall be removed to waste. The resulting void shall be backfilled with well compacted approved fill material.
label | Standard / Specification - PS 14.2.3
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - R
label | Verification Activity: By - SE
checkpoint | 2.01.4 - Obsolete culverts
label | Acceptance / Conformance Criteria - Obsolete culverts shall be removed or may be left in place subject to the agreement of the Engineer. Abandoned culverts shall be plugged with concrete at each end or if the culvert is within 1.0m of the surface it shall be completely filled with a cement grout.
label | Standard / Specification - PS 14.2.4
label | Verifying Document - Site Record
label | Frequency - Each Occurrence
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 3.01 Stormwater General
checkpoint | 3.01.1 - Setout
label | Acceptance / Conformance Criteria - Prior to the commencement of any drainage works for a particular drainage line, the Contractor shall set out the line, level, and position of the proposed drainage line, including inlet and outlet positions and levels, and present it to the Engineer for their consideration. The Contractor shall provide at least 48 hours’ notice to the Engineer ahead of set-out and allow 48 hours for the Engineer to respond prior to commencing work.
label | Standard / Specification - PS 16.6.1
label | Verifying Document - Survey Records
label | Frequency - Prior to the commencement
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.01.2 - Dealing with Water
label | Acceptance / Conformance Criteria - The Contractor shall maintain all trench inverts free from flowing or accumulated water. Water arising from, or draining into, the trench shall be drained or pumped. Any sumps required shall be refilled to formation level as directed by the Engineer.
label | Standard / Specification - PS 16.7.1
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 3.02 Pipe Installation and Backfill
checkpoint | 3.02.1 - Open Trenches
label | Acceptance / Conformance Criteria - All open trench excavations for pipelines shall be to a minimum depth of 100mm below the pipe external walls. Where excavating in natural ground or existing carriageways, no more than 100 metres of trench (per drain laying operation) shall remain open at any one time.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.2 - Saw Cutting
label | Acceptance / Conformance Criteria - Where trenching through roads, prior to excavation, the surface shall be saw-cut a minimum of 100mm beyond the trench wall and parallel to the proposed alignment.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.3 - Stability check
label | Acceptance / Conformance Criteria - Where trenching is near new or existing structures (within 5m horizontally, or where the trench invert is below a plane projected downwards at 1(V) in 2(H) from the base of the structure), a stability check shall be undertaken to ensure undermining of the structure is avoided. The Contractor shall undertake a stability check in these situations.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.4 - Trench Width
label | Acceptance / Conformance Criteria - The minimum trench widths are as indicated on Drawing WD-0131 but not less than the external pipe diameter plus 600mm and not more than the external pipe diameter plus 1200mm.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.5 - Unsuitable Material
label | Acceptance / Conformance Criteria - All material deemed to be unsuitable shall be removed to a depth of 600mm or a greater depth as specified by the Engineer, until suitable material is reached.
label | Standard / Specification - PS 16.9.2.10
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.6 - Trench invert subgrade inspection
label | Acceptance / Conformance Criteria - The Engineer shall have the opportunity to complete a Visual Inspection to NZTA F/3:2010 on the trench subgrade each day on each pipeline during installation.
label | Standard / Specification - Suitability
label | Verifying Document - Engineers Record
label | Frequency - Daily
label | Verification Activity: Activity - WP
label | Verification Activity: By - ENG
checkpoint | 3.02.7 - Trench invert subgrade testing
label | Acceptance / Conformance Criteria - The subgrade shall be tested for CBR>5 by Scala or shear vane. This test shall be undertaken at the design subgrade level and at a depth of 300mm below the design subgrade level.
label | Standard / Specification - PS 16.9.1.3, PS 16.32.3
label | Verifying Document - Scala or Shear Vane Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.02.8 - Subgrade Undercut and Replacement
label | Acceptance / Conformance Criteria - The insitu trench base shall be tested and if CBR is less than 5, it shall be undercut and backfilled with AP65 compacted to compacted to a MDD of 90%
label | Standard / Specification - PS 16.9.1.3
label | Verifying Document - Site Records / NDM / Clegg Report
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.9 - Pipe bedding and haunch zone inspection
label | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe bedding and haunch zone
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Engineers Record
label | Frequency - 1 per trench length (Between Chambers)
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.02.10 - Pipe bedding and haunch zone Density Testing
label | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The pipe bedding and haunching zone shall be compacted to a MDD of 90%
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.02.11 - Backfilling of pipes and culverts with embankment fill - QA Acceptance
label | Acceptance / Conformance Criteria - Prior to Backfilling of pipes and culverts with embankment fill the test results for bedding, haunching, side zone, and overlay zone material properties, grading curves and compaction tests are accepted by the Engineer.
label | Standard / Specification - PS 16.37
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to Backfilling of pipes and culverts with embankment fill
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.02.12 - Pipe laying in Embankments
label | Acceptance / Conformance Criteria - The Contractor shall have each pipe checked for level as it is laid, by a competent technician using an Engineer’s level, pipe laser or other approved equipment. Pipes shall be laid on uniform gradients between successive designated manholes at the gradients specified on the Drawings.
label | Standard / Specification - PS 16.9.2.8
label | Verifying Document - Survey Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | 3.02.13 - Pipe Connections
label | Acceptance / Conformance Criteria - A flexible joint shall be provided to the outside face of any structure (manholes, catchpits, catchpit manholes and headwalls) into which a pipe is built. The length of the next pipe (rocker pipe) join away from the structure shall be no more than 600mm for all concrete stormwater pipes and shall be constructed in accordance with Typical Details on the drawings.
label | Standard / Specification - PS 16.9.2.15
label | Verifying Document - Site Records
label | Frequency - Each Structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.02.14 - Cutting of Concrete Pipes
label | Acceptance / Conformance Criteria - Where it is necessary to cut a concrete pipe the pipe supplier should be informed of such requirement specifically where the dimensional tolerance for the pipe is deemed critical.
label | Standard / Specification - PS 16.9.2.16
label | Verifying Document - Suppler Approval
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.15 - Cut Pipe Sealing
label | Acceptance / Conformance Criteria - All cut surfaces, not encased within benching or other in-situ concrete, shall be coated with an epoxy resin mortar in accordance with the manufacturer/supplier recommendations, leaving no exposed reinforcement.
label | Standard / Specification - PS 16.9.2.16
label | Verifying Document - Site Records
label | Frequency - Each Occurrence
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.16 - Side zones Density Testing
label | Acceptance / Conformance Criteria - Pipe surround material shall be placed and compacted over the full width of the trench to a finished minimum thickness of 150mm above the crown of the pipes. The Side zones shall be compacted to a MDD of 90%
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per backfill layer per 15m trench length. Minimum of 2 tests backfill layer per trench between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.02.17 - Compaction above Pipe
label | Acceptance / Conformance Criteria - Only hand operated compaction tools shall be used until the backfill has achieved a depth of 300mm above the crown of the pipe.
label | Standard / Specification - PS 16.32
label | Verifying Document - Site Records
label | Frequency - During Works
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.02.18 - Pipe overlay zone inspection
label | Acceptance / Conformance Criteria - The Engineer shall complete a Visual Inspection to NZTA F/3: 2010 each strength length on Pipe overlay zone
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Engineers Record
label | Frequency - 1 per trench length (Between Chambers)
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.02.19 - Pipe Overlay Zone Density Testing
label | Acceptance / Conformance Criteria - Backfill material shall be built up in layers not exceeding 200mm. The Pipe overlay zone shall be compacted to a MDD of 90%
label | Standard / Specification - PS 16.32.3, PS 16.6
label | Verifying Document - NDM / Clegg Report
label | Frequency - 1 per 15m trench length Minimum of 2 tests between pits/manholes
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.02.20 - Pipe invert levels/lid levels at all drainage structures
label | Acceptance / Conformance Criteria - Pipes shall be installed within 20mm of stated invert level (vertical tolerance) and within 50mm or 5% of the pipe diameter of proposed horizontal alignment (whichever is greater). Catchpits and catchpit manholes shall be located to align with proposed kerb and channel (or dish channel) and finished to be flush with the finished road surface unless otherwise specified on the Drawings.
label | Standard / Specification - PS 16.34.2
label | Verifying Document - Survey Records
label | Frequency - At the completion of each stormwater pipeline
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
section | 3.03 Subsoil Drain
checkpoint | 3.03.1 - Trench Grade
label | Acceptance / Conformance Criteria - Unless otherwise specified trenches shall have: a minimum gradient of not less than 1 in 100; vertical sides from the trench bottom to a minimum of 300 mm above the top of the pipe; and a minimum depth that will ensure that, when the pipes are laid, the invert level shall be not less than one metre below finished subgrade level.
label | Standard / Specification - NZTA F/5 PS 16.11.2
label | Verifying Document - Note only
label | Frequency - Each Pipe
label | Verification Activity: Activity -
label | Verification Activity: By -
checkpoint | 3.03.2 - Bedding and Installation of Drainage Pipe
label | Acceptance / Conformance Criteria - Prior to laying the drain pipes, the Constructor shall ensure that pipes do not become contaminated with clay or soil and that pipe slots are not blocked. Any such blockages shall be removed before pipes are laid.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.3 - Bedding Placement
label | Acceptance / Conformance Criteria - The filter material shall be placed, and the drain pipe installed such that the pipe is at a uniform grade and is underlain by a minimum of 50 mm and overlaid by a minimum of 150mm of filter material which completely surrounds the drain pipe. The filter material shall be placed in a manner to achieve a generally uniform dense state.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.4 - Pipe Orientation
label | Acceptance / Conformance Criteria - Pipes should generally be laid so that the perforations are oriented as shown in accordance with the manufacturer’s recommendations for corrugated HDPE pipes.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.5 - Pipe Jointing
label | Acceptance / Conformance Criteria - The drain pipe lengths shall be joined following the manufacturer’s instructions or as approved by the Engineer, with the pipe jointing carried out to leave a smooth flush internal surface. The top ends of the pipes shall be capped.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Each Joint
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.6 - Pipe Installation Inspection
label | Acceptance / Conformance Criteria - The drain pipe installation shall be inspected and approved by the Engineer before placing filter material and backfill.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to backfilling
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.03.7 - Lose Debris Removal
label | Acceptance / Conformance Criteria - Prior to placing filter material and backfill, the base and sides of the trench shall be cleaned of loose debris so far as is practical.
label | Standard / Specification - PS 16.11.3
label | Verifying Document - Site Records
label | Frequency - Prior to backfilling
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.8 - Subsoil Backfilling
label | Acceptance / Conformance Criteria - The backfill shall be filter sand as detailed in clause 2.2 of this specification. The backfill material shall be placed in layers not exceeding 150 mm loose depth and shall be positively compacted around the sides of the pipe to provide support of not less than that of the adjacent material
label | Standard / Specification - NZTA F/5 PS 16.11.2
label | Verifying Document - Site Records
label | Frequency - Each Pipe
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
checkpoint | 3.03.9 - Overlaying
label | Acceptance / Conformance Criteria - The completed drains shall be backfilled with an overlying capping layer to prevent the ingress of surface water.
label | Standard / Specification - PS 16.11.4
label | Verifying Document - Site Records
label | Frequency - On Completed Drains
label | Verification Activity: Activity - S
label | Verification Activity: By - SE
section | 3.04 Stormwater Structures General
checkpoint | 3.04.1 - Stormwater Structures Subgrade
label | Acceptance / Conformance Criteria - A hand Auger Scala / Shear Vane up to 4m deep shall be completed in the base of the excavation and the results submitted to the Engineer. The subgrade shall be CBR>5.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Scala / Shear Vane Results
label | Frequency - 1 per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.04.2 - Stormwater Structures Bedding material
label | Acceptance / Conformance Criteria - Stormwater Structures Bedding granular material shall be compacted to MDD of 95%.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - NDM Results
label | Frequency - 1 per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.04.3 - Stormwater Structures Backfill
label | Acceptance / Conformance Criteria - Stormwater Structures Backfill granular material shall be compacted to MDD of 95%.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - NDM Results
label | Frequency - 1 per backfill layer per structure
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.04.4 - Subgrade Clay
label | Acceptance / Conformance Criteria - If clay is present at subgrade level, then this should be supplemented with soaked CBR laboratory testing.
label | Standard / Specification - PS 16.32.3
label | Verifying Document - Soaked CBR
label | Frequency - Each Occurrence
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.04.5 - Culvert CBR Approval
label | Acceptance / Conformance Criteria - The contractor is to provide CBR testing of trench subgrade prior to placement of bedding and laying of culverts.
label | Standard / Specification - PS 16.38
label | Verifying Document - CBR
label | Frequency - Each culvert prior to bedding
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
section | 3.05 Catchpits (Structure)
checkpoint | 3.05.1 - Catchpits Base
label | Acceptance / Conformance Criteria - Catchpits shall be constructed on a compacted, on top of a 150mm layer of compacted AP65 or GAP100 granular material.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.05.2 - Precast Catchpit Sealant
label | Acceptance / Conformance Criteria - All joints between segments of precast catchpit risers shall be sealed with ‘Black Butyl Mastic Sealant – Hynds (MSR)’ or similar and approved.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.05.3 - Catchpits Grates
label | Acceptance / Conformance Criteria - Cast-iron grates and frames shall be set no more than 30mm lower than, but parallel to the cross fall and grade of the surrounding, finished pavement surface level. All grates and frames shall be haunched to lids.
label | Standard / Specification - PS 16.10.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.05.4 - Catchpits Sumps
label | Acceptance / Conformance Criteria - Catchpits must have sumps at least 450mm deep (below the invert of the outlet pipe level)
label | Standard / Specification - PS 16.10
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.05.5 - Catchpits Inlets
label | Acceptance / Conformance Criteria - All catchpits receiving stormwater from the highway shall be constructed with a back-entry inlet.
label | Standard / Specification - PS 16.10
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
section | 3.06 Manholes (Including Catchpit Manholes)
checkpoint | 3.06.1 - Manholes Base
label | Acceptance / Conformance Criteria - Manholes shall be constructed on a compacted, on top of a 150mm layer of compacted AP65 or GAP100 granular material
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.2 - Manholes Sealant
label | Acceptance / Conformance Criteria - All joints between ring segments of precast manholes and chambers shall be sealed with ‘Grey Butyl Manhole Sealant – Hynds (SM9020)’ or similar and approved.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.3 - Benching
label | Acceptance / Conformance Criteria - Benching is required in all manhole structures unless noted otherwise on Drawings. Benching shall be 20MPa concrete and to a F4 finish. Manhole benching shall accommodate pavement subsoil drain connections where required.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Catchpit
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.4 - Benching Fall
label | Acceptance / Conformance Criteria - All side benching shall be formed with a fall towards the channel unless otherwise stated.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.5 - Sealant
label | Acceptance / Conformance Criteria - All pipe work penetrations through manhole walls shall be sealed using Epoxy Mortar or an approved equivalent type of permanent sealant.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.6 - Lids
label | Acceptance / Conformance Criteria - All solid cast-iron covers and frames shall be set flush with the cross fall and grade of the surrounding finished surfaces. All grates and frames shall be haunched to lids.
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.7 - raised cover levels
label | Acceptance / Conformance Criteria - For new or existing manholes with raised cover levels, the height of the manhole access shaft (throat) shall be no greater than 600mm where access is required (all non-catchpit manholes). The shaft and any subsequent extensions to the shaft shall be constructed using either:
label | Standard / Specification - PS 16.15.2
label | Verifying Document - Site Records
label | Frequency - Each Manhole
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.8 - Adjust Manhole Service Lid Covers
label | Acceptance / Conformance Criteria - Following adjustment, the service cover shall be firmly held in place and shall not be 5mm higher or 0mm lower than the adjoining surface. The item shall cover adjustments + or – 300mm from the original height. Any adjustments exceeding these measurements shall be treated as a variation.
label | Standard / Specification - PS 16.12.1
label | Verifying Document - Site Records
label | Frequency - Each Lid
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.06.9 - Visual inspection of all Manholes
label | Acceptance / Conformance Criteria - 3-6 months following construction, Each manhole shall be inspected. No evidence of identifiable flow infiltration, settlement and riser displacement or cracking shall be present
label | Standard / Specification - PS 16.34
label | Verifying Document - Inspection Record
label | Frequency - Each Manhole 3-6 months after Construction
label | Verification Activity: Activity - W
label | Verification Activity: By - ENG
section | 3.07 Headwalls and Wingwalls (Structure)
checkpoint | 3.07.1 - Headwall Bedding
label | Acceptance / Conformance Criteria - Headwall aprons shall be constructed on a compacted, 75mm bedding sand underlay by 150mm layer of AP65 (or similar material as approved by the Engineer) granular material and compacted to a MDD of 95%.
label | Standard / Specification - PS 16.13.2
label | Verifying Document - NDM Results
label | Frequency - 1 Per Apron
label | Verification Activity: Activity - I
label | Verification Activity: By - SE
checkpoint | 3.07.2 - Precast and Cast in-situ Headwall and Wingwall tolerance
label | Acceptance / Conformance Criteria - +/- 10mm variance to vertical design set-out
label | ○ +/- 10mm variance to horizontal design set-out (values in accordance with NZS 3109: 1997)
label | Standard / Specification - PS 16.34
label | Verifying Document - Survey Records
label | Frequency - Every Unit
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
section | 3.08 Stormwater Concrete Capping (Pre Pour)
checkpoint | 3.08.1 - Construction Joint Locations
label | Acceptance / Conformance Criteria - Proposed location of construction joints to be submitted to the engineer for review prior to concrete pour.
label | Standard / Specification - Downer
label | Verifying Document - Approval
label | Frequency - Prior to Pour
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.08.2 - Dry Pack Mortar
label | Acceptance / Conformance Criteria - Dry pack mortar where specified on the drawings shall be places as per the manufactures instructions.
label | Standard / Specification - Downer
label | Verifying Document - Pre pour
label | Frequency - Before Works
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 3.08.3 - Reinforcement Pre Pour Inspection
label | Acceptance / Conformance Criteria - Handling, Fabrication, Placing and Fixing shall be inspected prior to pouring concrete.
label | Standard / Specification - Downer
label | Verifying Document - Pre pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 3.08.4 - Pre-Pour Inspection
label | Acceptance / Conformance Criteria - Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area.
label | Standard / Specification - Downer
label | Verifying Document - Signed Pre-Pour
label | Frequency - 48 Hours Notice Prior to Each Occurrence
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.08.5 - Delivery Dockets
label | Acceptance / Conformance Criteria - The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size.
label | Standard / Specification - Downer
label | Verifying Document - Dockets
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
section | 3.09 Stormwater Concrete Capping (Post Pour)
checkpoint | 3.09.1 - Post Pour Inspection
label | Acceptance / Conformance Criteria - Following the concrete pour, the concrete shall be inspected for Size, Shape, Features, inserts, reliefs, and Finish against the drawings.
label | Standard / Specification - Downer
label | Verifying Document - Post Pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 3.09.2 - Construction joints
label | Acceptance / Conformance Criteria - Construction joints shall be placed as per the drawings / agreement.
label | Standard / Specification - Downer
label | Verifying Document - Post Pour
label | Frequency - Each Pour
label | Verification Activity: Activity - R
label | Verification Activity: By - PE
checkpoint | 3.09.3 - Defective Concrete Finishes
label | Acceptance / Conformance Criteria - Repair of defective concrete finish other than that due to minor porosity of the surface shall be carried out only when approved by the Engineer.
label | Standard / Specification - NZS 3114
label | Verifying Document - NCR
label | Frequency - Prior to non Minor Repair
label | Verification Activity: Activity - V
label | Verification Activity: By - SE
section | 3.10 16.35 CCTV Inspections
checkpoint | 3.10.1 - CCTV stormwater pipe
label | Acceptance / Conformance Criteria - Every stormwater pipeline 300mm and greater shall be inspected by means of CCTV camera at the completion of each pipe trench backfill and compaction and at the completion of Earthworks operations (or at a time otherwise agreed with the Engineer).
label | Standard / Specification - PS 16.34, PS 16.35.1
label | Verifying Document - CCTV Video and Report
label | Frequency - At completion of pipes laying, backfilling but prior to final surfacing (Pavements, etc.)
label | Verification Activity: Activity - I
label | Verification Activity: By - PE
checkpoint | 3.10.2 - Pavement Construction CCTV Review
label | Acceptance / Conformance Criteria - Prior to pavement construction, The Contractor shall submit the pipe condition inspection report to the Engineer for acceptance. The pipe condition inspection report is to be based on CCTV for all pipes upon completion of backfilling the trench.
label | Standard / Specification - PS 16.37
label | Verifying Document - Engineers Acceptance
label | Frequency - Prior to pavement construction above Stormwater pipelines
label | Verification Activity: Activity - HP
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | 3.11 As Built Records
checkpoint | 3.11.1 - Survey Requirements - Stormwater Systems - Underground:
label | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings.: Trench invert. Pipe/structure bedding and backfill compaction. Pipe/structure size, class, alignment, and level. Manhole and catchpit position, levels (lid and inverts). Outlet structures including position, levels, erosion provisions and fish passages.
label | Standard / Specification - PS 16.33
label | Verifying Document - Survey
label | Frequency - All underground Stormwater Systems
label | Verification Activity: Activity - I
label | Verification Activity: By - SV
checkpoint | 3.11.2 - Survey Requirements - Stormwater Systems – Above ground:
label | Acceptance / Conformance Criteria - The following items shall be recorded for asbuilt drawings: Treatment swales, wetlands, basin’s location, profile and grade. Diversion Drain location, profile, and grade. Trench excavation and invert. Line, levels and grade of kerb and channels. Rodding eye locations.
label | Standard / Specification - PS 16.33
label | Verifying Document - Survey
label | Frequency - All above ground Stormwater Systems
label | Verification Activity: Activity - I
label | Verification Activity: By - SV