## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Events Gas QA |  |  |  |  | Yes | Events Gas QA | 0cdf96c2-0b30-4df8-8853-167f6150f5dc
checkpoint-status |  |  | checkpoint | Take 5/SWMS/Inductions been completed before works start
checkpoint-status |  |  | checkpoint | Kitchen layout is correct as per current drawings issued by client
checkpoint-status |  |  | checkpoint | Has a gas test been completed
checkpoint-status |  |  | checkpoint | Do all gas appliances have the minimum 500mm clearnace from combustable surfaces?
checkpoint-status |  |  | checkpoint | Do all gas appliances have an isolation valve installed and is valve in good condition?
checkpoint-status |  |  | checkpoint | Have all gas appliances been fixed in position?
checkpoint-status |  |  | checkpoint | Are gas flexable hoses installed off the floor?
checkpoint-status |  |  | checkpoint | Are the gas LPG bottles installed with the minimum 1500mm clearance from an ignition sorce and secured to the base plate with chain?
checkpoint-status |  |  | checkpoint | Have all appliances been commissioned? Are they working as intended?
checkpoint-status |  |  | checkpoint | Area Clean
holdpoint |  |  | signoff | Sign Off
checklist-flat |  |  | checklist | Transplumb General Works ITP |  |  |  |  | Yes | Transplumb General Works ITP | 453ebf4e-9fd0-4a51-90ed-066a243a45b2
checkpoint-status |  |  | checkpoint | Has a Prestart & SWMS sign off been completed before works start
checkpoint-status |  |  | checkpoint | Client notified of works to be carried out - description of works in comments below
button | b007ad0a-ca15-58cc-a54c-b74ffec71e56 |  | button | Do any of the works require pressure testing on completion | Yes,No
checkpoint-status |  |  | checkpoint | All requested works completed
checkpoint-status |  |  | checkpoint | Area clean & works signed off below
checklist-flat |  |  | checklist | Fix 1 ITP |  |  |  |  | Yes | Fix 1 ITP | 5977547b-3389-4519-b157-0e25c339dd9e
checkpoint-status |  |  | checkpoint | Working to an approved drawing
checkpoint-status |  |  | checkpoint | Setout is correct as per current approved drawings
text | 441a42cc-721f-5b9e-9bed-7af0175578f0 |  | textbox | Drawing no. & Revision
checkpoint-status |  |  | checkpoint | No cross-connection on all water lines
checkpoint-status |  |  | checkpoint | Support and fixings checked (water hammer/silicone) and in order
checkpoint-status |  |  | checkpoint | All lines new and existing capped for testing
checkpoint-status |  |  | checkpoint | Pressure tested waterlines 1500kpa for 30 mins with start photo attached below
checkpoint-status |  |  | checkpoint | Pressure tested waterlines 1500kpa for 30 mins with finish photo attached below
checkpoint-status |  |  | checkpoint | Fixture waste points heights and centres doubled checked before wall sign off
checkpoint-status |  |  | checkpoint | All suspended drainage has been supported as per AS3500 Requirements
checkpoint-status |  |  | checkpoint | All suspended drainage been flow tested and has no leaks
checkpoint-status |  |  | checkpoint | Please supply photos of all water and waste completetd installations
checkpoint-status |  |  | checkpoint | Area clean & works signed off below
checklist-flat |  |  | checklist | Transplumb Pump / Plant Report |  |  |  |  | Yes | Transplumb Pump / Plant Report | 60f32bd0-1256-44f3-b297-2a1972fca55d
checkpoint-status |  |  | checkpoint | Has a Take 5/SWMS been completed before works start
checkpoint-status |  |  | checkpoint | Pump / plant location and description
checkpoint-status |  |  | checkpoint | Control board clean and sealed from water ingress
checkpoint-status |  |  | checkpoint | Check operation of all controls
checkpoint-status |  |  | checkpoint | Check indicator and alarm light operations
checkpoint-status |  |  | checkpoint | Pump 1 working as intended including amp and motor continuity test
checkpoint-status |  |  | checkpoint | Pump 2 working as intended including amp and motor continuity test
checkpoint-status |  |  | checkpoint | Check system pipework, manifolds, hoses and related service lines
checkpoint-status |  |  | checkpoint | Pump well clean and free of foreign objects
checkpoint-status |  |  | checkpoint | Pump well access steps and pump guiderails in good condition
checkpoint-no-status |  |  | checkpoint | Comments
checkpoint-status |  |  | checkpoint | Area Clean
holdpoint |  |  | signoff | Final Sign off
checklist-flat |  |  | checklist | Transplumb Fire Plug QA |  |  |  |  | Yes | Transplumb Fire Plug QA | 7ea1f4df-f059-49a6-b40d-64c2ae46abd8
checkpoint-status |  |  | checkpoint | Has a Take 5/SWMS been completed before works start
checkpoint-status |  |  | checkpoint | Fire Plug Number
checkpoint-status |  |  | checkpoint | Fire Plug Location IB or OB (Insert Maps Location Screenshot) Photo Required
checkpoint-status |  |  | checkpoint | Fire Plug Isolation Valve Location (Insert Maps Location Screenshot) Photo Required
checkpoint-status |  |  | checkpoint | Is the current hydrant cover adequately sized and positioned for maintanance (Photo Required)
checkpoint-status |  |  | checkpoint | Has any maintenance works been completed
checkpoint-status |  |  | checkpoint | COMMENTS
holdpoint |  |  | signoff | Final Sign off
checklist-flat |  |  | checklist | Transplumb Drainage BG ITP |  |  |  |  | Yes | Transplumb Drainage BG ITP | 9209ffac-0c84-4e54-9ed4-bcc736eb30e2
checkpoint-status |  |  | checkpoint | Working to an approved drawing
checkpoint-status |  |  | checkpoint | Setout is correct as per current approved drawings
checkpoint-status |  |  | checkpoint | Pipe bedding materials comply (as per AS 3500)
checkpoint-status |  |  | checkpoint | Grades, fittings & joints installed to standards
checkpoint-status |  |  | checkpoint | Inspection & Testing carried out prior to backfill
checkpoint-status |  |  | checkpoint | Sealed any open ends
checkpoint-status |  |  | checkpoint | Backfill & compact trenches to code requirements
checkpoint-status |  |  | checkpoint | CCTV on completion
checkpoint-status |  |  | checkpoint | Area clean & works signed off below
checklist-flat |  |  | checklist | Transplumb Roofing ITP |  |  |  |  | Yes | Transplumb Roofing ITP | 94d3d39b-6ab1-42bb-af17-f7a2d73170c8
checkpoint-status |  |  | checkpoint | Take 5/SWMS/Inductions been completed before works start
label | b4bf08ab-dd2a-5736-b65c-3885bf1537e5 |  | note | Worker is qualified to work at heights
checkpoint-status |  |  | checkpoint | Working to an approved drawing - description of works entered in comments below
checkpoint-status |  |  | checkpoint | Only approved materials installed
checkpoint-status |  |  | checkpoint | All fixings correctly installed as per AS 3500
checkpoint-status |  |  | checkpoint | Boxgutters/sump/downpipes installed and clipped correctly as per AS 3500
checkpoint-status |  |  | checkpoint | Flashings installed correctly and siliconed
checkpoint-status |  |  | checkpoint | Testing carried out where possible
checkpoint-status |  |  | checkpoint | Area clean & works signed off below
checklist-flat |  |  | checklist | Blank Canvas Checklist |  |  |  |  | Yes | Add Blank Canvas Checklist | 965e35f2-e1e6-49ec-a735-052266b61df1
checkpoint-status |  |  | checkpoint | Add Comments, Files or Signatures here
checklist-flat |  |  | checklist | Events Kitchen QA |  |  |  |  | Yes | Events Kitchen QA | a259b630-c6c1-4e5d-aac9-2cfae9f8a599
checkpoint-status |  |  | checkpoint | Take 5/SWMS/Inductions been completed before works start
checkpoint-status |  |  | checkpoint | Kitchen layout is correct as per current drawings issued by client
checkpoint-status |  |  | checkpoint | Has a gas test been completed
checkpoint-status |  |  | checkpoint | Do all gas appliances have the minimum 500mm clearnace from combustable surfaces?
checkpoint-status |  |  | checkpoint | Do all gas appliances have an isolation valve installed and is valve in good condition?
checkpoint-status |  |  | checkpoint | Have all gas appliances been fixed in position?
checkpoint-status |  |  | checkpoint | Are gas flexible hoses installed off the floor?
checkpoint-status |  |  | checkpoint | Are the gas LPG bottles installed with the minimum 1500mm clearance from an ignition source and secured to the base plate with chain?
checkpoint-status |  |  | checkpoint | Have all water and waste pipes been installed neatly?
checkpoint-status |  |  | checkpoint | Is hot water unit connected and working as required?
checkpoint-status |  |  | checkpoint | Is macerator unit connected and working as required?
checkpoint-status |  |  | checkpoint | Are sullage tanks and sewer connections in place and connected as required?
checkpoint-status |  |  | checkpoint | Is water live to kitchen and has all water and waste been checked for leaks and repaired if required
checkpoint-status |  |  | checkpoint | Have all appliances been commissioned? Are they working as intended?
checkpoint-status |  |  | checkpoint | Area Clean
holdpoint |  |  | signoff | SIGN OFF
checklist-flat |  |  | checklist | Plant Introduction |  |  |  |  | Yes | Plant Introduction | b5cf7af1-b85e-444d-88c5-c1077b898456
checkpoint-status |  |  | checkpoint | Details entered below
text | b51df805-268e-5471-9ea5-c54bc45cd3b5 |  | textbox | Site representative
text | 470a2e55-62b3-5fcb-8849-5f1d6a80c691 |  | textbox | Independent contractor
text | 702a87a0-d305-5b7e-8c2a-1ae980186d35 |  | textbox | Item of plant
checkpoint-status |  |  | checkpoint | Hazard checklist been completed
checkpoint-status |  |  | checkpoint | Has a swms been provided and signed for the task
checkpoint-status |  |  | checkpoint | Log book provided
checkpoint-status |  |  | checkpoint | Maintenance log book provided
checkpoint-status |  |  | checkpoint | Operator's manual provided
checkpoint-status |  |  | checkpoint | Certification of operator provided
checkpoint-status |  |  | checkpoint | Noise level - operational
checkpoint-status |  |  | checkpoint | Final sign off attached below
checklist-flat |  |  | checklist | Transplumb Variations |  |  |  |  | Yes | Transplumb Variations | b7cc1029-8953-423d-b7f1-91df4c9135f1
checkpoint-status |  |  | checkpoint | Variation details entered below
text | 981a53fd-e115-5214-93a4-ef767419f1f5 |  | textbox | Variation Name
text | 3f9ca811-630f-5ad5-a57b-2fee92d92529 |  | textbox | Variation Description
checkpoint-status |  |  | checkpoint | Photos of works completed
checkpoint-status |  |  | checkpoint | Final signoff - any supporting docs and client signature attached below
holdpoint |  |  | signoff | Request Signoff
checklist-flat |  |  | checklist | Prestart / Toolbox Meeting |  |  |  |  | Yes | Prestart / Toolbox Meeting | c206ef10-bccb-4c66-a752-1257e17b1e93
checkpoint-status |  |  | checkpoint | Transplumb Prestart / Toolbox Meeting
text | 19e02069-4e92-57ca-ab35-d23775aef2d5 |  | textbox | Site location and job number
text | d6ff04d2-583d-55c2-9d15-26a6dff26d80 |  | textbox | Site foreman/supervisors name
text | ffdce9a0-47b8-5874-9ec5-c5f4135aa3e4 |  | textbox | Subject
checkpoint-status |  |  | checkpoint | Have all staff completed any required site inductions
checkpoint-status |  |  | checkpoint | Are any high risk tasks involved (such as work at heights, forklift, confined space)? If so are relevant staff trained and ticketed for these works?
checkpoint-status |  |  | checkpoint | Have all staff signed into the relevant company swms
checkpoint-status |  |  | checkpoint | Comments and points raised
checkpoint-status |  |  | checkpoint | Corrective action required
text | 16a3aeda-b2f6-56b2-bed1-84441bcd4bff |  | textbox | If yes, action by
checkpoint-status |  |  | checkpoint | Action complete
holdpoint |  |  | signoff | Transplumb Final Sign-off
checklist-flat |  |  | checklist | Hydraulic Pressure Test Record Checklist |  |  |  |  | Yes | Hydraulic Pressure Test Record Checklist | cde3122e-4994-4a5e-b106-f0c83d39cb37
checkpoint-status |  |  | checkpoint | Details entered below
text | fa2917c3-2ef9-5780-a039-4725e2e70bc7 |  | textbox | Description of system being tested
text | 3ff22a13-b5f1-544d-9abd-8109e6bc816c |  | textbox | Nominal Working Pressure (KPA)
text | 7a536bd8-9fb9-5be9-9465-c4b016c50eb1 |  | textbox | Max Test Pressure (KPA)
text | 62e8bd94-ab5a-59be-9f6e-6dfea570a436 |  | textbox | Test Type (Hydro/Air)
text | 146506e6-cc8d-5a6d-a11c-9dc8a76bb9ba |  | textbox | Gauges Calibration
text | 92ea395f-5215-5e40-bf79-2c54e1863d92 |  | textbox | Time at test
text | 45d3bff8-b106-53e5-8294-e031d9605beb |  | textbox | Time at test completion
text | 60f7aa28-4f78-5554-bb29-c786b8913809 |  | textbox | Pressure at completion
text | accec22b-63a9-5de7-8609-c9e6dfff51b5 |  | textbox | Duration of Pressure Test
checkpoint-status |  |  | checkpoint | Transplumb and witness signoff attached below
holdpoint |  |  | signoff | Request signoff
checklist-flat |  |  | checklist | Transplumb Backflow Testing |  |  |  |  | Yes | Transplumb Backflow Testing | d9aa5b9d-22f0-47aa-b5a5-e9342bd87b6f
checkpoint-status |  |  | checkpoint | Has a Take 5/SWMS been completed before works start
text | e03791a7-71f4-591a-a96e-5f0abe43f382 |  | textbox | Owner/Client
text | 1872454b-00bc-5496-af02-46cc8f0b1252 |  | textbox | Location Of Device (Insert Maps Location Screenshot)
text | bf510190-7344-5c5c-9803-01b944141fb4 |  | textbox | Meter Number
text | 825973cf-ccaf-56f9-b3fa-22cf7da12fda |  | textbox | Make/Size/Model/Serial No
text | edc2ec93-490a-53d3-a799-58b669a1db0a |  | textbox | Device Type (Rpzd, Double Check Valve,Single Check Valve)
checkpoint-status |  |  | checkpoint | Installation Complies With As/3500
checkpoint-status |  |  | checkpoint | Permission Received To Isolate Water
checkpoint-status |  |  | checkpoint | Strainer Installed And Cleaned
checkpoint-status |  |  | checkpoint | First Closed Test Result (Kpa)
checkpoint-status |  |  | checkpoint | Second Closed Test Result (Kpa)
checkpoint-status |  |  | checkpoint | Third Closed Test Result (Kpa)
checkpoint-status |  |  | checkpoint | Fourth Open Test Result (Kpa)
checkpoint-status |  |  | checkpoint | Test Equipment Used To Complete Results
checkpoint-status |  |  | checkpoint | Device Test Completed
holdpoint |  |  | signoff | Final Sign off
checklist-flat |  |  | checklist | Fix 2 ITP |  |  |  |  | Yes | Fix 2 ITP | df7fb5e3-7b61-413b-9092-8380924b4351
checkpoint-status |  |  | checkpoint | Only approved fixtures installed
checkpoint-status |  |  | checkpoint | Products checked and have no imperfections
checkpoint-status |  |  | checkpoint | Fixtures installed as per approved drawing locations
checkpoint-status |  |  | checkpoint | No cross-connection on all water lines
checkpoint-status |  |  | checkpoint | Hot water correct temperature & Hot water tempering valve set to 50c +/-5c)
checkpoint-status |  |  | checkpoint | DDA Hot water correct temperature & Hot water tmv set to 42c +/-2c)
checkpoint-status |  |  | checkpoint | Water pressure acceptable 350kpa - 500kpa
checkpoint-status |  |  | checkpoint | Checked all drainage is working correctly wth no leaks
checkpoint-status |  |  | checkpoint | Cleaned out all strainers
checkpoint-status |  |  | checkpoint | Commissioned all fixtures
checkpoint-status |  |  | checkpoint | Final check for any leaks
checkpoint-status |  |  | checkpoint | Area clean - sign off and photos attached below
checklist-flat |  |  | checklist | SWMS Checklist |  |  |  |  | Yes | SWMS Checklist | e136f617-f2fa-450f-bd18-cad60be2b452
checkpoint-status |  |  | checkpoint | Has a swms doc been uploaded
checkpoint-status |  |  | checkpoint | Do you agree to follow all procedures outlined within the attached swms
checkpoint-status |  |  | checkpoint | Are there any site specific additions or omissions to add to this swms
checkpoint-status |  |  | checkpoint | Have you signed into the attached swms
checklist-flat |  |  | checklist | Transplumb Events Asset I.D |  |  |  |  | Yes | Transplumb Events Asset I.D | fcf27d54-9cc1-4531-a59e-301bf4f84e0b
checkpoint-no-status |  |  | checkpoint | ASSET NO#
checkpoint-no-status |  |  | checkpoint | Asset Description
checkpoint-status |  |  | checkpoint | Asset Serial Number
checkpoint-status |  |  | checkpoint | Damage or Missing Parts
checkpoint-status |  |  | checkpoint | Current Location
holdpoint |  |  | signoff | Staff Sign Out