## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
6dc17c7d-e0c8-4de0-8a90-325c1c0d7408 | checklist | A/C Checklist Commissioning [F] |  | A/C Checklist Commissioning [F]
bf1b0c7f-f0ac-46bc-8a46-ccf1ec6cc04e | section | A/C Checklist Commissioning
313c495f-0b91-473d-b9c2-a2a85cdbaca8 | checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs?
c827da72-2bef-47dc-bf12-c063cdd3711b | checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum?
c9771447-8fa1-4dc8-be94-340068128cc3 | checkpoint | Indoor unit drains have been terminated to the tundish point?
7f0e1f95-62da-4f3f-ba1a-5b6f12f2480b | checkpoint | Outdoor unit drains have been terminated to the tundish point?
367eb163-c2fa-425f-85fa-436a32578857 | checkpoint | Indoor unit flare connection has been properly insulated with specified insulation?
ed552a90-3a85-4398-b8bd-c17dc00b6eb8 | checkpoint | Indoor unit drain connection point has been securely fastened and sealed?
944992bf-0867-47ed-b87b-e90a7e35a47d | checkpoint | A/C System Flows checked as per mechanical drawings
3ac3f3cf-35cd-4398-96a2-7a0c51aca3db | checklist | Apartment Fit-Off Checklist [E] |  | Apartment Fit-Off Checklist [E]
99b32cda-571f-4674-8f0f-a247abd785d0 | section | Apartment Fit-Off Checklist
0ae48914-11b2-4655-8ca8-49c5abeafec4 | checkpoint | AC grille to living room installed with no defect
f61a6b33-bd8b-4e2d-803e-7653a49599c5 | checkpoint | AC grille to bedroom installed with no defect
4d5923ec-90b1-4376-9e5e-036f5586834e | checkpoint | Return Air grille installed as per RCP drawings
d9e8e58d-6872-4d02-bdb6-ddf31a5d29d4 | checkpoint | Range hood duct connected and taped to ensure air tight
3fbd906b-a510-4fe6-aa8c-00c8ff34df55 | checkpoint | AC Controller installed as per RCP drawings
bfb08d69-fb02-454e-9f77-94d4c622a82e | checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point
481310e2-27b6-4125-9d16-7c73301029db | checkpoint | Ensuite Exhasut fans installed and pluged in as per mechanical drawings
dcde7d05-db00-42f2-9595-4155e2a3ba09 | checkpoint | Toielt Exhasut fans installed and pluged in as per mechanical drawings
5a93031e-d267-44bb-aaaa-47715dff4978 | checkpoint | Ensuite exhaust grilles installed
6205aeae-4988-42db-95c0-72a220320bd0 | checkpoint | Toilet exhaust grilles installed
64c63dd5-f081-44e2-ae2a-360a35772ff6 | checkpoint | Laundry Exhasut fans installed and pluged in as per mechanical drawings
87b5296a-5f36-4961-8a58-0a7306d2ad3d | checkpoint | Laundry exhaust grilles installed
10e8087b-d21f-452d-9236-3203c44d1abd | checkpoint | Access panels placed as per drawings
a7896690-8451-4111-a16c-c6f0fe17f4c7 | checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked
15e25f6f-7fb0-42ce-a0a2-d71d0dda8308 | checkpoint | External louvers installed all gaps sealed between plenum box and wall/ louver flange to wall , photo evidence provided for below 1.Box sealed internally and the gap between the box and wall is sealed 2.Louver flanges sealed to the external box
3d76a4a5-a35f-4062-9f7e-7769056a0efb | checklist | Ceiling Closure Checklist 1 Rough In [B] |  | Ceiling Closure Checklist 1 Rough In [B]
51dbba53-54b4-4111-a268-2fbc9281233c | section | Air Conditioning:
33f69769-a87a-45cc-83ae-5c0ef177d9a9 | checkpoint | Air Conditioning
d03bd283-eff6-5ffd-ac97-6a0578586338 | textbox | Inspection Date:
371ed52a-6134-4d6b-b19c-25e51414c02c | checkpoint | FCUs are installed and other services are not impeding access to fan coil?
a4354e09-f4c1-47b1-acff-954b8085c7e2 | checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
ffb6964d-f299-43a5-bd34-9156544de46f | checkpoint | Wiring connected to indoor unit electrical box?
12cef986-887e-43df-a788-2815c5e671aa | checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
8337c7e5-0c20-429d-b2b6-ac6f7d2c6dd9 | checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
1bad3b76-7c4e-4788-8784-222cc0836599 | section | Ventilation:
9e6e9180-bf65-473c-b5cc-678146586831 | checkpoint | Ventilation
c28831b6-58f3-52ab-a421-05160b7ffb35 | textbox | Inspection Date:
8ef301c9-b6d0-46f3-a361-14cd46e42821 | checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
3f58dd93-8e73-4c73-9536-0e908be7bf5b | checkpoint | All flex are installed and supported by intact load spreaders?
f90d6ee4-c8e3-4141-bd92-bf56e79221d0 | checkpoint | All flexible ducts inner core and outer core have been mechanically secured & taped to spigots and air terminals by using duct tape & fixing ties?
92cb39d5-31ba-4aef-ba7b-bffcdb07090b | checkpoint | Butterfly dampers are installed and they are in a fully opened position and air tight sealed?
f6619adb-a3cc-47ef-a0a9-e6d87714c921 | checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
ae22492c-bf18-46c2-b2a6-793503a49ad6 | section | Access Panel:
591611c5-2d2f-4918-8dc2-5aabb168f7b2 | checkpoint | Access Panel
da0894c0-62da-5a09-a487-b1f2e1dc70bc | textbox | Inspection Date:
c21f4cbb-388f-4079-a149-73c177cb3629 | checkpoint | Access Panel location has been marked on floor as per RCP and has been checked
f6c39d68-800e-434f-b045-e92dc2331383 | checkpoint | All other other services do not impede access
d4b4022f-64fa-4d41-96f0-d88077aa99bb | checklist | Ceiling Closure Checklist 2 Rough In [Q] |  | Ceiling Closure Checklist 2 Rough In [Q]
ad62fbf1-9d8d-4fe6-8e97-e8a4162fea7c | section | Air Conditioning:
01c8dc8e-fa93-4ff9-9042-ed9af9a6a88a | checkpoint | Air Conditioning
8e51c5fa-401d-5087-bfb4-c3509a743e72 | textbox | Inspection Date:
70dfdf18-6b82-4a3c-b967-346316e76d6c | checkpoint | FCU’s are installed and other services are not impeding access to fan coil?
30550476-d482-4464-9262-b7e701142eeb | checkpoint | Wiring connected to indoor unit electrical box?
6abe70a4-56af-45bf-8a83-6e3157848062 | checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
53c453e3-8fe6-429c-a6bf-e641f753dcbc | checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
58fce5b5-e5ad-4443-9d36-6c00c7946c98 | checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
51950454-f6d7-40e6-aa5b-a27ef3c8b425 | checkpoint | All FCU flexible ducts connections to air terminals and spigots have been air tight by using duct tape?
183d5150-241b-4bcc-822c-96dfbbcd3f75 | checkpoint | All FCU flexible ducts installed and supported by intact load spreader?
334601d8-ea9a-47ac-ba51-42692cab8f2d | checkpoint | All FCU flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties
ed4ce93f-2aa9-46b9-9935-4ac75c9431e7 | checkpoint | Are the zone controllers installed correctly and easily accessible?
b467560c-2932-423f-a2d2-f51e7c2ef85c | checkpoint | Are the zone motors wired correctly back to the zone controllers?
bd4f272e-abf5-4788-a2a7-6ddbf0527057 | checkpoint | Zone motors are installed and connected with junction boxes?
62a2317c-fc00-418c-a8b8-a4a86c085fa7 | checkpoint | Zone motors is side face?
af42bdb7-7fcc-4b75-88e4-601fc4581fbd | checkpoint | Supply boxes are installed and supported at correct location in the middle of bulkhead height?
6b9d46e1-624f-4997-b2c0-0dc7c92a8893 | section | Ventilation:
5c401f56-bb8f-4039-b919-bd70333a347a | checkpoint | Ventilation
55b43c4c-48a3-50a4-bd9e-7aed8eef78c5 | textbox | Inspection Date:
9386f8a4-a4e5-4d21-b3bf-79cf57b091d7 | checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
5e987715-6002-4b6f-8a97-f3d88cc725c2 | checkpoint | All ventilation flexible ducts connections to air terminals and spigots have been air tight by using duct tape?
6a30cca6-8ae2-4e91-a5e6-ec0cd49c7890 | checkpoint | All ventilation flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties?
a4e1c4b8-b072-48e0-b819-5b967d2d3b64 | checkpoint | All flex are installed and supported by intact load spreaders?
9bf0974c-e433-4bf2-a0ae-3dca8f10ba12 | checkpoint | Flexible ducts on the right location and not jammed?
49bc6186-501f-4da9-aaa4-c430f5cd3375 | checkpoint | Butterfly dampers are installed and they are in a fully opened position and air tight sealed?
54e16041-413e-4731-bcbd-e59a1d452659 | checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
f3895704-1924-411a-9aba-297650687b01 | section | Access Panel:
259288df-6886-4d87-b3e7-85329ae074d2 | checkpoint | Access Panel
44956548-9418-5d01-a708-30ea3c80571d | textbox | Inspection Date:
aa479cca-2c7c-4301-8fbe-357c7701560c | checkpoint | Access Panel location has been marked on floor as per RCP and has been checked?
52f33c4a-840d-49d2-b253-59cf071ecc94 | checkpoint | All other other services do not impede access?
28f41ef3-18c6-4b89-be69-0451dcd15e5c | checklist | Common Area Fit-Off Checklist [D] |  | Common Area Fit-Off Checklist [D]
f21a27da-309a-4e96-8c32-6bc91fe47f1b | section | Common Area Fit-Off Checklist
414c78d0-93a6-4f5d-98ea-9e957aff17c2 | checkpoint | Lobby supply grilles fitted
fe781843-48e2-478c-8f38-23f26155c29e | checkpoint | Lobby exhaust grilles fitted
5b3835ce-87a7-4c69-8add-8d420e30211f | checkpoint | Lobby Relief VCD is installed and the motirised actuator is fitted off and wired
32f5d07f-9d14-4b91-acea-e7248f3c9b39 | checkpoint | Lobby relief grilles fitted
ade336f2-678d-4214-96b4-a714d8cb7a03 | checkpoint | Stair pressurisation grilles in the stair shaft fitted
871a8387-3bb8-4332-9d7c-7251f9aabfd6 | checkpoint | Stair pressurization VCD / OBD is installed
16f21f7d-e1e0-4d51-b98a-937b19540932 | checkpoint | Carpark supply grilles fitted
a35ac5e4-b4dc-48fe-9462-4d99bbabdc72 | checkpoint | Carpark supply VCD / OBD is installed and the motirised actuator is fitted off and wired (if applicable)
5d7a805d-ce10-4371-83ae-c977f9432dc4 | checkpoint | Carpark Exhaust grilles fitted
fba05b49-f8cf-4cd3-bdc6-d883e0e34b62 | checkpoint | Carpark Exhaust VCD / OBD is installed and the motirised actuator is fitted off and wired (if applicable)
c5084299-cb39-4ccd-9ebe-06640afe7c53 | checkpoint | Garbage Exhaust grilles fitted
2f33d303-732f-449c-a697-87b396bf3a2b | checkpoint | Garbage Exhaust VCD/ OBD is installed
c624608a-4d16-461e-ace1-2fab00058d91 | checkpoint | General Exhaust grilles fitted
727ef2d2-4432-40e8-951b-75a60e1bcb67 | checkpoint | General Exhaust VCD / OBD is installed
33f8605e-f7ab-48a3-9539-58376236ba09 | checkpoint | Loading Dock grilles fitted
812fc18d-1b80-4dad-91c5-8019f5b1a3e3 | checkpoint | Loading Dock VCD / OBD is installed
11c49b50-c828-40fe-838f-e18f5f206a07 | checkpoint | Pump Room supply grilles fitted
bc7aba56-4546-44bc-8072-c5ee0fb784a8 | checkpoint | Pump room supply VCD / OBD is installed
1a53bd15-bcfc-47e1-9147-e0383fe40f57 | checkpoint | Toilet Exhaust grilles fitted c/w OBD
6734db87-4979-4f6d-b10a-913cd1aeba99 | checkpoint | Bike room grilles fitted
1bbccd6a-f66c-451a-a467-be5314a9c8bf | checkpoint | Bike room VCD / OBD installed
5d55b115-9beb-46d6-8172-99f7b57dbfac | checkpoint | Comms room supply grilles fitted
6a777ed8-90e6-4c56-a07c-2f207e8ce0f1 | checkpoint | Comms room VCD / OBD installed
015ea175-6567-4135-978d-5e4816b76bb1 | checkpoint | Main Switch room Supply grilles fitted
06cfa745-db07-4958-8ad9-051f05989e60 | checkpoint | Main Switch room Supply VCD / OBD installed
9ad0acf2-6fe9-485b-a19f-d38bb1a64433 | checkpoint | Storage room Supply grilles fitted
06043447-cf5a-4aa8-aba0-7307b375c514 | checkpoint | Storage room Supply VCD/ OBD installed
fd74a12d-dff6-4d78-855e-518cac8a53a3 | checkpoint | Bin room grilles fitted
fb54f461-63e6-4e5f-9ef6-d436b34fa609 | checkpoint | Bin room VCD / OBD installed
769a4ecb-85aa-45f3-aef6-625fbcda8810 | checkpoint | All fire dampers provided with an access panel as per mechanical drawings
ce67618a-1426-4e0b-b8f6-e51739cd3162 | checklist | Duct Installation Checklist [C] |  | Duct Installation Checklist [C]
7c6228aa-d16b-46ff-87b5-564f7e08aab0 | section | Duct Installation Checklist
9e5ac94c-dbbc-4728-b7cf-5a4354105b3e | checkpoint | Are drawings on site the latest issue
ab08f527-4fb5-4054-9d17-c315e7d26579 | checkpoint | Are plant and equipment location correct
41af4fdb-75e0-4213-8cc5-e3d23caef1f4 | checkpoint | Fan in the duct run has been installed
bc379083-69bb-4bc8-9c2a-3ae67d7a1fcf | checkpoint | Model of the fan is correct as per latest Fan Schedule
ab09eda5-54af-4642-a9d6-44d713a12609 | checkpoint | Duct size and location correct
cab29611-5a63-43d1-9af6-e0393a09f838 | checkpoint | Material and gauge correct
0c93763d-1c0c-433e-abac-fe078069ffa5 | checkpoint | Is correct support method being used - Risers are supported at each level.
3735cc83-7c2e-4b5e-bdeb-df1ccc8b208c | checkpoint | Is correct jointing method being used
3932787a-a9fd-41ce-89e5-5b4f243d831b | checkpoint | Are joints completed and cleated installed on flanges
e5efee34-9b38-4cc9-a14b-26a21a9f57f9 | checkpoint | Is correct joint sealant being used
0897b493-5708-4361-acad-687d66b4ccf7 | checkpoint | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
74d452fc-a859-4ac7-9f62-a8f4d11d76a0 | checkpoint | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
394e4760-0d73-48d0-a71d-592086fe70c5 | checkpoint | Is adequate distance between attenuator and fans been maintained?
ef0218b7-8b49-415f-bc39-79f1033d650d | checkpoint | Are the attenuator splitters in the plane of the bend ?
80f17622-0a7a-4692-8d51-6129bf1fd8ad | checkpoint | Are transitions close to attenuators gradual?
867a2eb2-52ae-48d4-a3f3-a3b76c70f5c1 | checkpoint | Is a settling duct between volume control dampers and attenuators allowed?
f5197073-1389-4b70-a3ba-cb2c48569ece | checkpoint | Are fire dampers installed and break away joint complete
ba9f6f20-d0cd-48da-b5e2-a6eb780533b9 | checkpoint | Are flexible ducts installed, supported and connected to spigot by approved mthod using duct tape on internal core and cable tie on outer core
0e32b379-683f-4a09-bd2c-5aa3a8746eaf | checkpoint | Is ductwork insulation as per drawings
6de5a886-7d50-4275-b245-10ccd77bf9b5 | checkpoint | Is ductwork fire rating complete
fa114539-e9f6-4b5a-9e18-590d099a8c79 | checkpoint | Are all spigots installed and dampers fully open
a6e56c5d-9167-49e9-b32d-1487a42ae49e | checkpoint | Are all access panels for fire damper access installed and closed
8add61ca-da28-475f-a11f-4f5047acc8ac | checkpoint | Is ductwork installation complete
5b144375-d4d5-4a80-9957-9a5a19e8ef2c | checklist | Ducting-Common Area [K] |  | Ducting-Common Area [K]
f49fece2-47e4-441b-98de-2db53fb9fff7 | section | Ducting-Common Area
efe3f4f0-4e26-447d-b039-17581dc5b969 | checkpoint | Riser
a3579c48-056a-44fc-bb94-ff628c960f3c | checkpoint | Are drawings on site the latest issue
4963625a-3d58-474a-ae75-06e5255d3736 | checkpoint | Are plant and equipment location correct
27de6423-e434-4c57-94e3-c2a944db7910 | checkpoint | Duct size and location correct
c72690b5-bc4e-46aa-8d51-a7f1266a5818 | checkpoint | Material and gauge correct
9cd965bc-172f-4a79-8567-1a13c036bb53 | checkpoint | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method
735fddc9-1727-45af-be2c-2321c7c56739 | checkpoint | Is correct Joining method being used
0fa42679-ae3d-4667-ae37-25be836282af | checkpoint | Are joints completed and cleated installed on flanges
1c878b3a-d11f-4a62-813a-756a6954969a | checkpoint | Is correct joint sealant being used
995133ba-1f55-41ff-89fa-957b9d98a14a | checkpoint | Is ductwork installation complete
c9935626-9d2e-4b09-a4a9-0812ea20f2d5 | checklist | Fire Damper Checklist [H] |  | Fire Damper Checklist [H]
f027f3b9-ee9a-44eb-be0f-dacf0375bc3d | section | Fire Damper Checklist
bd826f8b-e7e8-4587-9c4e-6fa567f3678d | checkpoint | Penetration details have been captured
6756fde6-f961-4453-9866-abebdba1dded | checkpoint | Position damper centrally in penetration aperture as per system drawing with IBS backing rod and temporary supports or packers.
0542e7bd-2a88-4a82-b555-6d7609ea8120 | checkpoint | Galvanised steel casing positioned centrally within aperture is 0.7mm or greater gauge
a30b535e-e5fc-4cad-beed-bcc4f2175d4b | checkpoint | Killargo fire rated mastic has been applied to the gaps between fire damper, casing perimeter & building element on both sides.Gaps between the fire damper and wall no greater than 25mm.Ensure fill depth is 50mm.No evidence of cracking.
3cd5a91d-799c-42bd-991e-1ed2c7f40238 | checkpoint | 0.7mm minimum steel angles at least twice the width of the penetration gap, fixed to damper casing with steel screws, bolts or pip rivets and fixed to wall with steel fixings at maximum 150mm centre spacing or 2 per side for casing lengths up to 250mm or 3 per side for casing lengths 251-400mm
c8fdce75-1b1c-42a6-b6eb-adeeb5a07410 | checkpoint | Ductwork is connected to either side of the casing with nylon bolts on the flanges as per the AS1682.2 break away joint method. Bolts do not exceed an 8mm diameter.
a257e59d-4b64-4a47-97b6-ffbad9133784 | checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
50c59366-f308-40eb-9fd0-62b9f54f933a | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
2381b962-d6fb-4824-a22b-15bdc4ceddcb | checkpoint | Pictures attached
cfe7d9d6-1b14-4a8f-bb53-ddba066663f3 | checkpoint | Signature (Contract/Subcontractor Assessor)
bed39aa9-c15f-4186-8c62-4294c6f5b0d7 | checkpoint | Signature (Builder Representative)
d443192e-6e3b-4eaf-a9ba-e7648cda5eb7 | checklist | Fire Damper Checklist [N] |  | Fire Damper Checklist [N]
98bdb0cf-e071-4873-95ab-9a438e77ae84 | section | Fire Damper Checklist
f069c932-049b-4169-b29f-4fa2ffaf2dee | checkpoint | Penetration details have been captured
ea2a0160-13d3-4516-b6b4-a5dda1ce3ea4 | checkpoint | Position damper centrally in penetration aperture as per system drawing with temporary supports or packers.
56711faf-b790-4b5a-bc0f-134300fe3b13 | checkpoint | Fasten 0.7mm thick steel mounting angles or brackets to damper with steel self drilling screws or steel pop rivets and to the building element with appropriate mechanical fixings at 200mm centre spacing or 1 per side as shown on system drawing.
a8ca5dda-5e0c-4515-8a06-c358d3bf2aa6 | checkpoint | Killargo fire rated mastic has been applied to the gaps between fire damper & building element on both sides.Gaps between the fire damper and wall no greater than 25mm.Ensure fill depth is 50mm. No evidence of cracking.
5da1cb93-a70d-4cc5-aade-3ab549e2432a | checkpoint | Ensure convenient access to fire damper for visual and/or maintenance inspections is provided.
82ce40cc-10b6-4448-86fe-f3e8f0160717 | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
1673dea4-4dbe-4cca-825d-4ebd2ffebac0 | checkpoint | Pictures attached
916de97a-164c-4f50-96d3-9be1f94bdc8c | checkpoint | Signature (Contract/Subcontractor Assessor)
e5f20f94-47ff-4e68-a5d4-420f48b87d80 | checkpoint | Signature (Builder Representative)
fc32a0ec-d698-422c-b52b-522a9dbb5248 | checklist | Fire Damper Checklist [O] |  | Fire Damper Checklist [O]
96195081-ddca-4153-8f14-8a4993dd5968 | section | Fire Damper Checklist
a950d67d-4b86-4e37-8ec7-be271ae7c295 | checkpoint | Penetration details have been captured
83b101bb-7254-4342-9706-2120ffeb91a2 | checkpoint | Does the fire damper mounting frame completely penetrates the wall or slab into which it is installed?
a15a6d65-3ec0-461a-adbd-f5b65bb65a18 | checkpoint | Does the damper mounting frame retained either, on both sides by means of flanges butted against the face of the wall or slab and fixed to the mounting frame or on one side by one flange only, fixed to the wall and damper frame allowing the damper body to expand without distortion to the blades?
fcfd27cb-46a7-457b-9b48-0dc124e452b3 | checkpoint | Does the penetration for the fire damper have clearance on all sides equal to half the width of the flange used to retain the damper frame?
a9ae480a-b246-4d3a-82eb-9e6c7930d389 | checkpoint | Is this clearance filled with an approved non-combustible compressible material such as rockwool to the full thickness of te wall or slab involved?
4f2d57b0-d613-4056-8ba5-a527c6252674 | checkpoint | Does the method of attaching ductwork to fire damper ensure that the damper remains functional if the ductwork is damaged in any way and must allow the ductwork to fall away?
3f45a909-3432-4f70-a954-8e86270fafc0 | checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
779fe149-e6c3-4de4-a78b-d93c291fe473 | checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
42035c92-58a7-4d13-9171-6e3af66399cb | checkpoint | Pictures attached
62e55501-3074-464f-a9f9-6de1730b0d83 | checkpoint | Signature (Contract/Subcontractor Assessor)
e261a335-fb13-4f41-b84e-6895f6fa6de3 | checkpoint | Signature (Builder Representative)
2e102e84-bc92-4ce5-b958-5c71d6ea34c8 | checklist | Incident Report - Checklist |  | Incident Report - Checklist
af256410-cd82-42d4-b9b4-5478f1100c5d | section | Injured Workers Details
fe05e6ef-4737-4cc3-9d64-e5973c1456c8 | checkpoint | Injured Worker
a3ae49c4-7b95-588f-9071-f57be164ae3f | textbox | Name of Employer of injured Person(s) (If any):
28871292-0d5e-5df6-9f77-8cf158b2c292 | textbox | Business address of Person/Organisation in charge of the equipment:
b1e63876-0cbd-521c-ad7a-83ee97316860 | textbox | Full name of Employee:
6c6d1e3f-f710-5ff5-9229-bf7ca9faf3fc | textbox | Date of Birth:
8665aa36-5e26-5694-995d-2c0db1397354 | button | Sex: | Female,Male
49dd8e1c-1e56-5a25-8cf0-14e46f979b4e | textbox | Residential address and telephone number (if known):
a1585c3d-a79f-5370-8215-6fd69b1ad8c9 | textbox | Occupation of Employee:
340600c0-5c22-4329-935e-43fc8092f979 | section | Incident Details
92ea6d15-c47a-4ece-a192-69aefab3bcc2 | checkpoint | Incident
877d1322-3157-55a0-9dd9-3ee674249043 | textbox | Date of Birth:
2215c660-4543-53ef-9d93-2e2f448833fc | textbox | Place/Location where incident occurred:
1feb952e-50ce-5a69-b93d-42c06e684159 | textbox | Work/activity being performed at time of incident and equipment being used:
deabdb82-7e69-5fbc-948f-804ad1331844 | textbox | Brief description of incident:
e19ca196-6b34-5b17-9c5d-fda292954ba9 | textbox | Treatment given/action taken at the time of the incident: (Attach Statements below)
4fd2780d-1ba2-55c8-84ab-7b5e0f12cce4 | textbox | Name of Witnesses or Name of Person(s) who first attended the scene: (Attach Statements below)
11e58049-157c-540d-a3cb-a9ec28696670 | textbox | Action taken/intended, if any, to prevent recurrence of the incident:
150cca82-0600-5d6e-a47d-b1a72656cdaa | note | Add diagram or picture of incident below
642bf4fe-1beb-4f7e-90a7-0cf84247342a | section | Treatment Details
bad21572-08fd-4ee9-99b3-8010ed7c2630 | checkpoint | Details
926c7c1e-d269-5427-9fef-965bbd41c11a | button | Did the injury necessitate loss of time? | No,Yes
a09a2557-a356-5df9-979c-38feb30c4ecc | note | If "Yes" selected
e6d9485a-2afb-5e07-bbef-cb167c5eb657 | textbox | Name the clinic/medical centre attended:
48ea3bd5-842d-5fc5-b975-ddeed19d980f | note | Attach WorkCover Certificate of Capacity (Attach below)
de61550a-11be-50e6-8f96-63b64526b41a | button | Was an ambulance required? | No,Yes
d89251d8-a4d8-598c-865c-505592a68a41 | button | Was the incident reported to WorkSafe Victoria? | No,Yes
4b8fdf22-790e-5181-aafe-326e7566698b | note | If "Yes" selected
73ab8597-7418-53e6-853a-65c8d55381e3 | textbox | WorkSafe Incident notification number is:
64cb4a3a-ded9-490f-bd64-6397c39d4058 | section | Form Details
dc779387-9e60-47f5-9d06-17fb91a8e59b | checkpoint | Details of Person submitting this form
c734a79f-423f-55ee-92a3-ff417f26b994 | textbox | Name:
b8df6b70-9df1-5306-88af-123a70f51e28 | textbox | Position/Title:
46cffef5-abc9-5c60-98c5-c89bbf97240f | textbox | Date:
da17b1ab-4bce-530d-9bf9-d0d4fcdae3b5 | button | Type of Injury (Filled out by OHS Manager): | LTI,MTI,FAI
e162d3fc-d424-4519-92cf-af8f8bf89dfc | checklist | Jet Fans [L] |  | Jet Fans [L]
f7db29be-9b88-4c0a-8ac2-b57c04b633c6 | section | Jet Fans
60dd8ad1-fbae-4508-8b76-03b6bc284a1f | checkpoint | Are drawings on site the latest issue?
ef81dc3e-2df2-4a01-8bc5-684a48edcd2c | checkpoint | Are plant and equipment location installed correctly as per drawings?
232aac02-eccb-4000-b150-c29bbe2b4dce | checkpoint | Model of the fan is correct as per latest Fan Schedule?
f2c9ca10-e8e8-461f-a49c-be1ab467e6a5 | checkpoint | Is the fan attached to the ceiling structure of the carpark with hardware appropriate to the size and weight of the units (Typically 8mm fasteners)?
727b0ad9-3424-4de6-ab57-c7690e9fd605 | checkpoint | Are the correct anti-vibration mounts being used ?
689b436d-86ae-44d7-b93d-74c987909949 | checkpoint | Is the Fan discharge parallel to beams?
9b842210-79bd-4135-a0bb-48f7f51f97f7 | checkpoint | Do we have sufficient Clearance?
926eb521-da39-4d2d-af5d-f8e5f3fee0ef | checkpoint | Is the obstruction too close?
2dd4aea7-96f8-4619-9eb7-ecf6902b0fcb | checkpoint | Is the fan installation site coordinated between trades to avoid clashes with pipe work, signage and other obstructions?
5403c861-8e1e-4f98-847a-e3c7ead36ae5 | checklist | Job Details |  | Job Details
1533bd7d-ce50-4d51-bb7d-75adf7e5aa2c | section | Details
d9934cd8-b12a-4497-9a03-4a8a292add24 | checkpoint | Site Info
9b9fd4f7-78f1-544d-82a0-b28b9d2e71f9 | textbox | Site Address
fc606004-3e7d-5e6e-9643-03a84e496e8c | textbox | Builders Details
a1312c53-6b63-5bea-b028-d8bd1f4c0298 | textbox | Project Managers Details
2aa54e1f-3a2a-5bac-a1ef-ac22c863ea54 | textbox | Site Managers Details
f3056fcb-7968-4a62-a932-8e3d3561a83d | checkpoint | Latest drawings (attached or referenced)
7ad269ac-241d-4c40-badf-747b93e14a29 | checkpoint | Scope of Works Attached
2090e43f-bb61-4f73-b0ba-34876b7ac698 | checkpoint | Additional Pre-Start Docs (attached or referenced)
55431c1b-a553-4e47-b564-979d92778ae2 | checklist | Lobby Area [J] |  | Lobby Area [J]
92ae0ef0-b56e-4c90-8621-e7fbde1cef5f | section | Lobby Area
bb220db0-3502-4771-98df-23b521790cff | checkpoint-no-value | Inspection Date:
393eff40-637c-59cb-892b-a3684c88d668 | textbox | Date:
3df9ab23-c741-4b2f-bf12-7833a2e5a2fb | checkpoint | Other services installed are not impeding access to fan coil
23327e07-c3e8-4675-91af-38051e751e2e | checkpoint | All Ductwork passing block walls are flushed and sealed
636f153e-6a87-45a4-b842-c1795352c2f1 | checkpoint | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed
e1997032-aabd-4bb3-b7e6-c319f43d5f67 | checkpoint | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed
f02c94dc-1aaf-4e63-bad6-cc20be9758c6 | checkpoint | Refrigerant pipes passing through fire rarted walls are sealed at wall penetratiobn by using approved material
dd910f39-f1c4-4dd5-9a99-3b15c57805af | checklist | Prestart OH&S Documents |  | Prestart OH&S Documents
ce0c1b2d-eb70-4a08-8c13-b2a079d8d038 | section | Details
83a3f7b2-45c2-4232-82fe-c6c8cacc96bb | checkpoint | All Pre-start OH&S Documentation Completed, Reviewed & Attached
b93b6cb9-c2e3-5572-b707-b5c4d426b16e | note | Public Liability and Work Cover Insurances
407a9f65-6c4d-572a-88a2-02165d68d312 | note | Company Safety Plan
27f2f8d6-5fa4-5010-a7b7-dc9fd668edcf | note | SWMS & MSDS (Attached below)
017d5b58-82fc-5154-8c52-1e2cf62df76a | note | Additional Prestart OH&S Documents
4cf6d546-e0d1-4a1c-b975-d3820d92ec12 | checklist | Sign Off |  | Sign Off
ff599e04-678a-4281-954f-c2d1bbb4424d | section | Details
10697934-a009-4101-9baf-c4c03bca62de | checkpoint | Sign-Off Completed as per below (Pass once complete)
47a7a642-1602-590d-8fa5-26b061ee5deb | tickbox | Contract/Subcontractor Assessor Sign Off
4f466ea9-99fd-5278-ae22-6a6b68aa1711 | tickbox | Builder Representative Sign Off
77642a92-4e7e-560e-a027-8ce5e0171f77 | textbox | Inspection Date:
e4e2a572-f7ed-45af-8471-9ec00d02f63e | signoff | Request Sign-Off(s) + Click to Add Signature(s)
44f913f8-e6b8-47a9-80db-d67eb4984b28 | checklist | Sign Off (Fire Dampers) |  | Sign Off
075f7f98-f721-4ec8-a8f4-8dac19996c72 | section | Details
973331ac-69fb-4e3e-911c-5c30033f6620 | checkpoint | Sign-Off Completed as per below (Pass once complete)
3e08f6cf-7364-546a-bd26-d005c2a62bab | tickbox | Pictures/Comments attached below
d383dc5a-4115-5e55-a5b4-a7d0150b9465 | tickbox | Notes/Additional Comments
0cabdf11-5f8b-5407-b01d-6ca124641415 | tickbox | Sign-Off Completed as per below (Pass once complete)
2d5f3170-36bd-5dc4-8419-643f35df3a4e | tickbox | Contract/Subcontractor Assessor Sign Off
6c0a0b5c-ceb8-5221-a167-74be57119807 | tickbox | Builder Representative Sign Off
fb8a9f63-be2a-4836-9106-47e065c5b777 | signoff | Request Sign-Off(s) + Click to Add Signature(s)
94b70a81-635a-4725-b333-b2420b9d965b | checklist | Smoke Damper Checklist [I] |  | Smoke Damper Checklist [I]
dc3d2b24-f3b5-4f79-aae8-11d6f6542320 | section | Smoke Damper Checklist
5d1cb12e-1c5c-414d-bb97-27148e2448a9 | checkpoint | Smoke damper must be placed in the duct work so the closed blades are with 610 mm of the smoke barrier and before any duct inlets or outlest (See photo attached)
f09b6191-1f2c-4dfb-85c0-3666bcaf99ee | checkpoint | When joining or fastening the damper to duct work, dampers shall be fastened with M6 bolts or M5 screws. Fasteners shall be spaced a maximum of 305 mm center to center with a minimum of two fastners per side.
bb3e67cc-450e-4934-a4a5-6d8db90dae45 | checkpoint | Smoke dampers must be sealed between the damper frames and duct work. The sealant shall be pressed in place to dispel any air and shall be applied to one side of the damper's face. Use the minimum amount of the material to completely seal the joint.
42d2b0ca-3495-4065-b1a9-762627c75515 | checkpoint | Access Panel for Actuator and wiring according code and regulations
5059e37e-7763-4b5a-a067-f625f499421a | checklist | Toolbox Meeting |  | Toolbox Meeting
8194bd17-54aa-4278-a05c-24ab54b87701 | section | Details
71e2200d-bab3-4131-a9f5-32746941774f | checkpoint | Toolbox meeting completed & Specific Document(s) attached
7000d3fe-68d5-5534-97ab-ae02712f7b26 | textbox | Date
d2a9f8f3-cf92-5a7f-914c-3b3b24121907 | textbox | Site Address
68b3dceb-1e6b-5f48-9371-ad1e3009a3e4 | textbox | Toolbox meeting topic
f0a476cf-f061-5d4d-870d-e6bd00ff2498 | textbox | Toolbox Item 1 - (Add any resolutions below item)
14221379-bd84-522f-842f-72f9481d8ca2 | textbox | Toolbox Item 2 - (Add any resolutions below item)
d13ba46a-c47f-5f86-9bb5-4bacfd179758 | textbox | Toolbox Item 3 - (Add any resolutions below item)
4aa8ec1e-f87d-528d-996e-e734a5a8729b | textbox | Toolbox Item 4 - (Add any resolutions below item)
b9b731bc-8bd0-4483-a55e-cb6bb861e17c | checkpoint | Toolbox meeting pdf attached (Add below)
7d0febe9-b79b-5b08-ab2f-9a24be6b63aa | note | Broad Air takes safety seriously and we encourage all persons representing the company to speak up if something is not right. If you find yourself unsure about something when it comes to safety, ASK! There is no such thing as a stupid question.
aebe7854-b7b6-400d-8897-b8417cb8f877 | checkpoint | Sign Off – By signing this page you acknowledge your attendance of this toolbox meeting and your co-operation with our policies & procedures
c71bfe26-9252-458f-bd5f-de73e940123f | signoff | Click to 'Add' signature's of each attendee
ee457f12-73cc-42b4-90a7-316d66c7e8ce | checklist | Variation (21/05/2020) |  | Variation (21/05/2020)
9538f66e-21e1-45e0-b82b-bcdeb6d9bae1 | section | Details
5f194963-7e9a-4d51-92d4-fa2a08e5f2db | checkpoint | Variation Details Complete (Pass once inputted)
65737232-f484-5697-9fbc-269340c56d53 | textbox | Variation Name
44141221-7fda-588c-9f08-c8358ba7893e | textbox | Variation Description
3bc27542-231d-58af-b72f-2294bd42cc4d | textbox | Materials & labour breakdown (Names, Hours & Material(s)/Quantities)
25370633-4495-517c-b49e-d5f4c3fa7e08 | textbox | Acknowledgement (Who requested the work to be done)
e02e2995-6cc6-58bf-8c57-eb4f24d38339 | textbox | Signature/Reference Mail (Who to send the variation too)
c3229232-b9ff-4ccc-9271-312023fde940 | checkpoint | Supporting Documentation (Attached or Referenced)
f576b3a7-27e2-594a-8994-6bcca4291727 | note | Add Photos/Comments of variation work below
28cc7dca-f609-4f27-8d67-f1463404a992 | checkpoint | Variation Sign-Off - Click to Add signatures below
9461154a-5d1d-5002-8d00-5ebca965f1fa | button | Broad Air Representative Signature Added below | Yes,No
15a29d66-371b-5ae5-a3e2-d4f84a9c0fd3 | button | Builder Representative Signature Added below | Yes,No
b324662f-4e67-452b-bc1d-402f1fed13ca | signoff | Click to Add Signatures of Wilson & Builder's Representative
a96dacf0-bfd3-4a5d-9ed7-b5113426c06a | checklist | Ventilation Checklist Commissioning [G] |  | Ventilation Checklist Commissioning [G]
fe97addd-775f-4f4b-92a4-d0f16fd9ad63 | section | Ventilation Checklist Commissioning
fc3774f4-de97-49ba-b4ce-1c61ee09949b | checkpoint | Fan has been tested and is operational?
a5fe4bd0-d29e-4883-938d-f42351925d0d | checkpoint | Adequate flow has been achieved in bathroom 1?
dc821812-6d7f-49a2-b1e8-ffa1aa0c95a3 | checkpoint | Adequate flow has been achieved in ensuite?
41e1c60b-1f32-42f3-b490-424120485dc9 | checkpoint | Adequate flow has been achieved in laundry?
d2fa39b3-2c6a-4489-a71f-0ac1a8ea7034 | checkpoint | Flexible ducts on the right location and not jammed?
69497ef6-5d17-4f65-9af6-ceac90cc2349 | checkpoint | Range hood has been tested and is operational?
2210ee40-c278-4fec-8d0b-851fb09dc72c | checklist | Ventilation Checklist Commissioning [M] |  | Ventilation Checklist Commissioning [M]
1af8f0a3-bfe1-457e-a766-6301615434b7 | section | Ventilation Checklist Commissioning
2c66da8f-03b4-4787-85ca-69c2c7878aab | checkpoint | Visual survey of installed area. Are all items secured, compliant and no loose elements?
22f1d502-fb24-4de7-8cc3-c9c072d66e1b | checkpoint | Fan has been tested and is operational?
26119ec8-7ed2-48cb-9c74-e86383cb7920 | checkpoint | Adequate flow has been achieved through the grille / outlet?
25490de1-07b2-4621-8b56-ec67fdcd0e6f | checkpoint | Does the fan comply to work with control strategy as per the spec?
105d2099-9a20-40dc-b0ec-1da99a8acd08 | checklist | Wall Closure Checklist 1 Rough In [A] |  | Wall Closure Checklist 1 Rough In [A]
3530c32e-1a9e-4d55-8124-ccf215c2e7ba | section | Wall Closure Checklist 1 Rough In
5453fbe3-b7a3-4cbc-ba6b-234818d35511 | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule?
8a3f7307-aa08-468c-9855-568624725106 | checkpoint | FCU installed at right height to ensure grille is centred into the bulkhead?
f47f0b50-2594-4fe8-a1f8-c5b6fb2c31e0 | checkpoint | Thermostat control cabling has been installed?
8c98ea00-e216-4319-8d67-40ebe851d324 | checkpoint | Thermostat location is correct as per RCP?
31edff08-c26f-49d0-9c3b-d8fc3646211e | checkpoint | Drains have been run to Tundish and does not protrude wall framing?
b43d6fea-cd56-4bcd-8c79-3ff5ad1cb14c | checkpoint | Drains tested and witnessed by Boad Air?
28198a2e-eed8-4480-90e4-bcbec58fd065 | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
28cfd092-d70d-4b65-802b-58839e4d0f48 | checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
21d26b91-d6b5-47f9-ab3f-0b285b259aeb | checkpoint | Refrigeration pipes run through cavity without being kinked or damaged?
77a0d971-4c8d-4fad-af06-7c5ccc1c852f | checkpoint | Pipe projecting the wall cavities in balconies have been sealed?
b50b454b-6be2-4790-9ca7-ea64f55c5886 | checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
7ee730ea-4ee4-4666-bd3a-a693efd5de85 | checklist | Wall Closure Checklist 2 Rough In [P] |  | Wall Closure Checklist 2 Rough In [P]
52fdeac6-7bba-4480-a699-ae53658283d2 | section | Wall Closure Checklist 2 Rough In
173b6b43-db28-4897-a4c9-f1b5056ecf06 | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule?
ce4ae4ce-e3c7-4cbc-bca7-8457313a265a | checkpoint | FCU installed at right height with 5% slope towards the drain point?
938df39e-fd7f-4713-81f8-32bc5ba75013 | checkpoint | Thermostat control and zone control cabling has been installed and location is correct?
c3c26faf-11ab-40c7-bda3-4827ef1f8883 | checkpoint | Drains have been run to Tundish and does not protrude wall framing?
cbbb0116-3aac-49ca-a826-f4b9f4624d3a | checkpoint | Drains tested and witnessed by Boad Air?
a46d09f9-2e18-45e7-84d9-cf80f43600e4 | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
4dbb3cf1-74b7-4848-94ee-31754c2b95b8 | checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
a86bd23c-2cc6-4498-aa62-b92c9f49bdfc | checkpoint | Refrigeration insulation is not damaged?
0a2147c9-5cf3-4249-b1a5-2862e265a474 | checkpoint | Pipe projecting the wall cavities in balconies have been sealed?
211f6c82-18b0-4987-b716-5276e19eecf9 | checkpoint | Refrigeration pipes run through cavity without being kinked or damaged?
dd64bffe-b613-43ac-b295-c5651c8f8684 | checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
a28281ec-db29-45e4-a035-92b0407f7a73 | checklist | Ω (Deprecated) Ceiling Closure Checklist 1 Rough In [B] (v0) |  | Ceiling Closure Checklist 1 Rough In [B]
39631992-26b6-457f-b7a8-3c29ae59df09 | section | Air Conditioning:
44ed83aa-0456-4212-ab7f-1edf3ae258d9 | checkpoint | Air Conditioning
b2d61e23-e2e2-5c7b-b6f1-306a907be304 | textbox | Inspection Date:
2fb3d805-daee-45db-9388-f2437927a8f1 | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
edd3461b-06e4-4532-b0dc-40a4e35595ee | checkpoint | Units all hung with isolation mounts and with 5% fall to drain point
6cbfb9c7-60a2-48ce-ac72-4b5f9ea95f2b | checkpoint | Other services installed are not impeding access to fan coil
98e22e56-07c9-4191-a8b2-02722d324e2d | checkpoint | Wiring connected to indoor unit electrical box
a0023d31-5558-4ed1-b9a1-78b2f403622d | checkpoint | Refrigeration pipes run is not exceeding the pipe length limits in VRV systems?
20876a9d-cba4-4202-95d5-2facf10c3aae | checkpoint | Condensate drainage is in correct location & height
474a3bad-c339-4c9a-ab3c-ba94e362b501 | checkpoint | Filter Track for return air have been installed at the back of unit
4b27f24c-c956-4e11-98d4-1390960f48e1 | checkpoint | All flexible ducts connections to air terminlas and spigots have been air tight by using duct tape
3e029ff2-a868-471e-ac41-3e3099a102ac | checkpoint | All flexible ducts connections to air terminlas and spigots have been secured by using fixing ties/cables ties
1d7ca123-00ae-46bd-8155-d808808a0fd5 | checkpoint | Fresh air to apartment
68a044ca-c8ce-45e4-8038-005ca4aa3df7 | section | Ventilation:
0ae13d81-4142-4fcc-9b4e-8e08b78deb39 | checkpoint | Ventilation
c6a5ad1b-3bfe-5016-afdd-16f6ce508a30 | textbox | Inspection Date:
73466996-cad3-4a56-b2ce-f8177b96b9c3 | checkpoint | Fans installed within ceiling areas are in the correct location as per Mechanical Drawings
227c0317-c2ce-41a1-ac09-5008d75a3c93 | checkpoint | Fans Installed correctly with rubber isolation pads
c19fa4dd-cf07-4622-9c2d-8b0e567b96ee | checkpoint | All Flex has been run to correct location
49f27b73-0597-4243-ad84-99e8411245a0 | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
1d0b215f-9960-493d-a9e0-ffe222d2eead | checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties
24b4a3c6-8b44-4f23-9027-37987a0daaa6 | checkpoint | Butterfly dampers are installed on the PODs grille neck and they are in a fully opened position and air tight sealed
1fd10c4f-e194-4f2e-a8eb-30d76d5792f4 | checkpoint | PVC sleeves has been installed in wet area walls
3d13ad52-50e0-4761-b2f6-028fc6031b91 | checkpoint | Vent boxes are intalled in correct location as per RCP and SEALED
8601e567-5f46-421b-9d39-142db35ccf8c | checkpoint | PVC ducts have been hung and supported indicidually by using hanging straps
efdb3384-9234-4108-94a8-ba4761dd0cf4 | section | Access Panel:
7555451f-d9bd-44ca-a9c0-d0c7ff6eb535 | checkpoint | Access Panel
fff4c51b-0b26-5f1b-8116-3bab9d6c15fd | textbox | Inspection Date:
30a93de7-1e8c-4c0e-94c1-a1eba7020f34 | checkpoint | Access Panel location has been marked on floor as per RCP
3e248d4b-28a9-44f4-b86e-be7b90a31740 | checkpoint | Access panel location allows sufficient access equipment
e29ef7de-1f4b-48fc-98df-6d449278585d | checkpoint | All other other services do not impede access
ad2f70d6-698e-4cb3-9c2c-12c68921e6fc | checklist | Ω (Deprecated) Ceiling Closure Checklist 1 Rough In [B] (v1) |  | Ceiling Closure Checklist 1 Rough In [B]
b9b72e83-6bcf-481d-a889-d1dcb0301580 | section | Air Conditioning:
906ea562-eb00-464b-ab08-5d69077352c7 | checkpoint | Air Conditioning
3aa7153d-c0aa-56d7-8379-2b7b21c2a88b | textbox | Inspection Date:
7097ed58-f534-4c9d-b884-17a6499269b9 | checkpoint | FCUs are installed and other services are not impeding access to fan coil?
2137a26b-612d-4587-a28c-ce089e158407 | checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
54a6b24f-a6be-42b3-a185-5ad7aaed41ff | checkpoint | Wiring connected to indoor unit electrical box?
7345e1a0-c8d9-44a5-928e-1fafed03d88e | checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
0e2d2d2d-04fa-4903-bf15-04262ad7283c | checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
84160a2f-d292-48e8-8b19-ae7c45b28f1e | section | Ventilation:
1ec48bdd-bb4f-4d29-8402-2804d162d30d | checkpoint | Ventilation
0562d568-5472-502e-902b-ddd648f1eb58 | textbox | Inspection Date:
4957685f-39e7-4a9c-b1c2-b8ae9f81e995 | checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
8c7044db-16a9-4514-94c5-eff32fe9b51b | checkpoint | All flex are installed and supported by intact load spreaders?
668ca2d2-d3bf-4e27-9c79-c0d5fa66a7a9 | checkpoint | PVC ducts have been hung at correct height and supported by hanging straps
368896cc-af10-48a8-ab2f-8927cfcc2795 | section | Access Panel:
73b2b8be-81e8-4d8c-b8c1-5de1503e3f1d | checkpoint | Access Panel
f92fbc1d-023d-5119-aaa3-3678291ca6ce | textbox | Inspection Date:
420bd728-1eba-4436-aa96-114c0d89411f | checkpoint | Access Panel location has been marked on floor as per RCP and has been checked
83571c21-37f7-48ae-97d8-79ace6dad240 | checkpoint | All other other services do not impede access
1477d7c6-6cd5-4756-ad72-49c77b89e613 | checklist | Ω (Deprecated) Ceiling Closure Checklist 2 Rough In [Q] (v0) |  | Ceiling Closure Checklist 2 Rough In [Q]
07485d10-b89f-4047-ba50-70b304fa94cf | section | Air Conditioning:
5572a1b5-00e6-433a-9f0d-3b3e83a7eb50 | checkpoint | Air Conditioning
f298420a-a488-5b7a-8f92-4de32c5a2cb9 | textbox | Inspection Date:
7c316dce-b299-4eee-8577-0a05b2343477 | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
dc5766cf-91af-4c53-a753-72bc1cfb15cb | checkpoint | Units all hung with isolation mounts and with 5% fall to drain point
c8b38a99-a147-4c61-ac05-aea7ff6d720c | checkpoint | Other services installed are not impeding access to fan coil
fe309b6a-59da-4eb9-bd44-49d160921034 | checkpoint | Wiring connected to indoor unit electrical box
a548384c-66bb-4ee4-bc9e-75211644c911 | checkpoint | Refrigeration pipes run is not exceeding the pipe length limits in VRV systems?
9c458870-afde-4f1a-96c6-a87e0a4e62a6 | checkpoint | Condensate drainage is in correct location & height
bd035f7b-4081-44e2-bd0a-1334fefb038d | checkpoint | Filter Track for return air have been installed at the back of unit
a40315f8-79f8-4313-8816-2a4be8726f49 | checkpoint | All flexible ducts connections to air terminlas and spigots have been air tight by using duct tape
1637f2d8-60de-4620-9437-e034d49fd95d | checkpoint | All flexible ducts connections to air terminlas and spigots have been secured by using fixing ties/cables ties
adb8cd90-3bbd-4b5b-bd69-95f55b16fb38 | checkpoint | Are correct concrete fixings used for ductwork?
d3b013cb-b97e-446f-abb0-392a6b39fb34 | checkpoint | Is the duct joining/fixing undertaken correctly?
e340eaf0-70de-4618-9e87-048b25ffce3b | checkpoint | Are the correct /approved spigot sizes installed?
23f83a8f-3167-47ba-bcd9-bf8f4943c4e2 | checkpoint | Is correct size & voltage for zone dampers installed for living & bedrooms served by ducted fcus?
b50012d5-af1f-4566-b29a-98ebd8609019 | checkpoint | Is correct size BTOs & Y pieces used?
ddc87ded-3ac3-48c9-9701-873139fdb7c0 | checkpoint | Fresh air to apartment
2b682751-96b5-459a-84a4-6295226231d3 | section | Ventilation:
00760d48-d3b0-43bd-a8eb-91609de450c2 | checkpoint | Ventilation
54a4bc64-a371-5e47-a218-7d589cbf9ee3 | textbox | Inspection Date:
bd06ca29-4664-47ea-a108-f03a89e69e43 | checkpoint | Fans installed within ceiling areas are in the correct location as per Mechanical Drawings
3a62e6d7-5a8a-4b6f-8d8c-d5975a9675cc | checkpoint | Fans Installed correctly with rubber isolation pads
d598f3aa-ca32-4223-b46c-2850eb57e9a2 | checkpoint | All Flex has been run to correct location
50445e26-a896-4d70-a85c-6ac884000f27 | checkpoint | All flex are hung independent of other services and supported by intact load spreaders
133a73ac-03e7-4b3e-bd00-e743b4b1f486 | checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties
09078c29-074c-4c2f-9b34-68851483aae3 | checkpoint | Butterfly dampers are installed on the PODs grille neck and they are in a fully opened position and air tight sealed
60f6bec7-253f-457f-bc4a-bbd5d8dcea7e | checkpoint | PVC sleeves has been installed in wet area walls
78603f60-fe19-4b3e-9ec5-94192629a0bb | checkpoint | Vent boxes are intalled in correct location as per RCP and SEALED
4199c8fa-05e3-4e21-b7a1-43b75e028ea9 | checkpoint | PVC ducts have been hung and supported indicidually by using hanging straps
f2c65c35-c076-4805-a3ba-3d97bda0d111 | section | Access Panel:
ec3683bd-6ea6-46c2-a1c8-1c59b694739e | checkpoint | Access Panel
4390d68a-de50-5eaa-8e11-c61e61a69957 | textbox | Inspection Date:
9aed7abf-1403-4fb3-9771-9c40c77f791e | checkpoint | Access Panel location has been marked on floor as per RCP
4ccc90e1-d5a5-41be-bbc2-dd4ddf66f489 | checkpoint | Access panel location allows sufficient access equipment
83a414dd-9e17-4070-95c7-70f0f8d8a7b7 | checkpoint | All other other services do not impede access
ead143e4-fde6-42b3-ab6e-494ce540ede8 | checklist | Ω (Deprecated) Ceiling Closure Checklist 2 Rough In [Q] (v1) |  | Ceiling Closure Checklist 2 Rough In [Q]
c47a3dd3-e56b-47fb-a88e-1f45693dcd59 | section | Air Conditioning:
673d19a9-83fa-4cc2-8107-f47b77bc98b6 | checkpoint | Air Conditioning
48bac7c0-4e6a-51f0-a134-2f656e412b4f | textbox | Inspection Date:
503b985f-335e-4dc2-b2e0-5eec89517fef | checkpoint | FCU’s are installed and other services are not impeding access to fan coil?
ba5a629a-2196-4017-bdc4-69d990c7c552 | checkpoint | Wiring connected to indoor unit electrical box?
260c89f4-459a-49a5-a673-1a1b42cac88e | checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
ac8e2038-8f66-4987-94d7-a04f509cd95c | checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
86692475-0480-4791-9661-baa9245634ac | checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
bfa87660-d301-4df9-b51a-ed6daf45b4ce | checkpoint | FCU flexible ducts installed and supported by intact load spreader?
51529086-b64a-40e8-a2f5-80761639d12c | checkpoint | Zone motors are installed and connected with junction boxes?
fc6435ac-7848-466a-a845-e0a1596b1fa4 | checkpoint | Zone motors is side face?
b9309ef3-d3fd-40d8-a23b-cb00d9cb43c7 | checkpoint | Supply boxes are installed and supported at correct location in the middle of bulkhead height?
45415458-1028-4793-adbe-7902674b6348 | section | Ventilation:
54e757a4-582e-4d4e-8d5d-716b8c8c7ab7 | checkpoint | Ventilation
a0fc0cf0-c440-512f-97c3-01ec5697c970 | textbox | Inspection Date:
e4d7a1a4-a63d-4e93-854c-0a7bf5c36629 | checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
9d9661de-4620-43bb-b84f-8f9fa09ce8aa | checkpoint | All flex are installed and supported by intact load spreaders?
ed79dada-2338-47bc-8349-0aa9c63cf7ea | checkpoint | Flexible ducts on the right location and not jammed?
ad26fadc-c799-4c2d-ae6e-dd8fe3c0b0ec | checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
9760ef6a-e2dc-4ea8-93d4-efa8705a660c | section | Access Panel:
db95f94a-3e2b-436a-bbec-2fada5585c4c | checkpoint | Access Panel
022d9b6b-342f-574e-b15e-cf6bd9544679 | textbox | Inspection Date:
17dcce0a-7ca6-48d2-aa70-a21edf970ce0 | checkpoint | Access Panel location has been marked on floor as per RCP and has been checked?
2e47c539-5297-4558-bb3c-f3758549bbaf | checkpoint | All other other services do not impede access?
8c34a4fa-8bce-45fc-924d-4988b6ac4311 | checklist | Ω (Deprecated) Duct Installation Checklist [C] (v0) |  | Duct Installation Checklist [C]
a8e2d49a-a8e0-417a-9f2c-bed54c7c0e8c | section | Duct Installation Checklist
9eb7e823-391b-4a42-89ef-8135d439f99c | checkpoint | Are drawings on site the latest issue
1dde3cdf-8fd0-4f81-af48-415655621312 | checkpoint | Are plant and equipment location correct
a2581b73-d5be-4b15-9b8a-10644705a18f | checkpoint | Fan in the duct run has been installed
27c3dbfe-d4a1-4369-9942-4345fdf44ee2 | checkpoint | Model of the fan is correct as per latest Fan Schedule
aee33b86-01ed-43fc-bba2-c406485a25f3 | checkpoint | Duct size and location correct
d0a70bad-0ccd-471d-bee1-b5c76ec04b60 | checkpoint | Material and gauge correct
d678e60b-fb17-4ab7-8b71-3746b417af62 | checkpoint | Is correct support method being used - Risers are supported at each level.
17dc772b-c2b6-4778-9930-f9d6fbc89fa2 | checkpoint | Is correct jointing method being used
6b80de97-6efd-4451-9758-33cf31607137 | checkpoint | Are joints completed and cleated installed on flanges
544b1a5c-df69-4668-889e-624c9c24842a | checkpoint | Is correct joint sealant being used
72a411d5-0a26-4258-89da-1663b9eb7be0 | checkpoint | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
030e188e-3ebb-4e8a-9a93-a46cd6c76c2a | checkpoint | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
603397f0-febf-462e-aea5-d142d03a64ef | checkpoint | Is adequate distance between attenuator and fans been maintained?
13c34b8d-95c5-43b9-acbc-24f4308f725f | checkpoint | Are the attenuator splitters in the plane of the bend ?
1ccd3565-e2c1-4260-82c2-78e9a3a0c766 | checkpoint | Are transitions close to attenuators gradual?
7227d2be-82ef-4354-95e8-64017b8a9ee7 | checkpoint | Is a settling duct between volume control dampers and attenuators allowed?
8b1dc1e6-9555-4df2-8eeb-56c2a91521eb | checkpoint | Are fire dampers installed and break away joint complete
726d8ba6-3dfe-4980-aae4-cf301f386f66 | checkpoint | Are flexible ducts installed, supported and connected to spigot by approved mthod using duct tape on internal core and cable tie on outer core
96398b91-f219-45ba-bbeb-c24b592f1596 | checkpoint | Are flexible connections to equipment sealed and aligned
805b81ae-d3be-4fbd-9936-cc908f73d685 | checkpoint | Is ductwork insulation as per drawings
b1da487a-4c7a-4c74-b22c-d0228074d69a | checkpoint | Is ductwork fire rating complete
4304c92b-a2f1-4c55-a066-4f816f3ab424 | checkpoint | Are all spigots installed and dampers fully open
873cae5e-8da4-4925-954e-b81bdaa82357 | checkpoint | Are all access panels for fire damper access installed and closed
7dc78814-a864-4217-9131-fa3432686d3f | checkpoint | Is ductwork installation complete
e9306b2f-d969-43ad-9b31-2fe1d28ea24d | checklist | Ω (Deprecated) Ventilation Checklist Commissioning [G] (v0) |  | Ventilation Checklist Commissioning [G]
7170d1e2-2a32-4148-8762-75c6e7f1ebce | section | Ventilation Checklist Commissioning
c2572f42-785b-4fe9-a7d6-044b147ac5c0 | checkpoint | Fan has been tested and is operational?
d37f558b-777b-4a61-85fe-31b35af30b1d | checkpoint | Adequate flow has been achieved in bathroom 1?
a1bb0d4d-e702-42b0-841f-8a46280a9120 | checkpoint | Adequate flow has been achieved in ensuite?
f8ed4432-7d6f-464e-9d12-a2b12a8b0c8a | checkpoint | Adequate flow has been achieved in laundry?
a498c814-9c02-4ebe-ac3f-5b033e1c3eae | checkpoint | Range hood has been tested and is operational?
54a7fe79-df43-4f6a-b61c-43deb88134b4 | checklist | Ω (Deprecated) Wall Closure Checklist 1 Rough In [A] (v0) |  | Wall Closure Checklist 1 Rough In [A]
2d5354fb-bf66-49ad-8d14-373dad83c69c | section | Wall Closure Checklist 1 Rough In
4c006936-1e09-43f9-be4e-9e6dfe864c05 | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
2c132f69-20b6-451e-b2db-5ed4a94de2a5 | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule
303a9b7b-51e8-45c2-af3d-31a212d7c507 | checkpoint | FCU installed as hight as possible with 5% slop tward the drain point
8e315a22-1e1c-409f-98a6-4a8fe08f1e6a | checkpoint | Thermostat control cabling has been installed
e1f8d1fb-a9d2-47c8-99c2-00f9f14b62c1 | checkpoint | Thermostat location is correct as per RCP
ee64474d-002b-4c8d-ac76-c778bf8ace75 | checkpoint | Drains have been run to Tundish
93e9b950-aadc-49d5-baf0-c81d9f62b8d0 | checkpoint | Drains tested and witnessed by Boad Air
a9825cb6-ae29-441a-860b-134f03aa50a9 | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect
d282694e-8929-45cb-bc87-2466f8d1b104 | checkpoint | Refrigeration insulation is not damaged
aac842ee-7694-49f0-bc19-86bd58424a0c | checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation
52a0723d-1e22-4f28-9dec-6245847d63a1 | checkpoint | Pipe projecting the wall cavities in balconies have been sealed
1bd77387-9446-4c56-937a-0597f8e66ca5 | checkpoint | Refrigeration pipes are run through cavity without being kinked or damaged
b829c188-0e55-4124-bf16-022bacea394d | checkpoint | Refrigeration pipes run is not exceeding the pipe length limits in VRV systems?
20f44b52-21aa-4177-923e-a247e3a71ae1 | checkpoint | Vent boxes are sealed
6fce8540-0d84-4c35-a568-9b1d124afad3 | checkpoint | Add divider using brackets inside Exhaust plenum boxes to separate toilet & kitchen exhaust?
47561e6c-9b33-4c2b-a731-48e3d0205cda | checklist | Ω (Deprecated) Wall Closure Checklist 1 Rough In [A] (v1) |  | Wall Closure Checklist 1 Rough In [A]
93cd3e43-9f1a-4194-b2ea-55ee2a2b66d5 | section | Wall Closure Checklist 1 Rough In
10c6e052-fee6-4e13-91bf-f74ed0aba06e | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule
08f539f7-f94d-430d-a5ff-de1c7e8f12c3 | checkpoint | FCU installed as hight as possible with 5% slop tward the drain point
8b288bf4-8d54-4359-a5ff-d959177802b1 | checkpoint | Thermostat control cabling has been installed
3478c3df-4b9b-49f5-ba53-19be350dd850 | checkpoint | Thermostat location is correct as per RCP
1aa4cd3b-3f68-46f0-94ef-2158259be1df | checkpoint | Drains have been run to Tundish and does not protrude wall framing
e56ebe09-ebb1-4982-9b86-5d3212e24e80 | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect
4cd95764-6343-431f-a6ac-c323e1e916ab | checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height
52163769-58b4-4d2b-883a-8d7a24ad9452 | checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
4116e408-a342-4a01-8451-34248938ca46 | checklist | Ω (Deprecated) Wall Closure Checklist 2 Rough In [P] (v0) |  | Wall Closure Checklist 2 Rough In [P]
b7896c87-7770-458d-9a40-6347109aa3a8 | section | Wall Closure Checklist 2 Rough In
c577a2a7-a18b-4cf5-985f-ddc91ead651a | checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
379d0986-a114-4f47-be85-bcefee8ef1bd | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule
f880572f-7bff-416d-9843-226bfd838a53 | checkpoint | FCU installed as hight as possible with 5% slope towards the drain point
85836a27-7765-43a7-9cb0-ceea0327b3da | checkpoint | Thermostat control cabling has been installed
eaa257c3-4b01-4d09-b705-feec0b3e271a | checkpoint | Thermostat location is correct as per RCP
398749e5-563c-4a35-9a6b-3204112e176a | checkpoint | Drains have been run to Tundish
84765817-1468-4e0f-a038-004f1524b9d5 | checkpoint | Drains tested and witnessed by Boad Air
c3b64b9e-b810-4bc5-9919-4eaf4cc79cea | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect
d802242a-3a5e-4cdf-8d47-2f1db2687a6c | checkpoint | Refrigeration insulation is not damaged
979090f1-2414-489f-8d71-e7d27d7abd5d | checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation
60f5b536-6804-4ff3-aacb-f09a52595980 | checkpoint | Pipe projecting the wall cavities in balconies have been sealed
1368c776-2ea1-43f2-a59c-464faae6b732 | checkpoint | Refrigeration pipes are run through cavity without being kinked or damaged
9300f2a0-e890-4e81-a16f-ff247d340601 | checkpoint | Refrigeration pipes run is not exceeding the pipe length limits in VRV systems?
6df36242-850a-490c-bebe-cbea3c73cb6a | checkpoint | Is the Ductwork to FCU insulated & correct size? Is ductwork installed & sealed correctly?
6d68793c-0f9c-4031-b2d5-21573b7a81ff | checkpoint | Is flex duct running through walls squashed?
0f9add44-5f1a-4603-93f4-2728e4c77abb | checkpoint | Is correct size & insulation of flex duct run from ducted FCUs to the grille terminals?
750ca16e-a685-4f94-8ffa-559aef360427 | checkpoint | Are the uniboots for Supply Grille installed & sealed correctly?
e53a98e9-ffdd-479a-919c-95eee3af7b46 | checkpoint | Vent boxes are sealed
ee5e0377-9375-4860-a285-a268a0f4ea38 | checkpoint | Add divider using brackets inside Exhaust plenum boxes to separate toilet & kitchen exhaust?
8de593e9-636c-4418-a330-bced03e5ceb7 | checklist | Ω (Deprecated) Wall Closure Checklist 2 Rough In [P] (v1) |  | Wall Closure Checklist 2 Rough In [P]
832166ca-eb56-4659-965a-0147c76c329d | section | Wall Closure Checklist 2 Rough In
f444ccaa-0661-45b2-a542-c710f2b90e18 | checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schdule?
8fbec628-6e3d-4498-b70a-27a1dd53fca3 | checkpoint | FCU installed as hight as possible with 5% slop tward the drain point?
aea28c68-86b4-4615-94fc-fb182bef21db | checkpoint | Thermostat control and zone control cabling has been installed and location is correct?
f6af40d7-12b8-47d9-8ef1-83e30e8613e3 | checkpoint | Drains have been run to Tundish and does not protrude wall framing?
34258c3b-ae50-4dec-a31b-00238db4e410 | checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
423cc94f-4ec0-4245-ab70-96e1df573934 | checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
c2290a0b-52b3-42fb-9189-acdec977c01f | checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?