## Table 1
FC6.1.084.V - Fulton Hogan - Melbourne Airport Zulu Taxiway 5.0MPa Flexural Strength PCC (for Aircraft Pavement) ITP | [8 empty] | Issue Date: 22-May-2024 Owner: TMVC This document is uncontrolled when printed
Holcim Melbourne Airport
Test - Tester |  | Tech - Technical Manager | PS – Production Supervisor |  | Trans – Transport | W - Witness Point (Holcim checks result)
Lab Mgr - Lab Manager |  | Qal Mgr - Quality Manager | AOM – Area Operation Mgr |  |  | R - Report point (Holcim checks result & sends report to customer)
|  | Ops Mgr - Operations Mgr | Company - HOL's client |  |  | H - Hold Point (HOL checks, reports to customer & supplies only on client approval)
No. | Code / Spec Ref | Inspection Description | Test / inspection method | Acceptance Criteria | Frequency | Initiated by | Approved by | Verification / witness |  |  | Verifying document | Record Location
[8 empty] | Supplier | HOL | Company
1) Plant
1.1 | AS1379 4.2.1 | Batch tolerances |  | AS1379 Table 4.1 | Each Batch | PS | PS |  | W |  | Electronic | Batch computer
1.2 | HOL QMS PN6.1 | Record Plant Malfunctions |  | All plant mulfunctions are to be documented | Each Time | PS | AOM |  | W |  | Register | AOM office
1.3 | AS1379.3.3.2 | Weigh Hopper (Cem & Agg) | AS1379 | ± 0.4% of the Max. Scale Value | VicRoads Min. 3 Monthly | PS | AOM |  | W |  | Calibration Report | Google
1.4 | AS1379.3.4.2 | Water Meters (Plant, Slump Stands & Trucks) | TRBE652973 | ± 2% | VicRoads Min. 3 Monthly | PS | AOM |  | W |  | Calibration Report | Google
1.5 | AS1379.3.4.2 | Admixtures | BASF TM033 | ± 5% | VicRoads Min. 3 Monthly | PS | AOM |  | W |  | Calibration Report | Google
2) Cementitous materials
2.1 | AS1379.2.2 | Type GP cement | AS2350 | AS3972 Table 2 | Cement Australia Supplied (as per AS3972 Clause 5.2) | Supplier | Tech Mgr | W, R | W | H | Supplier test report | Tech Mgr office
| BECA Cl 11.4.7, 11.24.5 | Reference Sample | - | - | Plant Sample : 10kg / 1000 tonnes | Supplier | Tech Mgr |  |  | W | Record only | Tech Mgr office
2.2 | AS1379.2.2 | Flyash | AS3583 | AS/NZS3582.1 Table 1 - Grade 1 | Cement Australia Supplied (as per AS/NZS3582.1 Table 2) | Supplier | Tech Mgr | W, R | W | H | Supplier test report | Tech Mgr office
2.3 | AS1379.2.2 | Slag | AS3583 | AS3582.2 Table 1 | Cement Australia Supplied (as per AS3582.2 Table 2) | Supplier | Tech Mgr | W, R | W | H | Supplier test report | Tech Mgr office
3) Coarse Aggregate
3.1 | AS1379.2.3 | Particle Size Distribution | AS1141.11.1 | AS1379.2.3 | 1/1000 tonnes | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.2 | AS1379.2.3 | Flakiness Index | AS1141.15 | AS1379.2.3 | 1 per month | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.3 | AS1379.2.3 | Particle Density & Water Absorbtion | AS1141.6.1, AS1141.5 | AS1379.2.3 | 1 per 3 months | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.4 | AS1379.2.3 | Los Angeles Abrasion Index Value | AS1141.23 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
FC6.1.084.V - Fulton Hogan - Melbourne Airport Zulu Taxiway 5.0MPa Flexural Strength PCC (for Aircraft Pavement) ITP | [8 empty] | Issue Date: 22-May-2024 Owner: TMVC This document is uncontrolled when printed
Holcim Melbourne Airport
Test - Tester |  | Tech - Technical Manager | PS – Production Supervisor |  | Trans – Transport | W - Witness Point (Holcim checks result)
Lab Mgr - Lab Manager |  | Qal Mgr - Quality Manager | AOM – Area Operation Mgr |  |  | R - Report point (Holcim checks result & sends report to customer)
|  | Ops Mgr - Operations Mgr | Company - HOL's client |  |  | H - Hold Point (HOL checks, reports to customer & supplies only on client approval)
No. | Code / Spec Ref | Inspection Description | Test / inspection method | Acceptance Criteria | Frequency | Initiated by | Approved by | Verification / witness |  |  | Verifying document | Record Location
[8 empty] | Supplier | HOL | Company
3.5 | AS1379.2.3 | Weak Particles | AS1141.32 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.6 | AS1379.2.3 | Wet/Dry Strength Variation | AS1141.22, AS2758.7 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.7 | AS1379.2.3 | Petrographic Analysis | ASTM C295 | AS1379.2.3 | 1 per 2 years | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.8 | AS1379.2.3 | Sodium Sulphate Soundness | AS1141.24 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
3.9 | BECA Cl 11.4.6.2 | Reference Sample | - | - | Once Only : 2 x 25kg samples of each coarse aggregate fraction | Supplier | Tech Mgr |  |  | W | Record only | Tech Mgr office
4) Fine Aggregate
4.1 | AS1379.2.3 | Particle Size Distribution | AS 1141.11.1 | AS1379.2.3 | 1/1000 tonnes | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.2 | AS1379.2.3 | Sodium Sulphate Soundness | AS1141.24 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.3 | AS1379.2.3 | Particle Density & Water Absorbtion | AS1141.6.1, AS1141.5 | AS1379.2.3 | 1 per 3 months | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.4 | AS1379.2.3 | Petrographic Analysis | ASTM C295 | AS1379.2.3 | 1 per 2 years | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.5 | AS1379.2.3 | Sugar Content | AS1141.35 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.6 | AS1379.2.3 | Clay & Fine Silts | AS1141.33 | AS1379.2.3 | 1/1000 tonnes | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.7 | AS1379.2.3 | Organic Impurities | AS1141.34 | AS1379.2.3 | 1 per month | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.8 | AS1379.2.3 | pH Value | AS1289.4.3.1 | AS1379.2.3 | 1 per year | Supplier | Tech Mgr | W, R | W |  | Supplier test report | Tech Mgr office
4.9 | BECA Cl 11.4.6.2 | Reference Sample | - | - | Once Only : 2 x 25kg samples of fine aggregate | Supplier | Tech Mgr |  |  | W | Record only | Tech Mgr office
FC6.1.084.V - Fulton Hogan - Melbourne Airport Zulu Taxiway 5.0MPa Flexural Strength PCC (for Aircraft Pavement) ITP | [8 empty] | Issue Date: 22-May-2024 Owner: TMVC This document is uncontrolled when printed
Holcim Melbourne Airport
Test - Tester |  | Tech - Technical Manager | PS – Production Supervisor |  | Trans – Transport | W - Witness Point (Holcim checks result)
Lab Mgr - Lab Manager |  | Qal Mgr - Quality Manager | AOM – Area Operation Mgr |  |  | R - Report point (Holcim checks result & sends report to customer)
|  | Ops Mgr - Operations Mgr | Company - HOL's client |  |  | H - Hold Point (HOL checks, reports to customer & supplies only on client approval)
No. | Code / Spec Ref | Inspection Description | Test / inspection method | Acceptance Criteria | Frequency | Initiated by | Approved by | Verification / witness |  |  | Verifying document | Record Location
[8 empty] | Supplier | HOL | Company
5) Water
5.1 | AS1379.2.4 | Mains water |  | Main complies | Nil
5.2 | AS1379.2.4 | Non mains water ~ Sugar ~ Oil & grease ~ pH ~ Chlorides ~ Sulfates ~ Total suspended solids | AS1141.35 APHA 5520 AS1580.505.1 | 100 mg/L max 50 mg/L max > 5 500 mg/L max 500 mg/L max 2000 mg/L max | 1 / 6 months | AOM | Tech Mgr |  | W |  | Lab report | Tech Mgr office
6) Admixtures
6.1 | AS1379.2.5 | WR Admixture general acceptance | AS1478.2 | AS1478.1 Table 2.1 | Initial | Tech Mgr | Tech Mgr | W, R | W |  | Supplier report | Tech Mgr office
6.2 | AS1379.2.5 | WR Admixture Uniformity test | AS1478.2 | AS1478 Cl 2.1.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.02), Non-volitle content (+/- 2%)] | MBCC Supplied (Each Batch) | Supplier | Tech Mgr | W, R | W |  | Test Reports | Plant
6.3 | AS1379.2.5 | AEA Admixture general acceptance | AS1478.2 | AS1478.1 Table 2.1 | Initial | Tech Mgr | Tech Mgr | W, R | W |  | Supplier report | Tech Mgr office
6.4 | AS1379.2.5 | AEA Admixture Uniformity test | AS1478.2 | AS1478 Cl 2.2.3 [Supplier specs for pH (+/- 1), Relative density (+/- 0.01), Non-volitle content (+/- 1%)] | MBCC Supplied (Each Batch) | Supplier | Tech Mgr | W, R | W |  | Test Reports | Plant
7) Transport
7.1 | HOL QMS PN6.1 | Agitator blade inspection | - | Concrete Barrel Solution - No excess buildup, No excess wear | 1 / 3 months | PS | AOM |  | W |  | Inspection report | Plant
7.2 | AS1379 3.5.1 (a) | Mixer uniformity test | AS1012 | AS1379 Appendix A Table A1 | Initial for agi type | Trans | Tech Mgr |  | W |  | Manufacturer report HOL test report | Tech Mgr office