## ITP-022
|  |  | Inspection and Test Plan - Control and Supervision of the Works | [7 empty] | Document # GT4-ITP-020
[11 empty] | Revision : 0 |  | Date: 10/04/2023
Client: |  | Hobart International Airport Pty Ltd |  | Construction Process: |  | Prepared by: |  | Reviewed by : |  |  | Approved by :
Project: |  | Project Mercury Early Works At Hobart International Airport |  | Sewer Rising Main Installation |  | Name: | Carter Lawson -Kelleway | Name: | Carter Lawson-Kelleway (VOC by David Hart) |  | Name:
Contract No: |  | MER-EW-001 |  | Specifications: Specification 706 & WSA 02-2014-3.1 Gravity Sewer Code of Australia, MRWA Specification
|  |  |  | Structure / Component: Sewer Incl. Rising Main |  | Signed : | CLK | Signed : | CLK |  | Signed :
|  |  |  | Location: Hobart International Airport |  | Date : | 10/04/2024 | Date : | 2024-04-10 |  | Date :
Item | Task/Activity Description |  | Inspection / Controls and Verification Detail |  |  |  |  | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
No. |  |  | Frequency | Acceptance Criteria | Reference Documents | Inspection / Test Method | Record of conformity |  | Project Engineer Site Engineer Superintendent Surveyor Foreman | Client | Fulton Hogan | FH's Sub-contractor | Date
1 | Preliminary Works
1.1 | Check that current revision drawings are being used |  | Prior to Commencing Work | Issued For Construction (IFC) and latest available revision used | IFC Project Drawings/ Drawing Register | Document review | Latest revision IFC drawings | *WP | Site Engineer | N/A |  | N/A
1.2 | Confirm understanding of current EMP related to the work area and that all prescribed environmental controls are in place |  | Prior to Commencing | All environmental measures to be implemented as per current CEMP and local authorities. Sediment control measures to be installed and protected vegetation to be clearly identified | CEMP, Site induction | Document review & Site inspection | ITP signed | *WP | Site Engineer | N/A |  | N/A
1.3 | Traffic Management (When required) |  | Prior to Commencing Work | Approved TMP and WASIN (where required) | Applicable TMP | Document review & Site inspection | Approved TMP | *HP | Site Engineer | N/A |  | N/A
1.4 | Survey set out works |  | Prior to Commencing Work | Survey activities undertaken to ensure and validate that all works meet level and location requirements. The establishment and integrity of the survey network shall be verified before commencing any survey and set out activity. IFC and latest available revision used. | IFC Project Drawings | Site inspection | Survey records & marks on the ground. This ITP Signed off. | HP | Site Engineer / Surveyor / Superintendent | N/A |  | N/A
2 | Material Conformance
2.1 | Water Pipes and fittings |  | Every batch of new material | Sewer pipe material to be free from defects and be sized to the following: EW-CE-DRW-600-002- Schedule 1: New Pipe WSA-02-2014-3.1 | WSA-02-2014-3.1 WSA PS 207 WSA PS-230 Drawing(s): HB19198-C1271 HB19198-C1272 HB19198-C1273 EW-CE-DRW-600-001 | Verify | ITP signed Receival Inspection Checklist | IP | Site Engineer | N/A |  | N/A
2.2 | Correct embedment / backfill materials onsite |  | Every batch of new material | Inspect bedding and backfill material to ensure suitability. If watermain is to be protected, use stabilised sand or concrete encasement TYPE R - REFER TO TRENCH DETAIL . | MRWA-W-201 to 203 EW-CE-DRW-600-006 | Verify | ITP signed Receival Inspection Checklist | IP | Site Engineer | N/A |  | N/A
3 | Excavation of trenches
3.1 | Trenching details |  | Ongoing | • Trench's to be excavated to conform with IFC drawing details. • Sides of excavation to be kept vertical to at least 150mm above the pipe. • Ensure trench width and depth are within tolerance • Ensure trench foundation & wall firm, stiff & suitable | Drawing(s): MRWA-W-2023 EW-CE-DRW-600-006 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
3.2 | Benching & shielding (where required) |  | As Required | Trench support is required where the trench is more than 1.5 metres, unless the trench has been assessed as safe by a geotechnical engineer and written confirmation provided as such. | Work Procedures | Verify | ITP signed | *HP | Site Engineer | N/A |  | N/A
3.3 | Capping and grouting of abandoned mains |  | Before bedding material is installed | Where it is necessary to fill a redundant pipeline, low strength grout (<5 MPa), similar material or sand shall be used. | Drawing(s): WSA 03-2011 3.1 EW-CE-DRW-600-004 | Verify | Release of Hold Point | WP | Site Engineer/Superindendant | N/A |  | N/A
4 | Watermain Installation
4.1 | Bedding |  | Each Lot | Bedding materials : 5 or 7mm single sized aggregate used Bedding depth: 75mm>x>150mm for 150dia pipe | AS2053.1:2001 MRWA-W-201 EW-CE-DRW-600-006 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
4.2 | Pipe Joints |  | Each Lot | Ensure pipe joint deflection is acceptable, as per drawings and product specifications. ALL JOINTS SHALL BE BUTT WELDED. WHERE BUTT WELDING IS NOT POSSIBLE MECHANICAL JOINTS SHALL BE USED. ELECTROFUSION SHALL NOT BE USED UNLESS APPROVED PRIOR BY THE SUPERINTENDENT. | MRWA-W-103 Drawing(s): EW-CE-DRW-600-001 | Verify | ITP signed, photo of each joint | IP | Site Engineer | N/A |  | N/A
4.3 | Pipe Embedment |  | Each Lot | Embedment Type R including 5/7mm single sized aggregate. Min Overlay: 300mm (Compaction with ride on equipment) Side Support: 100mm>x>350mm Embedment placed under haunches by shovel and worked around pipe to ensure all voids at haunches are filled | Table 201-D, MRWA-W-201 MRWA-W-202 EW-CE-DRW-600-006 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
4.4 | Pipe Backfill Material |  | Each Lot | Backfill material (Type R): Class 2 FCR (depth <1.5m) Class 4 FCR (depth >1.5m) | MRWA-W-201 Drawing(s): EW-CE-DRW-600-006 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
4.5 | Pipe Backfill Compaction |  | Each Lot | Backfill compacted in <= 200mm loose layers to achieve minimum density R_D 95% (MDDR = 95%). Avoid compaction within 500mm of top of pipe Trafficable Areas: R_D 95% (MDDR = 95%) Non-Trafficable Areas: Below 600mm = 90% MDDR, Above 600mm = 95% MDDR | MRWA-W-201 MRWA Specification No. 04-03 . | Test report | ITP signed | TP | Site Engineer | N/A |  | N/A
4.6 | Marking Tape |  | Each Lot | Marking tape to be laid along the route of the alignment ontop of first backfill layer | MRWA-W-202 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
4.7 | Valves |  | Each Lot | • Install valves in the vertical position and provide surface fittings and valve markings in accordance with Drawings • Inspect the valve for damage. Repair any damage to the external coating in accordance with the manufacturer’s instructions • Check the valve and off-take clamp flanges to ensure the sleeves fit in the bolt holes. Trim insulation sleeves such that they join inside one flange, and not at the flange joint. • Lid on valve to be cenrally placed | WSA 03-2011 3.1 MRWA-W-300, MRWA-W-301 and MRWA-W-302 EW-CE-DRW-600-004 | Verify | ITP signed | *HP | Site Engineer | N/A |  | N/A
4.9 | Scour/Pump Out Points |  | Each Lot | • DN100 SCOUR/PUMP OUT POINT IN A 1200 CONCRETE MH PIT to be installed where denoted on the drawings. • SEWER SCOUR OUTLETS TO BE IN ACCORDANCE WITH STANDARD DRAWINGS SPS-1602 AND SPS-1603 | EW-CE-DRW-600-004 | Verify | ITP signed | *HP | Site Engineer | N/A |  | N/A
4.1 | Thrust blocks |  | Where required | • CONNECTION TO THE EXISTING RISING MAIN MUST BE ANCHORED TO PREVENT MOVEMENT CAUSED BY THRUST IN ACCORDANCE WITH MRWA-W-205A. THRUST BLOCK AREA = 0.89m2 | MRWA-W-205a EW-CE-DRW-600-001 | Verify | ITP signed | WP | Site Engineer | N/A |  | N/A
5 | Testing
5.1 | Compaction Testing (when applicable) |  | Completion of pipe installation & fittings. | Undertake field density testing of trench fill in accordance with the methods specified in WSA 02 - 2014-3.1 | MRWA Backfill Spec 04-03.2 EW-CE-DRW-600-006 | Compaction Testing | Test Report | WP | FH Engineer / Superintendent | N/A |  | N/A
5.2 | Pipeline Pressure Testing |  | Completion of pipe installation & fittings. | Undertake pressure testing of pipelines in accordance with the methods specified in WSA 02 - 2014-3.1 & WSA 03 - 2011-3.1. Gravity sewer to be tested for 28 Kpa for minimum 3 minutes and sewer rising main to be tested at 31m 1000 Kpa for minimum 2 hours. | WSA 02 - 2014-3.1 WSA 03 - 2011-3.1 EW-CE-DRW-600-001 | Pressure Testing | Completed CL-003- Pressure Testing Record & CL-003(A, B or C) -Pressure Testing | HP | FH Engineer / Superintendent | N/A |  | N/A
6 | Completion
6.1 | As constructed drawings |  | Each Lot | Ensure all conduit deviations are captured on redline drawings for updating the IFC Drawings, and providing asbuilt data for AutoCAD | EW-CE-DRW-600-004 | Verify | ITP signed | IP | Site Engineer | N/A |  | N/A
Final Inspection
The signature below verifies that this ITP has been completed in accordance with the FH’s Quality system Procedures and verifies lot compliance with specifications.
| Print Name: | Carter Lawson-Kelleway | Position: Site Engineer |  | Signature: | Carter Lawson-Kelleway |  |  |  | Date: | 2024-06-21
Legend
HP | Hold Point | Work shall not proceed past the HP until released by the Superintendent |  |  | IP | Inspection point |  | Formal Inspection to be done and recorded
HP* | FH Hold Point | Work shall not proceed past the HP* until released by FH |  |  | TP | Test Point |  | Product compliance test to be undertaken and recorded/reported
AP | Approval Point | Written or verbal approval given by the Superintendent |  |  | SCP | Survey conformance point |  | A qualified surveyor to check product/section/structure and report
WP | Witness Point | An inspection which must be witnessed by the Superintendent |  |  | WP* | Fulton Hogan Witness Point |  | An inspection which must be witnessed by Fulton Hogan Representative