## Table 1
Electrical - Substation L2
Inspection and Test Plan - ITP
SECTION 1 - GENERAL
Client: |  |  | Asset |  |  |  |  | ITP Template No.: | Revision:
[8 empty] | ZENT-ITP-7039 | A
Project Name: |  |  | Area |  |  |  |  | Prepared By: | Prepared Date:
[8 empty] | Brendan King | 2023-12-19
Project Number: |  |  | Discipline | Component | Location |  |  | Approved By: | Approved Date:
|  |  | Electrical | ITP - Electrical - Substation L2 |  |  |  | Brendan Hile
SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
Name: |  | Position: |  | Signature: |  | Data:
Comments:
SECTION 3 - LEGEND
Term |  | Description
WITNESS |  | Activity is to be witnessed by Zenviron ¦ Advance notification mandatory ¦ Activity can proceed once the minimum notification period has elapsed
HOLD POINT |  | Activity is to be witnessed by Zenviron ¦ Advance notification mandatory ¦ Hold point can only be waivered formally in writing
SECTION 4 - Level 2 - Pre-commissioning/Secondary System Tests
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: (ZENVIRON ONLY)
[6 empty] | NAME | SIGNED | DATE | COMMENTS
4.1 | Earthing System Tests | Injection tests on earthing system to measure transfer of potential, continuity, step & touch voltages. | As per IFC Drawings and Schedule 02 - Employers Requirements | Substation Earthing Commissioning Report ZX115-REP-7901 | N/A
4.2 | 330/33kV Main Transformer | Post assembly inspections of main power transformer | As per IFC Drawings and Schedule 02 - Employers Requirements | Subcontractor/OEM Documentation 1 Per Item | N/A
4.3 | 330kV Circuit Breaker | Pre-energisation verification testing of 330kV Circuit Breakers Incl | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7361 Outdoor Circuit Breaker and/or Subcontractor/OEM Documentation 1 Per Item | N/A
4.4 | 330kV Disconnector / Earth Switch | Pre-energisation verification testing of 330kV Disconnector/EarthSwitch(s) | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7362 Outdoor Disconnector and/or Subcontractor/OEM Documentation 1 Per Item | N/A
4.5 | 330kV Voltage Transformer | Pre-energisation verification testing of the Voltage Transformer(s) | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7379 Outdoor Voltage Transformer 1 Per item | N/A
4.6 | 330kV Current Transformer | Pre-energisation verification testing of the Current Transformer(s) | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7364 Outdoor Current Transformer 1 Per item | N/A
4.7 | 330kV Overhead Busbar and Flexible Conductor | Ductor and insulation resistance testing of 330kV Overhead Busbar and Flexible Conductor | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7368 Level 2 ITR Overhead Rigid Busbar/Flexible Conductor 1 Per Bay or Section (Or replaced by equivalent Subcontractor Documentation) | N/A
4.8 | Neutral Earthing Resistor | Pre-energisation verification testing of the Neutral Earthing Resistor | As per IFC Drawings and Schedule 02 - Employers Requirements | ZX115-ITR-7380 Neutral Earthing Resistor and/or Subcontractor/OEM Documentation 1 Per Item | N/A
SECTION 5 - Level 2- Completion
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: (ZENVIRON ONLY)
[6 empty] | NAME | SIGNED | DATE | COMMENTS
5.1 | Redline markup of Construction Drawings | Redline markup of relevent Construction Drawings in Master Drawing Folder | In line with ZX115-REP-0201 Earthworks, Roads and Drainage Specification and BMS- WIN-1024 - Document Red-Line Markup | Redline Markup in Master Drawing Folder | N/A
5.1 | Generate Punch List | Subcontractor walk-down inspection | Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register | BMS-TMP-0044 Punch List record | N/A