## Table 1
Civil - Access Track
Inspection and Test Plan - ITP
SECTION 1 - GENERAL
Client: |  |  | Asset |  |  |  |  | ITP Template No.: | Revision:
Fluence |  |  | LV BESS |  |  |  |  | ZX118-ITP-7020-1 | 0
Project Name: |  |  | Area |  |  |  |  | Prepared By: | Prepared Date:
Latrobe Valley BESS |  |  | Access Track |  |  |  |  | L.Blazevic | 2024-11-01
Project Number: |  |  | Discipline | Component | Location/Chainage |  |  | Approved By: | Approved Date:
ZX118 |  |  | Civil | Access Track | - |  |  | R.Burke | 2024-11-01
SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
Name: |  | Position: |  | Signature: |  | Date:
Comments:
SECTION 3 - LEGEND
Term |  | Description
REVIEW |  | An Activity which is verified by examination of documentary evidence that inspection/tests have been satisfactorily conducted
WITNESS |  | Activity is to be witnessed by Zenviron ¦ Advance notification mandatory ¦ Activity can proceed once the minimum notification period has elapsed
HOLD POINT |  | Activity is to be witnessed by Zenviron ¦ Advance notification mandatory ¦ Hold point can only be waivered formally in writing
SECTION 4 - PRELIMINARY
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
4.1 | Design drawings, project specifications. | Design drawing revision status issued for construction, Project Specification and current controlled model issued. | Documents controlled through document management system. | N/A | WITNESS
4.2 | Survey and Setout. | ZX118-REP-0173 Civil Specification Report Survey and inspection of Control Points. | Control point survey. Visual inspection of control point/s. Survey equipment spot checked for calibration. | N/A | WITNESS
SECTION 5 - MATERIAL APPROVALS
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
5.1 | Subgrade Material Conformance - Import Fill | Verify conformance of material to: ZX118-REP-0173 Civil Specification Report As per ZX118-DWG-3702 Typical Access Track Details As outlined in AS 1289 | ZX118-REP-0173 Civil Specification Report Testing as per AS 1289.5.1 Designer Approval prior to placement Low Reactivity Granular CBR>15% | NATA Test Reports | REVIEW
5.2 | Base Course Material Conformance | Verify conformance of material to: ZX118-REP-0173 Civil Specification Report, Austroads Guide to Pavement Design - Part 4A, and ZX118-DWG-3702 Typical Access Track Details | ZX118-REP-0173 Civil Specification Report; Testing as per AS 1289.5.1 - Particle Size Distribution - in line with Class 3 according to Austroads Guide to Pavement Design - Part 4A - CBR >45% - Atterberg Limits targeting PI 9% +/-2% OMC - Wet/Dry Strength Variation ≥50kN | NATA Test Reports | REVIEW
5.3 | Drainage Backfill | Verify conformance of pipe bedding and backfill material to: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details | ZX118-REP-0173 Civil Specification Report Design Drawings - Bedding - Evenly graded Class 2 FCR with 20mm nominal size or other designer approved material - Backfill - Class 3 FCR with 30mm nominal sizing or other design approved material | NATA Test Reports | REVIEW
5.4 | Drainage Elements | Verify conformance of pipes and headwall to: ZX118-REP-0173 Civil Specification Report | ZX118-REP-0173 Civil Specification Report RCP compliance to AS/NZS 4058 and/or polypropylene to AS/NZS 5065 | Material Data Sheets | REVIEW
SECTION 6 - CONSTRUCTION PROCESS - ACCESS TRACK STRIP SOIL
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
6.1 | Clear and Grub | Verify area has been cleared and grubbed. | Area cleared of all refuse, artificial and deleterious materials. Consult with landowner prior to removing any fencing or gates Ensure CEMP is adhered too | N/A | WITNESS
6.2 | Topsoil Stripping | Confirm top soil removed and stockpiled adeqautely | Strip topsoil to a depth required to remove all topsoil from the footprint area Ensure the area is self draining Ensure CEMP is adhered to. Temporary ERSED controls in place as required | N/A | WITNESS
SECTION 7 - CONSTRUCTION PROCESS - SUBGRADE AND CONDITIONING
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
7.1 | Earthworks Foundation | Earthworks on subgrade treatment to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and ZX118-DWG-3701 General Notes | Test results on founding layer compliant to ZX118-REP-0173 Civil Specification Report - Proof Roll using fully loaded 10000L water truck or other approved vehicle - DCP - 1 test per 50lm | ZX118-ITR-7209 - Proof Roll Inspection DCP Field Results / NATA Test Report ZX118-ITR-7210 (Where applicable) - including Location plan of soft, wet or unsuitable material including replacement methodology. | HOLD POINT
7.2 | Structural Fill/ Rock Fill Embankment (Where Required) | Earthworks on structural fill/ rock fill embankments to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, ZX118-DWG-3701 General Notes and AS 1289 | Test results and/ or proof roll records obtained for the fill layers compliant to ZX118-REP-0173 Civil Specification Report - Compaction to 98% SMDD at ±2% OMC - Frequency of 1 test every 300m and every second layer within 1000mm of finished subgrade level | NATA Test Report (Where Required) ZX118-ITR-7209 - Proof Roll Inspection | HOLD POINT
7.3 | Rock Subgrade (Where Required) | Rock Subgrade compromising of reasonable strength rock to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report | Proof roll records obtained - Fully loaded 10000L water truck or other approved vehicle | ZX118-ITR-7209 - Proof Roll Inspection If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology. | HOLD POINT
7.4 | Finished Subgrade | Test results obtained for the finished subgrade layer compliant to: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track, Details, ZX118-DWG-3701 General Notes, and AS 1289 | Test results and proof roll records obtained for the finished layer compliant to ZX118- REP-0173 Civil Specification Report - Compaction to 98% SMDD at ±2% OMC - Frequency of 1 test every 300lm - Proof Roll using fully loaded 10000L water truck or other approved vehicle | NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection | HOLD POINT
SECTION 8 - CONSTRUCTION PROCESS - ACCESS TRACK BASE COURSE PLACEMENT
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
8.1 | Base Course Pavement Placement | Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and AS1289 | Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report - Compaction to 98% SMDD at ±2% OMC - Frequency of 1 test every 300lm - Proof roll using fully loaded 10000L water truck or other approved vehicle | NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection | HOLD POINT
SECTION 9 - CONSTRUCTION PROCESS - LONGITUDINAL DRAINAGE
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
9.1 | Excavation | Ponding monitered and made free draining | Visual Inspection | N/A | WITNESS
9.2 | Erosion Controls | Erosion controls in line with: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3717 Erosion & Sediment controls | Visual Inspection | N/A | WITNESS
SECTION 10 - CONSTRUCTION PROCESS - CULVERTS
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
10.1 | Culvert Foundation | Floor of excavation is sound and no presence of soft or under yeilding material | Visual Inspection | If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology. | WITNESS
10.2 | Bedding | Placed via hand ramming to a minimum 100mm compacted thickness | Visual Inspection | N/A | HOLD POINT
10.2 | Pipe Placement | Location to be confirmed on-site. Grade and RL as per Design requirements | Visual Inspection Confirm pipe flows in the correct direction, barrel of the pipe is laying evenly on the full length of the bedding material and all sockets face upstream | N/A | HOLD POINT
10.3 | Haunching and Backfill | Earthworks on backfill to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details | ZX118-REP-0173 Civil Specification Report ZX118-DWG-3703 Typical Stormwater Details - Compaction & Density 98% SMDD at ±3% OMC - 1 test per drainage line | NATA Test Report | HOLD POINT
10.4 | Erosion Controls - Rock Armouring | Permananet ERSED Controls in place in line with ZX118-DWG-3717 Erosion & Sediment controls | Visual Inspection of scour protection for compliance to: ZX118-REP-0173 Civil Specification Report | ZX118-ITR-7217 Culvert Installation Checklist | WITNESS
SECTION 11 - COMPLETION AND HANDOVER
ITEM | ACTIVITY/ TASK DESCRIPTION | INSPECTION POINT (QUALITY CONTROL ACTIVITY) | ACCEPTANCE CRITERIA | VERIFYING DOCUMENT | SUPERVISION TYPE | RECEIVED AND ANALYSED BY: ZENVIRON
[6 empty] | NAME | SIGNED | DATE | COMMENTS
11.1 | Redline markup of Construction Drawings | Redline markup of relevent Construction Drawings in Master Drawing Folder | In line with: ZX118-REP-0173 Civil Specification Report | Redline Markup in Master Drawing Folder | N/A
11.2 | Generate Punch List | Subcontractor walk-down inspection | Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register | BMS-FRM-1033 Punch List Sheet record | N/A