## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ZENT-ITP-7039 - ITP - Electrical - Substation L2 | [5 empty] | ZENT-ITP-7039 - ITP - Electrical - Substation L2
section | SECTION 1 - GENERAL
checkpoint | General
label | ITP Template No.: ZENT-ITP-7039
label | Revision: A
label | Prepared By: Brendan King
label | Prepared Date: 19/12/2023
label | Approved By: Brendan Hile
label | Discipline: Electrical
label | Component: ITP - Electrical - Substation L2
section | SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
checkpoint | Close Out Signature
textbox | Name:
textbox | Position:
date | Date:
holdpoint | Signature:
section | SECTION 4 - Level 2 - Pre-commissioning/Secondary System Tests
checkpoint | 4.1 - Earthing System Tests
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Injection tests on earthing system to measure transfer of potential, continuity, step & touch voltages.
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: Substation Earthing Commissioning Report ZX115-REP-7901
label | SUPERVISION TYPE: N/A
checkpoint | 4.2 - 330/33kV Main Transformer
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Post assembly inspections of main power transformer
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: Subcontractor/OEM Documentation 1 Per Item
label | SUPERVISION TYPE: N/A
checkpoint | 4.3 - 330kV Circuit Breaker
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of 330kV Circuit Breakers Incl
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7361 Outdoor Circuit Breaker and/or Subcontractor/OEM Documentation 1 Per Item
label | SUPERVISION TYPE: N/A
checkpoint | 4.4 - 330kV Disconnector / Earth Switch
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of 330kV Disconnector/EarthSwitch(s)
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7362 Outdoor Disconnector and/or Subcontractor/OEM Documentation 1 Per Item
label | SUPERVISION TYPE: N/A
checkpoint | 4.5 - 330kV Voltage Transformer
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Voltage Transformer(s)
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7379 Outdoor Voltage Transformer 1 Per item
label | SUPERVISION TYPE: N/A
checkpoint | 4.6 - 330kV Current Transformer
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Current Transformer(s)
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7364 Outdoor Current Transformer 1 Per item
label | SUPERVISION TYPE: N/A
checkpoint | 4.7 - 330kV Overhead Busbar and Flexible Conductor
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Ductor and insulation resistance testing of 330kV Overhead Busbar and Flexible Conductor
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7368 Level 2 ITR Overhead Rigid Busbar/Flexible Conductor 1 Per Bay or Section (Or replaced by equivalent Subcontractor Documentation)
label | SUPERVISION TYPE: N/A
checkpoint | 4.8 - Neutral Earthing Resistor
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Pre-energisation verification testing of the Neutral Earthing Resistor
label | ACCEPTANCE CRITERIA: As per IFC Drawings and Schedule 02 - Employers Requirements
label | VERIFYING DOCUMENT: ZX115-ITR-7380 Neutral Earthing Resistor and/or Subcontractor/OEM Documentation 1 Per Item
label | SUPERVISION TYPE: N/A
section | SECTION 5 - Level 2 - Completion
checkpoint | 5.1 - Redline markup of Construction Drawings
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Redline markup of relevent Construction Drawings in Master Drawing Folder
label | ACCEPTANCE CRITERIA: In line with ZX115-REP-0201 Earthworks, Roads and Drainage Specification and BMS- WIN-1024 - Document Red-Line Markup
label | VERIFYING DOCUMENT: Redline Markup in Master Drawing Folder
label | SUPERVISION TYPE: N/A
checkpoint | 5.2 - Generate Punch List
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Subcontractor walk-down inspection
label | ACCEPTANCE CRITERIA: Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register
label | VERIFYING DOCUMENT: BMS-TMP-0044 Punch List record
label | SUPERVISION TYPE: N/A
checklist | ZX118-ITP-7020-1(0) - ITP - Civil - Access Track | [5 empty] | ZX118-ITP-7020-1(0) - ITP - Civil - Access Track
section | SECTION 1 - GENERAL
checkpoint | General
label | ITP Template No.: ZX118-ITP-7020-1
label | Revision: 0
label | Prepared By: L.Blazevic
label | Prepared Date: 11/01/2024
label | Approved By: R.Burke
label | Approved Date: 11/01/2024
label | Client: Fluence
label | Asset: LV BESS
label | Project Name: Latrobe Valley BESS
label | Area: Access Track
label | Project Number: ZX118
label | Discipline: Civil
label | Component: Access Track
section | SECTION 2 - CLOSE OUT SIGNATURE (ZENVIRON ONLY)
checkpoint | Close Out Signature
textbox | Name:
textbox | Position:
date | Date:
holdpoint | Signature:
section | SECTION 4 - PRELIMINARY
checkpoint | 4.1 - Design drawings, project specifications.
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Design drawing revision status issued for construction, Project Specification and current controlled model issued.
label | ACCEPTANCE CRITERIA: Documents controlled through document management system.
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
checkpoint | 4.2 - Survey and Setout.
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): ZX118-REP-0173 Civil Specification Report Survey and inspection of Control Points.
label | ACCEPTANCE CRITERIA: Control point survey. Visual inspection of control point/s. Survey equipment spot checked for calibration.
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
section | SECTION 5 - MATERIAL APPROVALS
checkpoint | 5.1 - Subgrade Material Conformance - Import Fill
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of material to: ZX118-REP-0173 Civil Specification Report As per ZX118-DWG-3702 Typical Access Track Details As outlined in AS 1289
label | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report Testing as per AS 1289.5.1, Designer Approval prior to placement Low Reactivity Granular CBR>15%
label | VERIFYING DOCUMENT: NATA Test Reports
label | SUPERVISION TYPE: REVIEW
checkpoint | 5.2 - Base Course Material Conformance
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of material to: ZX118-REP-0173 Civil Specification Report, Austroads Guide to Pavement Design - Part 4A, and ZX118-DWG-3702 Typical Access Track Details
label | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report; Testing as per AS 1289.5.1
label | – Particle Size Distribution - in line with Class 3 according to Austroads Guide to Pavement Design - Part 4A
label | – CBR >45%
label | – Atterberg Limits targeting PI 9% +/-2% OMC
label | – Wet/Dry Strength Variation ≥50kN
label | VERIFYING DOCUMENT: NATA Test Reports
label | SUPERVISION TYPE: REVIEW
checkpoint | 5.3 - Drainage Backfill
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of pipe bedding and backfill material to: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details
label | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report Design Drawings
label | – Bedding - Evenly graded Class 2 FCR with 20mm nominal size or other designer approved material
label | – Backfill - Class 3 FCR with 30mm nominal sizing or other design approved material
label | VERIFYING DOCUMENT: NATA Test Reports
label | SUPERVISION TYPE: REVIEW
checkpoint | 5.4 - Drainage Elements
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify conformance of pipes and headwall to: ZX118-REP-0173 Civil Specification Report
label | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report RCP compliance to AS/NZS 4058 and/or polypropylene to AS/NZS 5065
label | VERIFYING DOCUMENT: Material Data Sheets
label | SUPERVISION TYPE: REVIEW
section | SECTION 6 - CONSTRUCTION PROCESS - ACCESS TRACK STRIP SOIL
checkpoint | 6.1 - Clear and Grub
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Verify area has been cleared and grubbed.
label | ACCEPTANCE CRITERIA: Area cleared of all refuse, artificial and deleterious materials. Consult with landowner prior to removing any fencing or gates. Ensure CEMP is adhered to.
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
checkpoint | 6.2 - Topsoil Stripping
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Confirm top soil removed and stockpiled adeqautely
label | ACCEPTANCE CRITERIA: Strip topsoil to a depth required to remove all topsoil from the footprint area. Ensure the area is self draining Ensure CEMP is adhered to. Temporary ERSED controls in place as required.
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
section | SECTION 7 - CONSTRUCTION PROCESS - SUBGRADE AND CONDITIONING
checkpoint | 7.1 - Earthworks Foundation
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on subgrade treatment to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and ZX118-DWG-3701 General Notes
label | ACCEPTANCE CRITERIA: Test results on founding layer compliant to ZX118-REP-0173 Civil Specification Report
label | – Proof Roll using fully loaded 10000L water truck or other approved vehicle
label | – DCP - 1 test per 50lm
label | VERIFYING DOCUMENT: ZX118-ITR-7209 - Proof Roll Inspection DCP Field Results / NATA Test Report ZX118-ITR-7210 (Where applicable) - including Location plan of soft, wet or unsuitable material including replacement methodology.
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.2 - Structural Fill/ Rock Fill Embankment (Where Required)
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on structural fill/ rock fill embankments to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, ZX118-DWG-3701 General Notes and AS 1289
label | ACCEPTANCE CRITERIA: Test results and/ or proof roll records obtained for the fill layers compliant to ZX118-REP-0173 Civil Specification Report
label | – Compaction to 98% SMDD at ±2% OMC
label | – Frequency of 1 test every 300m and every second layer within 1000mm of finished subgrade level
label | VERIFYING DOCUMENT: NATA Test Report (Where Required) ZX118-ITR-7209 - Proof Roll Inspection
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.3 - Rock Subgrade (Where Required)
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Rock Subgrade compromising of reasonable strength rock to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report
label | ACCEPTANCE CRITERIA: Proof roll records obtained
label | – Fully loaded 10000L water truck or other approved vehicle2
label | VERIFYING DOCUMENT: ZX118-ITR-7209 - Proof Roll Inspection If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology.
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 7.4 - Finished Subgrade
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Test results obtained for the finished subgrade layer compliant to: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track, Details, ZX118-DWG-3701 General Notes, and AS 1289
label | ACCEPTANCE CRITERIA: Test results and proof roll records obtained for the finished layer compliant to ZX118- REP-0173 Civil Specification Report
label | – Compaction to 98% SMDD at ±2% OMC
label | – Frequency of 1 test every 300lm
label | – Proof Roll using fully loaded 10000L water truck or other approved vehicle
label | VERIFYING DOCUMENT: NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 8 - CONSTRUCTION PROCESS - ACCESS TRACK BASE COURSE PLACEMENT
checkpoint | 8.1 - Base Course Pavement Placement
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report, ZX118-DWG-3702 Typical Access Track Details, and AS1289
label | ACCEPTANCE CRITERIA: Material placement compliance test results in accordance with: ZX118-REP-0173 Civil Specification Report
label | – Compaction to 98% SMDD at ±2% OMC
label | – Frequency of 1 test every 300lm
label | – Proof roll using fully loaded 10000L water truck or other approved vehicle
label | VERIFYING DOCUMENT: NATA Test Report ZX118-ITR-7209 - Proof Roll Inspection
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 9 - CONSTRUCTION PROCESS - LONGITUDINAL DRAINAGE
checkpoint | 9.1 - Excavation
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Ponding monitored and made free draining
label | ACCEPTANCE CRITERIA: Visual Inspection
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
checkpoint | 9.2 - Erosion Controls
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Erosion controls in line with: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3717 Erosion & Sediment controls
label | ACCEPTANCE CRITERIA: Visual Inspection
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: WITNESS
section | SECTION 10 - CONSTRUCTION PROCESS - CULVERTS
checkpoint | 10.1 - Culvert Foundation
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Floor of excavation is sound and no presence of soft or under yeilding material
label | ACCEPTANCE CRITERIA: Visual Inspection
label | VERIFYING DOCUMENT: If applicable Include; Location plan of soft, wet or unsuitable materialand the applied replacement methodology.
label | SUPERVISION TYPE: WITNESS
checkpoint | 10.2 - Bedding
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Placed via hand ramming to a minimum 100mm compacted thickness
label | ACCEPTANCE CRITERIA: Visual Inspection
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.3 - Pipe Placement
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Location to be confirmed on-site. Grade and RL as per Design requirements.
label | ACCEPTANCE CRITERIA: Visual Inspection. Confirm pipe flows in the correct direction, barrel of the pipe is laying evenly on the full length of the bedding material and all sockets face upstream.
label | VERIFYING DOCUMENT: N/A
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.4 - Haunching and Backfill
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Earthworks on backfill to be in line with methodologies outlined in: ZX118-REP-0173 Civil Specification Report and ZX118-DWG-3703 Typical Stormwater Details
label | ACCEPTANCE CRITERIA: ZX118-REP-0173 Civil Specification Report ZX118-DWG-3703 Typical Stormwater Details
label | – Compaction & Density 98% SMDD at ±3% OMC
label | – 1 test per drainage line
label | VERIFYING DOCUMENT: NATA Test Report
label | SUPERVISION TYPE: HOLD POINT
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.5 - Erosion Controls - Rock Armouring
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Permanent ERSED Controls in place in line with ZX118-DWG-3717 Erosion & Sediment controls
label | ACCEPTANCE CRITERIA: Visual Inspection of scour protection for compliance to: ZX118-REP-0173 Civil Specification Report
label | VERIFYING DOCUMENT: ZX118-ITR-7217 Culvert Installation Checklist
label | SUPERVISION TYPE: WITNESS
section | SECTION 11 - COMPLETION AND HANDOVER
checkpoint | 11.1 - Redline markup of Construction Drawings
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Redline markup of relevent Construction Drawings in Master Drawing Folder
label | ACCEPTANCE CRITERIA: In line with: ZX118-REP-0173 Civil Specification Report
label | VERIFYING DOCUMENT: Redline Markup in Master Drawing Folder
label | SUPERVISION TYPE: N/A
checkpoint | 11.2 - Generate Punch List
label | INSPECTION POINT (QUALITY CONTROL ACTIVITY): Subcontractor walk-down inspection
label | ACCEPTANCE CRITERIA: Generate specific area/scope Punch List and transfer the open items to the Punch List Master Register
label | VERIFYING DOCUMENT: BMS-FRM-1033 Punch List Sheet record
label | SUPERVISION TYPE: N/A