## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
fe0d2eaa-c289-4e50-81d5-b33ba171e031 | checklist | ITP - Electrical Cable Trenching & Installation | itp | ITP - Electrical Cable Trenching & Installation
f916d41e-935b-436d-8f2c-7e64ee653636 | section | Preconstruction
f8242ff6-87a3-4144-81bf-beb9ea77859d | checkpoint | Design Drawings
a72086ad-2182-5e0f-959d-b022148cf1d9 | note | Issued for Construction Drawings available
18314cb6-ff5f-4a42-b435-eec26d29db6b | checkpoint | Site Preparation
605d34f6-40ed-54fe-ae26-0999895d6070 | note | Visual inspection of cleared and levelled area
bb5b6de4-fb06-5c5c-a422-b9bb53f73e7e | note | Site free from debris, vegetation, and unevenness
8fe70f6c-0626-4f8b-b30a-643b45039cf6 | checkpoint | Survey and Marking
bcc2ede4-a229-5511-b545-db453b018282 | note | Alignment with approved IFC drawings & Digital Designs
55e91040-cdea-4f3f-b052-15e7889bc970 | checkpoint | Material Approval
6c407164-eb24-5b4c-83d3-ff559269ab4c | note | Bedding and backfill sand complies with the specification notes for thermal resistivity
1e6b4431-7488-448f-891d-9aeb4c7f524d | section | Finger Trenching - Trench Excavation
4c440875-26cc-4f2f-8419-3aa2cf632c60 | checkpoint | Trench Excavation
679363d8-5a4f-5c08-8a29-d4b9cf3ab05d | note | Finger trenches excavated to a minimum of 900 deep x 250mm wide
fe96aeea-30f6-570e-a556-a7be210b1633 | note | Finger trench invert is smooth without stones or rocks protruding
0db45145-2deb-47e6-bc46-d67eea15a31a | section | Finger Trenching - Trench Bedding
53d51188-125d-4f52-a6ff-e1d7e2ed3b9a | checkpoint | Finger trench bedding consists of a minimum of 100mm of sand
0ec6fc78-fa3c-4bdd-bec0-9e486cbef4f3 | section | Finger Trenching - Cable Installation
fc521dff-d97c-45ec-8149-7592773330a3 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
321ac694-1512-4546-837f-1080def44c63 | section | Finger Trenching - Trench Backfill
53b66f48-c97d-45ee-b094-49a53d1facde | checkpoint | Finger trenches shall include 75mm of sand over the cables
ddf813bd-fed9-45a9-9458-c276219af3f9 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
74e7838a-74f9-480c-9070-5494227e842a | checkpoint | 75mm of sand has been placed over the hard protective cover
207a1567-e053-4479-b6b0-d5c0e1bf8d69 | checkpoint | Earth cables have been installed on the final layer of sand
ee279c8e-f3b7-4b2c-9731-8141f77ae7bc | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
33b0cf62-597b-40f7-ad07-b62823c9fea1 | checkpoint | Existing excavated material is replaced and lightly compacted
cb50af2f-beac-416d-b01a-e49263751f66 | section | Finger Trenching - Reinstatement
ba1219aa-46fa-4e7b-94d8-6f79c32001a5 | checkpoint | Finger trenches are reinstated back to tie into existing ground levels and contours
fb3f40ec-fda8-4151-a8f8-ae10c5b2bc52 | section | Combined Services/DC Trenches - Trench Excavation
0fdc9fa6-9680-4f7c-b390-eb8b756f26dc | checkpoint | Combined Services trenches are excavated to a minimum of 900 deep and wide enough to accommodate all of the cables required including minimum separation distances
096eb1a4-0401-4fd3-8e21-501128334fe6 | checkpoint | Trench inverts are smooth without stones or rocks protruding
78803658-2920-4797-9ada-d5c352c97086 | section | Combined Services/DC Trenches - Trench Bedding
d94f93df-327d-4ab3-a949-60e0a95870f8 | checkpoint | Combined Services trenches bedding consists of a minimum of 100mm of sand
04a2b694-7465-4325-bd85-536f28e6d1fe | section | Combined Services/DC Trenches - Cable Installation
0bfeb3a6-196b-4dd4-b251-f95f50a2ad39 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
8c3cc5d6-a65e-4208-8584-13f16f9fb337 | checkpoint | Minimum separation distances are observed
1439c217-a033-4163-b1db-5019c1d28cfd | section | Combined Services/DC Trenches - Trench Backfill
f63cff05-0e73-4a37-836b-e0b89c4e390b | checkpoint | Combined Services trenches shall include 75mm of sand over the cables
da4c43ab-4a99-4bb0-8362-aee68977ca63 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
0bc1cead-6f4f-5033-aa79-5de95f2e1732 | note | 75mm of sand has been placed over the hard protective cover
3fae18d0-2989-5424-a44e-250643ef00fa | note | Earth cables and comms ducts have been installed on the final layer of sand
be4294af-16bc-5a46-8b61-e52d1b0e283e | note | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
c944b01a-6c23-5cbe-a024-e9ba481114b2 | note | Existing excavated material is replaced and lightly compacted
4a16169f-01e9-4eca-8fdb-5e201cb89a02 | section | Combined Services/DC Trenches - Reinstatement
2cb773af-1efc-401f-b7ef-0b68fb2cefa1 | checkpoint | Combined Services trenches are reinstated back to tie into existing ground levels and contours
234bfa1d-2314-49ce-9b05-cd29b13c6936 | section | Comms & LV Trenches - Trench Excavation
51edcf40-f521-49d6-a022-abf702d097f2 | checkpoint | Comms/LV trenches are excavated to a minimum of 800 deep and 250mm wide
13af962c-672a-48e9-90a4-00fb7375f365 | checkpoint | Trench inverts are smooth without stones or rocks protruding
b3da0b78-8f27-454f-9670-20f7f74af30a | section | Comms & LV Trenches - Trench Bedding
22cef000-4647-4ef7-8dce-dee64332b80e | checkpoint | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed
c22ee600-855c-4713-8eba-5e16a1461cef | section | Comms & LV Trenches - Cable Installation
632a1b2d-27f7-45a4-bce2-e2a7e6569d86 | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
e497b53c-5575-4f24-89f6-19719bc4ec95 | checkpoint | Minimum separation distances are observed
13375d84-bd55-55c2-87e7-19d0edc546a5 | note | Cables have been installed in conduit
92ca59d2-c40e-4462-9b21-e163a32a930f | section | Comms & LV Trenches - Pull Pit Installation
1792fb15-fc90-4aa8-a4fa-d86b201df75e | checkpoint | Pulling Pits are installed on a 100mm of Gap20 bedding
5c5e60c6-29de-47f6-8c6c-2494e90d468b | checkpoint | Pulling pits are installed on the line of the conduits
51d703b3-27c5-4e01-a54d-bdfc9a17d822 | checkpoint | The tops of the pulling pits and level and clear of the road lane
690385f2-3bb6-4050-b0f3-1c4523526177 | section | Comms & LV Trenches - Trench Backfill
52079e5b-7f01-4065-b323-b0c91ef719a8 | checkpoint | Comms/LV trenches shall be completely backfilled with excavated trench material
f3b4ff6d-6b41-4822-a2c1-b4d517e3ff90 | checkpoint | Hard protection shall be installed over 75mm of backfill above the conduits
ec219b66-a8ff-4a13-a3a4-0400a8662b0c | checkpoint | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface
73220fd3-35c8-4d6b-b369-f7b72ced93a3 | section | Comms & LV Trenches - Reinstatement
8e83f3b0-6b71-4874-93a6-3d1a0d01d55b | checkpoint | Comms/LV trenches are reinstated back to tie into existing ground levels and contours
d865720c-bd47-42be-8fcc-96a05d6721a2 | section | 33kV AC Trenches - Trench Excavation
9f7ad33c-6039-49b4-b48a-f4a977677b61 | checkpoint | AC trenches are excavated to a minimum of 1200 deep and wide enough to accommodate the three cables laid in a trefoil arrangement
b74fe42c-b536-4fa4-8505-61f9f2c575af | checkpoint | Trench inverts are smooth without stones or rocks protruding
fd0e2850-9442-41a5-a009-cf0328eb5599 | section | 33kV AC Trenches - Trench Bedding
bb1e6682-6cc9-4cb1-ae1d-53f671a2a62d | checkpoint | AC trenches bedding consists of a minimum of 100mm of sand
bd326020-2350-4261-94d7-575ec94bb964 | section | 33kV AC Trenches - Cable Installation
acc8459a-c598-444e-bbda-894883092a9b | checkpoint | Cables installed in accordance with the IFC Drawings and specifications
45a0368c-c655-4b20-93ed-4dff726b8c86 | checkpoint | Minimum separation distances are observed of 1200mm to any other cable
1b4550a8-92b9-44e3-a7a0-e7c0a6be7825 | checkpoint | Cables to be installed with minimum of 1200mm cover
111ac375-4c17-4be6-ae8c-8e35dfb45a87 | section | 33kV AC Trenches - Trench Backfill
db5572c9-9b47-4230-9488-6b05d008b7e3 | checkpoint | AC trenches shall include 75mm of sand over the cables
2040fc37-1d8c-437d-8a61-15cb42e151c7 | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
f0ad483c-7c55-40e2-bd8d-6c8d104f58b7 | checkpoint | 75mm of sand has been placed over the hard protective cover
f4afef49-1797-4ca0-b819-bab46c52ed91 | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
54ed10c1-47e0-4dde-9ce2-be3e5f231b0b | checkpoint | Existing excavated material is replaced and lightly compacted
03aa8aab-46ae-414d-978e-7d04e82c82de | section | 33kV AC Trenches - Reinstatement
cbe9b74b-34be-43e7-8e97-0aa136e44514 | checkpoint | AC trenches are reinstated back to tie into existing ground levels and contours
b06132aa-1bfb-48ba-bda2-95c580726294 | section | Road Crossings - Trench Excavation
c07d8057-cf30-40f1-90d1-704473ba765d | checkpoint | Road crossing trenches are excavated to minimum widths and depths as described in the cross sections of the Electrical Drawings
5a08d1f7-3978-5d37-9502-53a4a71c2f5b | note | Minimum cover shall be:
07ebdd21-a626-5a70-9048-5de6087c91f3 | note | AC Cables - 1200mm
a782c5e8-ff8e-53af-8f12-9490ccb119d6 | note | DC Cables - 800mm
74678479-2c76-5e43-b98e-9ce95ec40366 | note | Auxiliary/comms/lighting - 600mm
cec7ee00-6f71-4d46-aa75-bb95db944651 | checkpoint | Trench inverts are smooth without stones or rocks protruding
577e782c-116d-43c8-8593-418ce416d34c | section | Road Crossings - Trench Bedding
49be1cb6-0832-4ec7-a3d1-5abe4beafb60 | checkpoint | Trench bedding consists of a minimum of 100mm of sand
e0359bab-fa7e-474f-88b1-0660d6d6461d | section | Road Crossings - Cable Installation
c29388bc-b01c-45d3-9874-f1ebe80bdb0f | checkpoint | Cables installed in accordance with the IFC Drawings and specifications in 100mm HD Conduits - AC cables to be in 150mm conduits
b9ae2163-a838-42f7-90c7-3cec98ff0172 | checkpoint | Minimum separation distances are observed:
b086d1fd-d02d-5158-9da9-5c1774908132 | note | 33kV - 1200mm
0c1cd4d9-e194-5209-9c84-56c5bdd9d57e | note | DC Cables - 300mm
18f15eb1-fd80-59e8-84f7-5e1664f7bb5b | note | more than 24 DC Cables a gap of 150mm in the middle
aa70f7bf-a7ac-54fc-8b36-1c05b0aa49d2 | note | Earth cables - 150mm
23170a8c-fa85-4ab8-a728-80a0c471faf1 | section | Road Crossings - Trench Backfill
1091e89f-6c06-4688-beb3-55dd45729d29 | checkpoint | Road Crossings trenches shall include 150mm of sand over the conduit
fd1ca2a3-0000-4d4a-9f82-28dad9e7601a | checkpoint | Hard protection shall be installed over the previous layer of sand to cover the full width and extent of cables
1fbcdcdb-6323-4098-adb4-c1dc19f7d61a | checkpoint | Soft warning tape is placed over the full extent of the cables in the trench at a maximum of 400mm below the existing ground surface
5664e8a8-0999-4b95-abe3-fb1d53039273 | checkpoint | Backfilled material shall excavated trench material backfilled and compacted to 95% native soil density
64e9289f-eb23-47e0-9374-19c63b802c99 | checkpoint | Existing excavated material is replaced and lightly compacted
076dc458-2126-470e-8515-f67dfb809254 | section | Road Crossings - Reinstatement
224cfd76-b775-4c40-8508-b2dbd0c8f5ac | checkpoint | AC trenches are reinstated back to tie into existing ground levels and contours
116a6bc3-958d-4e6a-ab50-997dd14d3e02 | section | Incoming LV Trench - Trench Excavation
6bef3b69-4ac0-4a74-8ce6-0d03e3844055 | checkpoint | Incomming LV trenches are a minimum of 800 deep cover if Direction Drilled
39bf0718-ec43-4628-89f6-676a87fd8607 | section | Incoming LV Trench - Trench Bedding
b9e9d86a-b468-43bd-bd9d-18867698bed9 | checkpoint | Comms/LV trenches do not require bedding due to the cables being installed in conduit, but if rock is encountered, a minimum layer of 100mm of sand shall be placed
e87e9479-a5c0-43f9-a1a6-791b478dcdec | section | Incoming LV Trench - Pull Pit Installation
f0f93b8d-eaf7-4fa5-a173-4f84b6bd110c | checkpoint | Pulling Pits are installed on Gap20 and Bidim
4b5061d2-0d57-43e7-9061-385a15b24d7b | checkpoint | Pulling pits are installed using 1050x900 Concrete Manhole Risers with Concrete and CI Lids
006ce0bb-b88a-4c9b-ba3e-cde47a565e3f | checkpoint | The tops of the pulling pits and level and Protrude a minimum of 300mm above the surrounding ground
fdf80a42-2fed-457f-9121-be0a0f6a2a00 | section | Incoming LV Trench - Trench Backfill
2e4142df-e3ca-4619-aa59-068c58e10278 | checkpoint | Comms/LV trenches shall be completely backfilled with excavated trench material
2b42f2d5-2334-4fff-80e1-1f29d3bd9333 | checkpoint | Hard protection shall be installed over 75mm of backfill above the conduits
3f871fbf-9eed-462f-a4d6-6598e01b15bf | checkpoint | Soft warning tape is placed over the full extent of the conduits in the trench at a maximum of 400mm below the existing ground surface
62a20fae-9d90-4d22-86b6-74649dc4fda7 | section | Incoming LV Trench - Reinstatement
dd2497f5-647f-4c4b-90a4-4a9676287eb0 | checkpoint | Comms/LV trenches are reinstated back to tie into existing ground levels and contours
8170426c-8430-47c5-82f2-deadeb05810e | section | Post Construction and Handover - Asbuilt Information
81fd7a9e-7868-4fbd-a460-59791e590f28 | checkpoint | Asbuilt information of trench layouts and locations are supplied
3897a9a6-a063-4ddc-a2b2-aab050a6cb9f | section | Post Construction and Handover - Final Walkthrough & Inspection
72761f1c-b6ac-4065-975b-d66d5ac38b66 | checkpoint | Final Walkthrough & Inspection
5bbe1f3b-3421-5cf1-971d-e82784b5370d | note | Comprehensive inspection of all elements relating to the Electrical Trenches
28afd4b1-d283-5940-9192-19da7a9c229e | note | Compliance with IFC drawings and specifications
fdb71828-fc43-5bf6-8aa3-ba10557ce9cb | note | Verify all Drainage meets design and functional requirements
6e9fa474-68e7-4ff1-8c06-cd343398e3c2 | signoff | United Civil & CHINT Hold Point
d0a35101-1a75-495d-990f-c8aed4abea90 | section | Post Construction and Handover - Non-Conformance-Reports
d809cd6b-1aa2-4308-8bcb-21dac26226ae | checkpoint | Each Non-Conformance Reported, Rectified & Closed Out
f90e2ca3-a10b-4fd9-902e-5297b67ec1da | section | Post Construction and Handover - Punch List
c9f2813c-b739-4f39-bf7d-c492f31d9432 | checkpoint | Development of Punchlist with Client and Contractor Representative
0de1d6c9-d086-5e13-acdc-17eaf781d619 | note | Punch List closed out in a timely mannor
11a63b49-57be-4463-9d2a-f8d37c52515c | section | Post Construction and Handover - Documentation
96c51761-fdbe-417f-aec7-0fbf96e74a7e | checkpoint | Documentation
55967e0b-a625-5db1-90d8-fd975f8f77ec | note | On completion of the RMU Drainage
d2958864-784d-553d-aceb-042e0af2730f | note | Submission of all test results, ITC's and any as-built drawings
0ce25684-2956-569c-b7cf-9f948ae4133e | note | Complete and approved by client
2ab9614e-e4f5-4c7f-8e7c-3c1de7244518 | signoff | United Civil & CHINT