## Table 1
INSPECTION AND TEST PLAN
SITE INSTALLTION | [7 empty] | ITP No. |  |  | Revision No. | REV02
ITP Name | Site Installation CLD-200 3mm alum perf CW module |  | Elevation or Area : building A 5&6
Project | New Footscray Hospital |  | Module. No or Item : CLD-200 3mm alum perf CW module
Building Ref. | Building A level 5&6 |  |  |  | Refer to O&M Manual for Project for maintneance and care proceedures for cladding types
Check / Inspection Required |  | Responsibility | Acceptance Criteria |  | Reference Document / IFC Shop Drawing Number AS1562.1-2018 | Frequency of Testing and Inspections | Client | Date | Facadex | Date | Comments
IFC Shop Drawings Approved |  | MPX | MPX / Architect Sign Off
Material Approval |  | MPX | MPX / Architect Sign Off | [7 empty] | Check colour is correct as per shop drawings
Module (Panels/Bolts/Screw/Washers) delivered to site free of damage and deformation |  | Facadex | Facadex sign off. | [7 empty] | Check colour is correct as per shop drawings
Grid lines established and site set out complete |  | Facadex | Facadex sign off. | [7 empty] | If installed off site no gridline available
250x50x6mm Alum angles spanning at the back of the module has been secured and fastened to the L brackets for haning the module. |  | Facadex | Facadex sign off.
ensure the 40x40x3mm SHS horizontal rail 450crs fixed to the C channels at the back of the module |  | Facadex | Facadex sign off.
ensure the Subsill has been installed with the support 250x100x3mm alum angles at the bottom. |  | Facadex | Facadex sign off.
bottom Shelfangles chemset fix to concrete slab has been installed for the module to be sit on where ther is a louvre behind. |  | Facadex | Facadex sign off.
0.48BMT colourbond flashing has been installed for the weather proof to IFC |  | Facadex | Facadex sign off.
Perf with CW frame Panels checked for paint scratches and dents post installation |  | Facadex | Facadex sign off.
Perf Cladding Panels installed to IFC specification |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
Connections (screws/rivets) checked for damages |  | Facadex | Facadex sign off.
HOLD POINT- All Criteria above must be signed off before proceeding
Client inspection of installed product with Facadex representative. Any sighted defects (incurred during installation) to be recorded and subcontractor to be notified within 24 hours of installation. |  | Facadex / Builder | Defect notification via email or chosen coorespondece
Evidence of close out / rectification
(SI / Photographic record & evidence of close out to be attached to this ITP for each wall type)
Sign of only once agreed that wall is defect free
AUTHORITY TO PROCEED
Foreman – Checklist Completed |  |  |  | Date / Time
Coordinator – Checklist Completed |  |  |  | Date / Time
In signing the above the Facadex Construction and Named parties are confirming that all works have been completed in accordance with all the relevant Design Documentation & Specifications. Facadex Construction located at 13-14 Adams Court Sunshine West, VIC 3020