## Table 1
INSPECTION AND TEST PLAN
SITE INSTALLTION | [7 empty] | ITP No. |  |  | Revision No. | REV02
ITP Name | Site Installation CLD-200 3mm alum perf subframing |  | Elevation or Area : Building D 5&6
Project | New Footscray Hospital |  | Module. No or Item : CLD-200 3mm alum perf subframing
Building Ref. | Building D 5&6 |  |  |  | Refer to O&M Manual for Project for maintneance and care proceedures for cladding types
Check / Inspection Required |  | Responsibility | Acceptance Criteria |  | Reference Document / IFC Shop Drawing Number AS1562.1-2018 | Frequency of Testing and Inspections | Client | Date | Facadex | Date | Comments
IFC Shop Drawings Approved |  | MPX | MPX / Architect Sign Off
Material Approval |  | MPX | MPX / Architect Sign Off
Materials (top hat/screws) delivered to site free of damage and deformation |  | Facadex | Facadex sign off.
Grid lines established and site set out complete |  | Facadex | Facadex sign off.
75x254x75x3mm thk folded Z has been set out and installed to steel purling @1500 crs and fixings @900crs as per IFC |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
50x50x3mm alum SHS/EA horizontal has been set out and installed to vertical folded Z with #12 tek screws@600crs |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
Packers has been used to ensure the subframe is plumb for perf panels to be cladded on. |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
Connections (bolts/washers/screws) checked for damages |  | Facadex | Facadex sign off.
HOLD POINT- All Criteria above must be signed off before proceeding
Client inspection of installed product with Facadex representative. Any sighted defects (incurred during installation) to be recorded and subcontractor to be notified within 24 hours of installation. |  | Facadex / Builder | Defect notification via email or chosen coorespondece
Evidence of close out / rectification
(SI / Photographic record & evidence of close out to be attached to this ITP for each wall type)
Sign of only once agreed that wall is defect free
AUTHORITY TO PROCEED
Foreman – Checklist Completed |  |  |  | Date / Time
Coordinator – Checklist Completed |  |  |  | Date / Time
In signing the above the Facadex Construction and Named parties are confirming that all works have been completed in accordance with all the relevant Design Documentation & Specifications. Facadex Construction located at 13-14 Adams Court Sunshine West, VIC 3020