## Table 1
INSPECTION AND TEST PLAN
SITE INSTALLTION | [7 empty] | ITP No. |  |  | Revision No. | REV02
ITP Name | Site Installation CLD-214 lysaght spandek |  | Elevation or Area : Lysaght spandek
Project | New Footscray Hospital |  | Module. No or Item : CLD-214 lysaght spandek
Building Ref. | Building E north elevation level 5&6 |  |  |  | Refer to O&M Manual for Project for maintneance and care proceedures for cladding types
Check / Inspection Required |  | Responsibility | Acceptance Criteria |  | Reference Document / IFC Shop Drawing Number AS1562.1-2018 | Frequency of Testing and Inspections | Client | Date | Facadex | Date | Comments
IFC Shop Drawings Approved |  | MPX | MPX / Architect Sign Off
Material Approval |  | MPX | MPX / Architect Sign Off | [7 empty] | Check colour is correct as per shop drawings
Materials (Panels/Bolts/Washers) delivered to site free of damage and deformation |  | Facadex | Facadex sign off. | [7 empty] | Check colour is correct as per shop drawings
Grid lines established and site set out complete |  | Facadex | Facadex sign off. | [7 empty] | If installed off site no gridline available
Cladding Panels installed to manufacturers specifications |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
Cladding Panels checked for paint scratches post installation |  | Facadex | Facadex sign off.
0.55mm colorbond flashing has been installed to the gap to the strcutrue |  | Facadex | Facadex sign off.
Connections (bolts/washers/screws) checked for damages |  | Facadex | Facadex sign off.
HOLD POINT- All Criteria above must be signed off before proceeding
Client inspection of installed product with Facadex representative. Any sighted defects (incurred during installation) to be recorded and subcontractor to be notified within 24 hours of installation. |  | Facadex / Builder | Defect notification via email or chosen coorespondece
Evidence of close out / rectification
(SI / Photographic record & evidence of close out to be attached to this ITP for each wall type)
Sign of only once agreed that wall is defect free
AUTHORITY TO PROCEED
Foreman – Checklist Completed |  |  |  | Date / Time
Coordinator – Checklist Completed |  |  |  | Date / Time
In signing the above the Facadex Construction and Named parties are confirming that all works have been completed in accordance with all the relevant Design Documentation & Specifications. Facadex Construction located at 13-14 Adams Court Sunshine West, VIC 3020