## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-206-CIV-Calder-Street Lighting (Supply and Install)
ITP Description: |  | Street Lighting (Supply and Install)
Discipline (e.g. CIV/STR/RAIL: |  | CIV
Revision Number: |  | 0
Revision Date: |  | 2024-10-08
ITP created by: |  | Jason Quan/Derek Collins
ITP approved for use by: |  | Pradeep Talasila
Special Notes to ConQA Team : |  | This ITP is only to be used in Calder Park Drive Project
Inspection & Test Plan - Street Lighting (Supply and Install)
|  |  | Doc No.: ITP-206-CIV-Calder-Street Lighting (Supply and Install) | [5 empty] | Revision: | 0
[9 empty] | Date: | 2024-10-08
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | IFC Drawings | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.2 | Non Dependent | Jemena Electricity Networks | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.3 | Non Dependent | VR Section 733 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.4 | Non Dependent | AS/NZS 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.5 | Non Dependent | AS/NZS 1158.3.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | Preliminaries Preliminaries - Materials
2.1 | Material Compliance - Obtain and review manufacturer documentations for the supply of materials. | IFC Drawings Section 733 | Materials comply with IFC Drawings,VESI Standards. All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001. * Enter: Teambinder Hold Point Release Number [free text box] | Document Review | Per Source | HP | Nominated Authority | ConQA HP Release
2.2 | Inspection of supplied items upon delivery. | IFC Drawings VR Std Dwg TC1064, TC1065 | Supplied items are to correct spec, class, size, undamaged and brand new. Luminaires: At the time of delivery, the supplier shall provide hard copies of the following:  Installation Instruction Manual  Operation Instruction Manual  Storage, handling, loading and off–loading instructions  Test Certificates  Warranty Information Attach Delivery Dockets & Records Required | Visual /Site Inspection & Document Review | Per Delivery | IP | SE/PE/SPE | This ITP Signed Off
3 | Preliminaries - Procedures & Documentation
3.1 | ACCC Form (Australian Competition and Consumer Commission) | MRPA Quality Management Plan Jemena Electricity Networks | Before any works commence, the accredited contractor shall obtain an "ACCC Form" from AusNet Services representative for permission to commence works. * Enter: Teambinder Hold Point Release Number [free text box] | Document Review | Once prior to works commencing | HP | Nominated Authority | ConQA HP Release
3.2 | Subcontractor Prequalificaiton | MRPA Quality Management Plan Jemena Electricity Networks | Subcontractor to be a VEDN (Victorian Electrical Distribution Networks) accredited contractor. * Enter: Teambinder Hold Point Release Number [free text box] | Document Review | Once prior to works commencing | HP | Nominated Authority | ConQA HP Release
3.3 | VESI (Victorian Electricity Supply Industry) Auditor | MRPA Quality Management Plan Jemena Electricity Networks | VEDN approved civil auditor. (VESI Auditor Register) * Enter: Teambinder Hold Point Release Number [free text box] | Document Review | Once prior to works commencing | HP | Nominated Authority | ConQA HP Release
4 | Pre-installation Activities
4.1 | IFC Drawings | MRPA Quality Management Plan | Check the revision of the IFC drawings are current as per the drawing register (on Teambinder) | Document Review | Prior to starting Works and at regular intervals | HP* | SE/PE/SPE | This ITP Signed Off
4.2 | Survey set out | IFC Drawings Jemena Electricity Networks Technical Specifications | Set-out survey carried out by a surveyor and within the tolerances as per IFC Drawings and AusNet drawings/specs. | Visual Survey | Each Element | IP | SE/PE/SPE | This ITP Signed Off
5 | Installation Activities
5.1 | Pit and Conduit Installation | IFC Drawings | Conduits and pits to be installed as per IFC Drawings Attach: Subcontractor Installation Checklist | Document Review Visual | Prior to commencement | WP | SE/PE | This ITP Signed Off
5.2 | Conduit and Cable Detailing | Jemena Electricity Networks Technical Specification | Trench inspection detailing all conduits and cables being installed by a AusNet services approved detailer. Attach: Verification Document (As-Builts) | Site Inspection | Upon completion of each section | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.3 | Prepare the plinth foundation (Excavation & levels) | IFC Drawings | Check levels conform to relevant drawing depending on type of pole to be installed. | Visual Survey | Per Lot | IP | SE/PE/SPE | This ITP Signed Off
5.4 | Installation of Light poles | IFC Drawings | Light Poles to be installed as per IFC drawings in accordance with VESI requirements. | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP Signed Off
5.5 | Asset Labelling | IFC Drawings | Pole Labelling to be as per IFC Drawings. | Visual Inspection | Per Lot | IP | SE/PE/SPE | This ITP Signed Off
5.6 | Commissioning & Testing (Civil Audit) | Jemena Electricity Networks Technical Specification | Upon completion of all trenching and conduit install, a Civil audit by a VEDN approved Civil auditor will be completed and approved before procceding. | Commissioning & testing | Upon completion of each section | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.7 | Commissioning & Testing (Trench Inspection) | Jemena Electricity Networks Technical Specification | Trench inspection detailing all conduits and cables being installed by a AusNet services approved detailer Verification document: As-Builts | Commissioning & testing | Upon completion of each section | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.8 | Commissioning & Testing (Pre-commissioning) | Jemena Electricity Networks Technical Specification | Passing of the pre-commissioning audit with all non-conformances rectified. | Commissioning & testing | Upon completion of each section | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.9 | Commissioning & Testing (Final Audit) | Jemena Electricity Networks Technical Specification | Passing of the final audit will be completed by Jemena Electricity Networks to inspect the completed works with all non-conformances rectified. | Commissioning & testing | Upon completion of each section | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.1 | Testing and Certificate of Electrical Safety | Jemena Electricity Networks Technical Specification IFC Drawings | Prior to final acceptance, the contractor shall test all distribution cabinets, circuits, switches, PE Cells, luminaires, and all other electrical and electronic components for correct installation and operation Attach Documentation: Certificate of Electrical Safety for electrical installation | Document Review | Upon completion/ Work area | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
5.11 | PC Cert of Jemena Electricity Networks Agreement | Jemena Electricity Networks Technical Specification IFC Drawings | To be accepted and signed-off by MRPA and Jemena Electricity Neworks | Document Review | Upon completion/ Work area | IP | SE/PE/SPE Services Engineer | This ITP Signed Off
6 | Post-installation Activities
6.1 | Verification of Subcontractor conformance records / signed ITPs including any relevant verification sheets. | IFC Drawings Notes | Check conformance report against project conformance criteria. Attach Verification Docs: QA Records, Signed ITP including any verification documents, Commissioning & Testing Certificates. | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP Signed Off
6.2 | As-Built Drawings | IFC Drawings Notes | As built drawings for the metered lighting installations to be provided to the satisfaction of MRPA & Cardinia Shire Council. Attach: As Constructured Plans / As-Builts | Document Review | Upon completion/ Work area | IP | SE/PE/SPE | This ITP Signed Off
6.3 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in TeamBinder. | Document Review | Once, prior to closure of this lot / element / Work area | WP | SE/PE/SPE | This ITP Signed Off
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /