## Table 1
[5 empty] | Inspection and Test Plan - Control and Supervision of the Works | [13 empty] | Doc ID: FH-ZU2-QU-ITP035 REV: 0
Client: Melbourne Airport | [6 empty] | Contract No: CP14038-01 | [8 empty] | Prepared By: Jamal Khodr
Project: Taxiway Zulu | [11 empty] | Reviewed By: Jamal Khodr | [6 empty] | Date: 28/03/2025
Construction Process: ALER 3 Plumbing | [11 empty] | Approved By: Marco Poggenberg | [6 empty] | Date: 1/04/2025
Specifications: ZULU-BECA-001-SPC-00005, Drawings
Structure / Component: Plumbing works
Lot No: |  | Lot Details: | [7 empty] | Lot size/Quantity: |  |  |  | Date:
Item No. |  | Task/Activity Description |  | Inspection/Test | [11 empty] | HP/ WP/ AP/ IP/ TP/ SCP | Responsibility | Checked by:
|  |  |  | Frequency |  | Acceptance Criteria |  | Reference Documents |  |  | Inspection/ Test Method |  | Record of conformity |  |  |  | Project Engineer Principal’s Rep. Surveyor Foreman | Principal’s Rep. |  | FH | Date
1 |  | Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
1.1 |  | Check for correct documentation |  | Prior to commencing activity |  | Ensure that all employees and subcontractors are: - using the correct and complete set of drawings. - all drawings are the latest revision. |  | Drawings / Aconex Register |  |  | Verify |  | Drawings and drawing registers |  |  | HP* | Project Engineer
1.2 |  | Implementation of all measures and controls |  | Prior to commencing activity |  | All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP. |  | PSP, EMP, TMP, JSEA, SWMS, WP |  |  | Visual inspection |  | This ITP signed |  |  | HP* | Project Engineer
1.3 |  | Survey Checks |  | Prior to commencing activity |  | Survey set out to be completed for all assets |  | Drawings |  |  | Verify |  | This ITP signed |  |  | HP* | Project Engineer / Surveyor
1.4 |  | Submission & approval of shop drawings |  | Prior to commencing activity |  | HOLD POINT Submit shop drawings to the principal’s representative for approval prior to fabrication commencement. |  | ZULU-BECA- 001-SPC- 00005 Drawings Shop drawings |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Principals Representative
1.5 |  | Material Submissions |  | Prior to commencing activity |  | HOLD POINT Items to include but not limited to: - Refer to materials register and list items |  | ZULU-BECA- 001-SPC- 00005 Drawings |  |  | Verify |  | Aconex Reference |  |  | HP | Project Engineer / Principals Representative
1.6 |  | Temporary Works |  | Prior to commencing activity |  | Submission and approval of the following documentation (not limited to): - Certification of Lifting Points - Lift Plan - Certification of Ground Platform for lift - Lifting inserts |  | ZULU-BECA- 001-SPC- 00005 Drawings |  |  | Verify |  | Temporary Works Geo Report |  |  | HP* | Project Engineer
1.7 |  | Certificates of Compliance |  | Each Lot |  | Provide Suppliers Certificate of Compliance and Spatial Certificate of Compliance for  pumps, hot water units, and valves. |  | ZULU-BECA- 001-SPC- 00005 Drawings C1900.6 |  |  | Verify |  | Supplier’s Certificate of Compliance Spatial Certificate of Compliance (where required) |  |  | HP*
2 |  | Construction
2.1 |  | Delivery of Materials to site |  | Each Lot |  | Inspection of materials whilst still loaded on the truck prior to accepting the delivery on site. Identify any damage/defects prior to unloading of the material. |  | ZULU-BECA- 001-SPC- 00005 Drawings |  |  | Visual Inspection |  | This ITP Signed Materials Inspection Checklist on Conqa |  |  | IP | Project Engineer / Site Engineer
2.11 |  | Installation – Cold Water System |  | Each Lot |  | Verify pressure and flow, installation of water meter assembly, isolation valves, and boosting/reducing systems. |  | ZULU-BECA- 001-SPC- 00005, C1700.2.2(a), Drawings, AS/NZS 3500.1 |  |  | Visual Inspection |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.12 |  | Installation – Hot Water System |  | Each Lot |  | WITNESS POINT Installation of electric instantaneous hot water units, temperature control, and thermostatic mixing valves. Give notice for inspection of installed elements prior to covering/lining. |  | ZULU-BECA- 001-SPC- 00005, C1700.2.2(b), Drawings, AS/NZS 3500.4 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | WP | Project Engineer / Site Engineer / Principals Representative
2.13 |  | Installation – Sanitary Plumbing & Sewer Drainage System |  | Each Lot |  | WITNESS POINT Installation of vented gravity sewer drainage, floor waste gullies, and inspection openings. Give notice for inspection prior to backfilling any pipework. |  | ZULU-BECA- 001-SPC- 00005, C1700.2.2(c), Drawings, AS/NZS 3500.2 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | WP | Project Engineer / Site Engineer / Principals Representative
2.14 |  | Installation – Roof Drainage System |  | Each Lot |  | Installation of downpipes, eaves gutters, and stormwater drainage systems. |  | ZULU-BECA- 001-SPC- 00005, C1700.2.2(d), Drawings, AS/NZS 3500.3 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.15 |  | Installation – Insulation |  | Each Lot |  | Application of thermal insulation, fire properties, and vapour barriers. |  | ZULU-BECA- 001-SPC- 00005, C1715.3, C1715.4, Drawings, AS/NZS 3500.4 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.16 |  | Installation – Pumps |  | Each Lot |  | Installation of submersible sump pumps, control panels, and electric motors. |  | ZULU-BECA- 001-SPC- 00005, C1719.4, C1719.6, Drawings, ISO 2858, BS EN ISO 9906 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.17 |  | Installation – Fixtures, Fittings, and Appliances |  | Each Lot |  | WITNESS POINT Installation and connection to water supplies and drainage piping. Give notice for inspection after installation. |  | ZULU-BECA- 001-SPC- 00005, C1750.1, Drawings, AS/NZS 3500 |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | WP | Project Engineer / Site Engineer / Principals Representative
2.18 |  | Testing |  | Each Lot |  | Carry out testing as per requirements in C1700.8 for water and sewer services. Conduct flushing, pressure testing and disinfection. |  | ZULU-BECA- 001-SPC- 00005 C1700.8 Drawings |  |  | Verify |  | This ITP Signed Building Eng ITP |  |  | IP | Project Engineer / Site Engineer
2.19 |  | Survey As Built |  | Prior to Covering Services |  | Survey to pick up services prior to covering |  | FH QMP |  |  | Verify |  | Survey |  |  | IP | Project Engineer/Survey or
Final Inspection The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications. Print Name: Position: Signature: Date: / /
Legend:
| HP |  | Hold Point | Work shall not proceed past the HP until released by the Principal’s Representative |  |  |  |  | IP |  | Inspection point |  |  |  | Formal Inspection to be done and recorded
| HP* |  | Fulton Hogan Hold Point | Work shall not proceed past the HP* until released by Fulton Hogan |  |  |  |  | TP |  | Test Point |  |  |  | Product compliance test to be undertaken and recorded/reported
| WP |  | Witness Point | An inspection which must be witnessed by the Principal’s Representative |  |  |  |  | SCP |  | Survey conformance point |  |  |  | A qualified surveyor to check product/section/structure and report
| AP |  | Approval Point | Written or verbal approval given by the Principal’s Representative
Notes