## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Test Equipment No: |  |  |  |  | Yes | Test Equipment No: | 0302521d-8ffd-4994-b7fa-e951a9319a18
checkpoint-status |  |  | checkpoint | Details
text | 17bdac6e-0ccd-5518-b403-aebff4dad6fa |  | textbox | Make
text | 9b3ea939-bc5f-5366-9b6b-71de0d291da5 |  | textbox | Model
text | 6f002d23-a46f-53d1-9841-7abecec29a02 |  | textbox | Serial No
text | 70b4f3a9-71de-53a8-86a0-3dbdba63038b |  | textbox | Calibration Expiry Date
checklist-flat |  |  | checklist | ITR-I-44A Entec - Fibre Optic Cable |  |  |  |  | Yes | ITR-I-44A Entec - Fibre Optic Cable | 142e0511-6c7d-4743-a670-52f17af2c066
checkpoint-status |  |  | checkpoint | Verify cable type, size, colour code and tag is in accordance with the Cable Schedule.
checkpoint-status |  |  | checkpoint | Check cable optical fibre loss and record data in the attached report.
checkpoint-status |  |  | checkpoint | Check fibres correctly identified and labelled.
checkpoint-status |  |  | checkpoint | Check fibres correctly terminated and secure.
checkpoint-status |  |  | checkpoint | Upload testing sheet scans
checklist-flat |  |  | checklist | Earth Pegs |  |  |  |  | Yes | Earth Pegs | 1708e3f0-1ac7-496c-a00e-74ca1c5fd8be
checkpoint-status |  |  | checkpoint | Mold type identified
select | ca089ef0-0ba8-57fc-a2ec-3268a6aeaefe |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | 2baf3733-adb9-5df9-ae78-361a69ce7000 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | 9f498b7a-9f8b-5e6e-a00f-75744326ce43 |  | textbox | Result:
label | 77d7e856-71bb-513c-b7b5-ed18f7cf5ee1 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Continuity test [Peg to Earth Bar]
text | 27546946-fd15-5ebc-b9e1-a3c2ade9e860 |  | textbox | Result:
checkpoint-status |  |  | checkpoint | 3 Wire Earth test
text | 8c1f08ed-994f-5329-b116-f2837397d159 |  | textbox | Result:
label | f2c9b208-609c-534e-ba61-aaf993a319c4 |  | note | Pass if <1 ohm
checklist-flat |  |  | checklist | TEST - Cadwelds Checklist |  |  |  |  | Yes | TEST - Cadwelds Checklist | 17f06001-f430-4f3e-85b1-e90fe58c8ced
checkpoint-status |  |  | checkpoint | Mold type, # and cable size identified
select | ba1a7d52-38af-58e0-bd39-468819b562e4 |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horrizontal Tee
select | 34a05e9e-9e56-5163-9232-ce1caede9b5f |  | dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C
select | 75459cf9-03e4-5e96-bac8-6c99220c0a32 |  | dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee Tee
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | 7613b12d-6a84-57f7-86d9-e8f133e2f9b9 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | 162fc000-0717-528e-aa7b-10cf77a54db3 |  | textbox | Result :
label | daabe1f1-2aaf-53c1-a3fe-5afe92c7c015 |  | note | Pass if <50 micro ohms
label | d981046b-4c8e-5ccd-aa01-e68f9c3d75db |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER, 3M TEMFLEX 1500 GREEN TAPE
label | 8e1caf8f-4b95-5f39-bbe9-4efe648f6d06 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | GPS coordinates taken
text | 5c675ed3-ea07-55d8-9d78-c2f8f47ffcd6 |  | textbox | Notes:
checklist-flat |  |  | checklist | ITR-E-03A Entec - UPS Installation |  |  |  |  | Yes | ITR-E-03A Entec - UPS Installation | 1911603a-0fb2-468d-8c0c-13a5eaec51b2
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule.
checkpoint-status |  |  | checkpoint | Check for mechanical damage.
checkpoint-status |  |  | checkpoint | Panel IP rating is correct.
text | 66d43c57-a995-5f34-9264-e5ebf0774d09 |  | textbox |  |  | IP.
checkpoint-status |  |  | checkpoint | Holding down arrangement and seat alignment correct.
checkpoint-status |  |  | checkpoint | Panels aligned correctly.
checkpoint-status |  |  | checkpoint | Earth alignment to vendor specification & connecting link bolts torqued to the manufacturers recommendations & marked.
checkpoint-status |  |  | checkpoint | External bonding correct
checkpoint-status |  |  | checkpoint | Bus bar alignment to vendor specifications & connecting link bolts torqued to the manufacturer’s recommendations & marked.
text | c92d7bb0-c3f4-5add-af4c-9edb4a804afc |  | textbox |  |  | Nm.
checkpoint-status |  |  | checkpoint | Phase identification correct.
checkpoint-status |  |  | checkpoint | Instrument, indication lamps & interlocks correct.
checkpoint-status |  |  | checkpoint | Main switches, contactors, fuses etc. sized & identified correctly as per Single Line Drawings.
checkpoint-status |  |  | checkpoint | Check main isolator switch operation.
checkpoint-status |  |  | checkpoint | Check bypass isolator switch operation.
checkpoint-status |  |  | checkpoint | Check DC UPS battery isolator switch operation.
checkpoint-status |  |  | checkpoint | COM Interface & Mod Link.
checkpoint-status |  |  | checkpoint | Padlocking facilities correct.
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check manual operation of selector switch, MCB, push button, etc.
checkpoint-status |  |  | checkpoint | Incoming cable correctly installed, terminated & supported.
checkpoint-status |  |  | checkpoint | Unused cable entries sealed.
checkpoint-status |  |  | checkpoint | All internal cabling & wiring neat, correct & tight.
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
checkpoint-status |  |  | checkpoint | Fans correctly installed.
checkpoint-status |  |  | checkpoint | Verify continuity of earth bar to frame
text | 4b8bacc9-09a5-5c81-ba5f-3275836cfb78 |  | textbox |  |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check Busbar Insulation resistance between Phases, Phases & Earth (690V-2500VDC, 400V -1000VDC)
text | f73da252-281b-56c3-a7eb-ce5a4c484f69 |  | textbox | Temp |  |  | Celsius
text | 2551a823-a08d-57a0-b9a5-f583fe41260f |  | textbox | L3-L2 |  |  | Megaohm
text | 2cacfc0b-83fb-54f8-b230-18f09429055b |  | textbox | L3-L1 |  |  | Megaohm
text | d1ed1486-0e78-5953-b706-1d253dd50941 |  | textbox | L3-N |  |  | Megaohm
text | 219eb719-f802-55b7-b04f-e4091532d598 |  | textbox | L3-E |  |  | Megaohm
text | ef4e1867-798b-564d-b15d-ae729381f993 |  | textbox | L2-L1 |  |  | Megaohm
text | 72aee538-7114-5306-98cd-18f57874a2df |  | textbox | L2-N |  |  | Megaohm
text | 9737212f-aab1-5a55-96d1-6bd4cd18d3d9 |  | textbox | L2-E |  |  | Megaohm
text | 6b66572e-005c-52bd-85ee-b01624a72d55 |  | textbox | L1-N |  |  | Megaohm
text | 5b7ceac6-eb51-5176-b340-c68d5629f471 |  | textbox | L1-E |  |  | Megaohm
text | c235f3e1-8ade-59ec-b232-31913f81f486 |  | textbox | N-E |  |  | Megaohm
checkpoint-status |  |  | checkpoint | Confirm Ductor test recorded- (ITR-E-21A)
checkpoint-status |  |  | checkpoint | Drawings marked up with relevant changes and As-builts complete.
checklist-flat |  |  | checklist | ITR-E-51A Entec - Cable tray and transits |  |  |  |  | Yes | ITR-E-51A Entec - Cable tray and transits | 1bfcad8d-bb94-4750-93d0-1297f2cc09b2
checkpoint-status |  |  | checkpoint | Verify cable tray installed as per drawings.
checkpoint-status |  |  | checkpoint | Verify cable tray correctly fixed to structure with adequate support.
checkpoint-status |  |  | checkpoint | Rack covers fitted where required.
checkpoint-status |  |  | checkpoint | All bend radiuses correct.
checkpoint-status |  |  | checkpoint | Cable tray has no sharp projections or edges.
checkpoint-status |  |  | checkpoint | Cable tray sections adequately secured to each other.
checkpoint-status |  |  | checkpoint | Earth continuity bonding strap secure and greased on hinged, flexible and split sections.
checkpoint-status |  |  | checkpoint | Tray identification stencilled on each side of each section.
checkpoint-status |  |  | checkpoint | Protective kick plates installed.
checkpoint-status |  |  | checkpoint | Cables mechanically protected where applicable.
checkpoint-status |  |  | checkpoint | Tray bonded to structure at correct locations.
checkpoint-status |  |  | checkpoint | Carry out ductor test and record result.
text | b1fe17eb-7145-5874-8946-78d8f88fc853 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Expansion guides fitted as required.
checkpoint-status |  |  | checkpoint | Cut edges made good and protected as per specification.
checkpoint-status |  |  | checkpoint | Transit frame installed as per drawings.
checkpoint-status |  |  | checkpoint | Transit frame identification marked correctly and visible.
checkpoint-status |  |  | checkpoint | Frame correctly packed with correct sized blocks and infills.
checkpoint-status |  |  | checkpoint | Correct stay plates fitted (non-ferrous for single core power cables).
checkpoint-status |  |  | checkpoint | Rated insulation installed to transit (where required).
checkpoint-status |  |  | checkpoint | Cables entering and leaving transits adequately supported and protected.
checkpoint-status |  |  | checkpoint | Cables pass through frames without strain on blocks.
checkpoint-status |  |  | checkpoint | All cables identified on both sides of transit and visible.
checklist-sectioned |  |  | checklist | ITR-E-53A Entec - Electrical Earthing |  |  |  |  | Yes | ITR-E-53A Entec - Electrical Earthing | 22753d21-1e66-45f4-9e72-5e94569cb30d
checkpoint-group |  |  | section | General
checkpoint-status |  |  | checkpoint | Confirm earth grid layout.
checkpoint-status |  |  | checkpoint | Record number or earth electrodes.
checkpoint-status |  |  | checkpoint | Record number of grid interconnections and number of equipment/structure connections and ensure that layout is in accordance with design drawings.
checkpoint-status |  |  | checkpoint | Ensure that all metal work is earthed as required.
checkpoint-status |  |  | checkpoint | Check welding of earth bosses and associated surface finish.
checkpoint-status |  |  | checkpoint | Ensure that earth cables/conductors have adequate mechanical protection i.e. conduits, kick-plates etc at points of high exposure.
checkpoint-status |  |  | checkpoint | Ensure that brazing or welding of all joints has been completed correctly.
checkpoint-status |  |  | checkpoint | Ensure that adequate corrosion and weather protection has been installed around all connections, joints, lugs, cad (thermal) welds and earth bosses
checkpoint-status |  |  | checkpoint | Ensure that earth electrodes are located within a protected, covered and identified surround.
checkpoint-status |  |  | checkpoint | All earth bosses and studs tight and fitted with shake proof washers and coated with protective coating.
checkpoint-group |  |  | section | Earthing Conductors
checkpoint-status |  |  | checkpoint | Ensure that earthing conductor size is correct in accordance with approved installation drawings.
checkpoint-status |  |  | checkpoint | Check cable terminations/joints to ensure that all lugs/barrels have been crimped correctly.
checkpoint-status |  |  | checkpoint | Check all points of connection ensure contacts clean and greased.
checkpoint-status |  |  | checkpoint | Check termination and ensure that correct flat and spring washers are in place.
checkpoint-status |  |  | checkpoint | Check terminations to ensure that all connections are correct and tight.
checkpoint-status |  |  | checkpoint | Check that all bi-metal connections have been performed correctly to manufacturer’s requirements.
checkpoint-status |  |  | checkpoint | Ensure that the earth cables to the main earth electrodes are terminated at each end of the main earth bar.
checkpoint-status |  |  | checkpoint | Ensure that earth cable identification markings are in place.
checkpoint-status |  |  | checkpoint | Ensure that earth connections are not multi-coiled or ‘pig-tailed’ but are terminated as straight as possible.
checkpoint-group |  |  | section | Earth Bar Installation
checkpoint-status |  |  | checkpoint | Check for correct assembly of equipment.
checkpoint-status |  |  | checkpoint | Check fixings and mounting points conform to project specification and are secure.
checkpoint-status |  |  | checkpoint | Check for equipment levels and alignment.
checkpoint-status |  |  | checkpoint | Using an Earth Resistance tester, measure earth resistance between auxiliary earth points (electrodes) or main earth bars & the earth body.
checkpoint-status |  |  | checkpoint | Measure earth continuity from each earthing location and/or equipment earth frame to the nearest auxiliary earth point (electrode) or main earth bar – (record resistances in following table).
checkpoint-status |  |  | checkpoint | Drawings marked-up to ‘as built’ status
checkpoint-group |  |  | section | Test Results
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests: From Main Earth Bar (Location) to Earth Body
text | f4686bb2-fc26-50ac-bc2a-848f0e76a80e |  | textbox |  |  |  | Location
text | d9703645-d81d-5af9-87cf-c87094fa099f |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests: From Main Earth Bar (Location) to Earth Body
text | 9582b667-b945-55d1-aaf3-8363ee8c393c |  | textbox |  |  |  | Location
text | 8c608077-c064-5d07-b3ed-74c5c2326df1 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests: From Main Earth Bar (Location) to Earth Body
text | 3c19585b-529f-552d-b2e1-d4b95e763954 |  | textbox |  |  |  | Location
text | 39a707ce-3aa2-5c5c-b641-9ce0b7d14762 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Resistivity Tests: From Main Earth Bar (Location) to Earth Body
text | ca5a5808-2b3a-5cbd-8480-3ad94f745230 |  | textbox |  |  |  | Location
text | 8a00f3f7-590d-5b3e-98bd-755f59358b41 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | ef60512d-87a3-5933-9e03-2323cb56090c |  | textbox |  |  |  | Location & #
text | ceae9962-53ba-5b2a-807a-32b3f5465133 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | 174cc819-019b-5e63-b728-4f5337bbfbae |  | textbox |  |  |  | Location & #
text | 2700b75c-d86a-507d-ab91-6a51a7091cdc |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | ad2c81b8-fe49-5466-91c5-04156f41a1a2 |  | textbox |  |  |  | Location & #
text | 8dd1baf7-2c63-5946-8d04-a178c64924d6 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | acb6d649-c2ed-5544-bf7e-e6097235e4ee |  | textbox |  |  |  | Location & #
text | 21538c4d-ed94-543b-8160-ddd1b4d24954 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | 9df7fb8b-70ca-51e7-b31b-c211246636e6 |  | textbox |  |  |  | Location & #
text | fc7f079d-3729-561b-be44-50cde6f9ee80 |  | textbox | Result: |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth Continuity Tests: From - Main Earth Bar (Location) to Earth Electrode (number/description)
text | ba5e31cb-3f83-5ca4-9ee5-089b80f946f4 |  | textbox |  |  |  | Location & #
text | 5741ab82-116f-5374-a356-06a441c14d4d |  | textbox | Result: |  |  | Ohm
checklist-flat |  |  | checklist | ITR-E-01A Entec - Cable Pre-installation |  |  |  |  | Yes | ITR-E-01A Entec - Cable Pre-installation | 234b1b14-8354-4382-b832-13be7e8bb7b2
checkpoint-status |  |  | checkpoint | Check cable details are correct and in accordance with cable schedule.
checkpoint-status |  |  | checkpoint | Where installing cable on cable tray/ ladder, conduit, Unistrut or similar cable enclosure, ensure (Cable Tray & Transits) has been completed and submitted.
checkpoint-status |  |  | checkpoint | Sufficient rollers in place to prevent excessive cable rubbing, (if applicable).
checkpoint-status |  |  | checkpoint | Care should be taken that cables are not left on any area where it may be subject to damage. Cables must not be left in or across trafficable areas.
checkpoint-status |  |  | checkpoint | If a winch is used for pulling, check:
boolean | c91be635-c753-5217-ba34-16db0a6b7cb2 |  | tickbox | Type and rated maximum loads are identified and pulling tension does not exceed recommended maximum tension rating of the winch or cable.
text | ac529813-e8e8-5eae-b17e-aa4c31e8af7e |  | textbox | Record maximum pulling tension. |  |  | kN
text | fc8234c9-8e00-53bc-adde-35c1acd9073b |  | textbox | Capstan speed. |  |  | RPM
text | 715943ce-9596-5cd7-85e3-a8c7e53addad |  | textbox | Cable speed. |  |  | Metre per minute
boolean | d6aad502-1c68-5468-bfb1-70bfc4c55a9b |  | tickbox | Is winch secured and anchored?
boolean | 1f843f8e-9b4b-5560-8ab0-3a7249c809b1 |  | tickbox | Cable stocking is correct size and secured?
checkpoint-status |  |  | checkpoint | In all cases, ensure the cable minimum bending radius is not exceeded.
checkpoint-status |  |  | checkpoint | Check cable installed undamaged & cable ends are sealed to prevent the ingress of moisture.
checkpoint-status |  |  | checkpoint | Cable clamps, cleats, ties, etc. are of suitable type and spacing as per the requirements.
checkpoint-status |  |  | checkpoint | Segregation from other electrical systems, pipes or structures has been by separation, barriers, or distance (a minimum of 300mm).
checkpoint-status |  |  | checkpoint | Cable markers are attached at either side of all transits and at every connection/ termination point.
checkpoint-status |  |  | checkpoint | All cable installation drawings marked up “As Built”.
checklist-flat |  |  | checklist | ITR-I-21A Entec - Instrument Cables |  |  |  |  | Yes | ITR-I-21A Entec - Instrument Cables | 25e4e6dc-e607-4f87-aaf5-22ea293775fe
checkpoint-status |  |  | checkpoint | Check for correct Tagging of Cable in both ends. Cable Type matches Cable Schedule.
checkpoint-status |  |  | checkpoint | Dressing / Clearing Check of Internal Connection Parts
checkpoint-status |  |  | checkpoint | Cable Mechanically protected
checkpoint-status |  |  | checkpoint | Cable correctly terminated and labelled
checkpoint-status |  |  | checkpoint | Continuity Check. (Test each conductor, inc shield)
checkpoint-status |  |  | checkpoint | Glanding / Locknuts correct
checkpoint-status |  |  | checkpoint | Bending radius satisfactory
checkpoint-status |  |  | checkpoint | Earthing in accordance with specification
checkpoint-status |  |  | checkpoint | Screen correctly made off
checkpoint-status |  |  | checkpoint | Confirm spare cores and Shields are terminated and conform to drawings and spec.
checklist-flat |  |  | checklist | ITR-I-25A Entec - Instrument Installation |  |  |  |  | Yes | ITR-I-25A Entec - Instrument Installation | 2c90e2d0-ccc9-4188-aa3c-dc26421c817d
checkpoint-status |  |  | checkpoint | Check Instrument is labelled, nameplate details are correct in accordance with the instrument index/ datasheet.
checkpoint-status |  |  | checkpoint | Instrument is suitably rated for area.
checkpoint-status |  |  | checkpoint | Ingress protection is suitable for area.
checkpoint-status |  |  | checkpoint | Instrument is undamaged, correctly mounted, orientation correct, elevation correct and free from vibration.
checkpoint-status |  |  | checkpoint | Instrument is accessible for maintenance and clear of obstruction and debris.
checkpoint-status |  |  | checkpoint | Vent lines are directed into a safe area.
checkpoint-status |  |  | checkpoint | Cable/s glanded and installed correctly, IP washers fitted, cable label installed.
checkpoint-status |  |  | checkpoint | Impulse, hydraulic, pneumatics, lines, air headers, correctly installed and supported.
checkpoint-status |  |  | checkpoint | In-line equipment installed and supported correctly.
checkpoint-status |  |  | checkpoint | Spare entries plugged correctly, using certified plug.
checkpoint-status |  |  | checkpoint | Instrument earthed in accordance with project specification.
checkpoint-status |  |  | checkpoint | Aspirator tubes and test gas tubes are installed and supported correctly.
checklist-sectioned |  |  | checklist | ITR-E-04A Entec - Conduit, Unistrut, Cable Tray / Ladder Installation |  |  |  |  | Yes | ITR-E-04A Entec - Conduit, Unistrut, Cable Tray / Ladder Installation | 4fa09410-33f1-419e-8a48-82cdd374c799
checkpoint-group |  |  | section | Conduit Installation Below Ground
checkpoint-status |  |  | checkpoint | Check equipment details are correct and in accordance with the data sheet and Equipment Schedule
checkpoint-status |  |  | checkpoint | Check conduit cable enclosure installation is as per design, layout drawings and specifications
checkpoint-status |  |  | checkpoint | Check conduit has been installed to the correct depth, cable below tape or Magslab installed
checkpoint-status |  |  | checkpoint | Confirm that there are no obstructions, and that the installation will be accessible for maintenance
checkpoint-status |  |  | checkpoint | Check all fixings are tight and secure
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bending radius
checkpoint-group |  |  | section | Cable Supports above ground
checkpoint-status |  |  | checkpoint | Check all machined parts cut or drilled shall have no rough edges, have been de-burred & protected by cold galvanising to restore the previous protection
checkpoint-status |  |  | checkpoint | All covers fitted if applicable
checkpoint-status |  |  | checkpoint | Check Unistrut supports are not a hazard to personnel
checkpoint-status |  |  | checkpoint | Correct ladder / tray size and type used
checkpoint-status |  |  | checkpoint | Support brackets welding and clamping, wire brushed and painted and complete
checkpoint-status |  |  | checkpoint | Sharp edges de-burred and cleaned, tray / ladder covers installed and secured
checkpoint-status |  |  | checkpoint | Splice plates, barriers, earthing system secure
checkpoint-status |  |  | checkpoint | Trays / ladders, supports, brackets not interfering with other disciplines
checkpoint-status |  |  | checkpoint | Check bends do not exceed the maximum cable bending radius
checkpoint-status |  |  | checkpoint | Inspect for system rigidity, and check levels to correct plane
checklist-sectioned |  |  | checklist | ITR-E-09A Entec - Earthing / Lightning Protection System Installation |  |  |  |  | Yes | ITR-E-09A Entec - Earthing / Lightning Protection System Installation | 599fb811-97e7-4141-b215-477d393c4ebf
checkpoint-group |  |  | section | Earthing System
checkpoint-status |  |  | checkpoint | Enter details here:
text | 0a174173-2a23-5221-9af2-43f00244a469 |  | textbox | Location of electrodes
text | c13d6856-bc7c-5012-ba1f-2a7997df47e2 |  | textbox | Electrode Length / Size
text | 47f556fd-831e-5e65-ad67-957065606ffe |  | textbox | Electrode type
text | d07ac44d-fc02-566a-a186-27148bd79fb0 |  | textbox | Method of Installing electrode
button | 1a906709-b663-5497-9616-7c75a55d4fe9 |  | button | Method of attaching to Electrode, please specify : | Cad Weld, Clamp, Lug/bolt
text | c92e73da-33b1-515d-ac27-b2e66800524f |  | textbox | No of electrodes
text | 3d907bf0-2475-501d-9a8f-5cb6f9e94381 |  | textbox | Drawing no.
checkpoint-group |  |  | section | Description
checkpoint-status |  |  | checkpoint | No of electrodes as per drawing, size, length material as per specifications
checkpoint-status |  |  | checkpoint | Earth pits correct as per specifications, covers, no damage
checkpoint-status |  |  | checkpoint | Connections to electrodes secure
checkpoint-status |  |  | checkpoint | Structural and equipment earth connections secure
checkpoint-status |  |  | checkpoint | Earth cable lugs secure, cable passes through concrete in PVC
checkpoint-status |  |  | checkpoint | Equipment bonding, connection to main earth bar secure
checkpoint-status |  |  | checkpoint | Earth electrode identified, MEN linked installed and labeled
checkpoint-group |  |  | section | Earth Electrodes Tests and Continuity Tests
checkpoint-status |  |  | checkpoint | Disconnected electrode (record results)
text | dfda050b-d16a-5651-bda1-7a6c7dd39522 |  | textbox | Electrode 1 |  |  | Ohm
text | ee266e72-4b86-5fd3-a7e5-a8f83a1bfdb4 |  | textbox | Electrode 2 |  |  | Ohm
text | d42bb4e6-8158-58aa-ab07-e4afdf398ce3 |  | textbox | Electrode 3 |  |  | Ohm
text | 42a231ee-6c60-559a-b3d7-5f7d95c8cf22 |  | textbox | Electrode 4 |  |  | Ohm
text | 9218128a-e3c7-5816-b567-ef6978bca45c |  | textbox | Electrode 5 |  |  | Ohm
text | 36eeb6ec-7dcf-55e7-8cef-3133e3f37855 |  | textbox | Electrode 6 |  |  | Ohm
text | eb5dafe8-9b90-5831-8daa-c99fc024844a |  | textbox | Electrode 7 |  |  | Ohm
text | 1f113b71-ae7c-544b-a379-f120b12c9152 |  | textbox | Electrode 8 |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth grid test results (electrodes connected)
text | 5fdb6884-16cb-56a9-ac1b-ac051e6b5904 |  | textbox | HV earth grid |  |  | Ohm
text | 49ecccb1-4cca-57bd-a811-949fcbdc1c8a |  | textbox | LV earth grid |  |  | Ohm
text | d6ea9f0f-301e-58ed-bf10-f6533803ca46 |  | textbox | Combine HV and LV earth grid |  |  | Ohm
text | c5a1fa96-0138-5f6d-b71e-404731de5432 |  | textbox | Instrument Earth |  |  | Ohm
label | 8d2b3d06-4017-5804-b435-78ee806b6ac5 |  | note | Note: Sketch of layout of earth electrodes showing electrode numbers and distances between electrodes.
label | ed069a5d-bc88-51d8-be0e-b9fff6c9ee5b |  | note | Test Equipment - as Per ITR 21A
checklist-flat |  |  | checklist | ITR-E-35A Entec - Distribution Board |  |  |  |  | Yes | ITR-E-35A Entec - Distribution Board | 616cb7b9-e11f-407d-978b-b7ab4194ce8f
checkpoint-status |  |  | checkpoint | Check Equipment and Nameplate details are correct and in accordance with the data sheet and Equipment Schedule.
checkpoint-status |  |  | checkpoint | Check holding down / mounting arrangement correct.
checkpoint-status |  |  | checkpoint | Check for mechanical damage
checkpoint-status |  |  | checkpoint | Check all internal cabling and wiring correct, including identification.
checkpoint-status |  |  | checkpoint | Check that Board is correctly earthed. Check Panel, Frame, Gland plate, Gland, Escutcheon plate.
text | 866a4309-2ea7-5086-8385-e3499e12e93d |  | textbox | Test and confirm the earth resistance between Board and local earth system is less than 1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Check tightness of circuit connections.
checkpoint-status |  |  | checkpoint | Check bus bars and connecting links tight.
checkpoint-status |  |  | checkpoint | Phase identification correct;
checkpoint-status |  |  | checkpoint | Check internals for cleanliness.
checkpoint-status |  |  | checkpoint | Check incoming cables are correctly terminated.
checkpoint-status |  |  | checkpoint | Check all unused entries are sealed correctly.
checkpoint-status |  |  | checkpoint | Check insulation resistance.
text | 4e1b48cd-3a61-5f4f-b6ad-a6935c00282b |  | textbox | Phase to Phase and Phase to Earth (Test voltage: 1000 V. Record Temp.) |  |  | Celsius
text | de950b79-ba96-5e16-a6f0-7b5670bdb7bd |  | textbox | L1 – L2 |  |  | Megaohm
text | 149e7006-2a80-5600-a15a-65221cb26604 |  | textbox | L1– L3 |  |  | Megaohm
text | d43b1000-42fc-54e5-966e-7f42f9e03751 |  | textbox | L2 – L3 |  |  | Megaohm
text | 8e65f7b7-1230-5ace-a44c-616ac7d960b7 |  | textbox | L1 – N |  |  | Megaohm
text | 05816050-d412-52c7-8383-1d35c330cf67 |  | textbox | L2 – N |  |  | Megaohm
text | 89da76d6-335b-5537-812e-6f2cb57a7b2e |  | textbox | L3 – N |  |  | Megaohm
text | 8437e9fd-c08f-5b4c-a3ca-b899d479e99a |  | textbox | L1 – Earth |  |  | Megaohm
text | 9f4b5bb8-dd09-5c9f-8783-9afb230464c1 |  | textbox | L2 – Earth |  |  | Megaohm
text | d00b511a-af9c-5330-8835-917436a5ab15 |  | textbox | L3 – Earth |  |  | Megaohm
checkpoint-status |  |  | checkpoint | Check fuses / breakers correct size per drawings.
checkpoint-status |  |  | checkpoint | Check glanding correct.(Type, size, installation)
checkpoint-status |  |  | checkpoint | Heaters correctly installed.
text | e01199e0-910c-53c4-887c-1abaa1c645dc |  | textbox | Measure and record insulation resistance. |  |  | Megaohm
checkpoint-status |  |  | checkpoint | Check all MCB's can be locked in the open position.
checkpoint-status |  |  | checkpoint | Ensure correct labelling to site standard-Circuits, board, cables, equipment
checkpoint-status |  |  | checkpoint | Confirm Legend is “As Built”
checkpoint-status |  |  | checkpoint | Check Different Voltage Segregation correct
checkpoint-status |  |  | checkpoint | Check enclosure IP rating is suitable for location
checkpoint-status |  |  | checkpoint | Check Door cable looms-cables are mechanically protected & multi stranded flexible.
checkpoint-status |  |  | checkpoint | Check correct rated RCDs fitted for Light & Power circuits
checkpoint-status |  |  | checkpoint | Check main switch operates in all active conductors-3/4 pole
checklist-flat |  |  | checklist | ITR-E-12B Entec - Schedule of test results DB |  |  |  |  | Yes | ITR-E-12B Entec - Schedule of test results DB | 63466452-99c8-4725-81c7-4811e3738d35
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-flat |  |  | checklist | ITR-E-22A Entec - Low Voltage Cable |  |  |  |  | Yes | ITR-E-22A Entec - Low Voltage Cable | 6923f2f8-9421-4635-bdb9-c43ef29cca55
checkpoint-status |  |  | checkpoint | Verify cable type, size, colour code and tags are in accordance with the Cable Schedule.
checkpoint-status |  |  | checkpoint | Check dressing / cleating.
checkpoint-status |  |  | checkpoint | Check cable for damage.
checkpoint-status |  |  | checkpoint | Check cable cores correctly identified and labelled.
checkpoint-status |  |  | checkpoint | Cable terminated with correct lugs and crimped with the correct die.
checkpoint-status |  |  | checkpoint | Check that cable phasing is correct and point to point each core for continuity.
checkpoint-status |  |  | checkpoint | Check Armour / Screen correctly made off.
checkpoint-status |  |  | checkpoint | Check armour continuity / earthing is maintained by the correct use of serrated washers and / or earth tags.
checkpoint-status |  |  | checkpoint | Glanding / Locknuts correctly installed.
text | d1222ad6-eecb-5c38-a6ca-913cca254bae |  | textbox | Gland type - from: |  | Haz. Area Rating
text | 134cbb4e-8314-5de3-9a53-739d109495a3 |  | textbox | Haz. Area Cert Details.
text | 7b9768f8-a1ac-5b21-ac8a-6dbf049f3ebf |  | textbox | Gland type - to: |  | Haz. Area Rating
text | ee9f868f-6f07-5800-bc2d-613971adde2b |  | textbox | Haz. Area Cert Details.
checkpoint-status |  |  | checkpoint | Insulation Resistance
text | dab145b1-17e2-54de-87cb-8e14e588dbdf |  | textbox | Amb. Temp. |  |  | Celsius
label | 8cacd81e-2a0c-5fb2-8644-a3c728530d8e |  | note | (Test voltage 1,000 VDC for LV cables and 5KVDC for HV cables)
text | 7e57af9f-73db-5992-8b9a-35229a192c4d |  | textbox | L1 – Earth |  |  | Megaohm
text | 9249d254-84e1-540d-a4cb-29b94d8a0f9b |  | textbox | L2 – Earth |  |  | Megaohm
text | d0fef0b8-e70e-52e1-b503-ac7d939ee388 |  | textbox | L3 – Earth |  |  | Megaohm
text | b20149f5-b3f2-5799-8368-7c2d92cc10de |  | textbox | L1 – L2 |  |  | Megaohm
text | 84cdc8b7-73c9-5100-bb5c-3b245f5e488d |  | textbox | L1 – L3 |  |  | Megaohm
text | 6c1481f5-d01b-5411-8975-8e7e03ad3aae |  | textbox | L2 – L3 |  |  | Megaohm
text | 711a418c-084b-581e-958b-ec0caf844ec4 |  | textbox | N – Earth |  |  | Megaohm
checkpoint-status |  |  | checkpoint | For multi-conductor cables record the lowest insulation reading:
text | 4cec44ed-01a3-5c6a-ac84-4831aac67248 |  | textbox | Between Conductors- |  |  | Megaohm
text | 107bd89c-eab0-568e-9549-51ce4aa79385 |  | textbox | Conductors to GND- |  |  | Megaohm
checkpoint-status |  |  | checkpoint | Confirm cable routing and segregation is correct.
checkpoint-status |  |  | checkpoint | Measure gland body continuity to earth. (Max 0.1 Ω)
text | b3227f78-ada9-5aea-af73-e28b92e8a84d |  | textbox
checklist-flat |  |  | checklist | ITR-E-17A Entec - Electrical Cable LV Power and control cable test record |  |  |  |  | Yes | ITR-E-17A Entec - Electrical Cable LV Power and control cable test record | 8b4660e4-cabf-4c88-ab71-57891d1bf521
checkpoint-status |  |  | checkpoint | Upload completed ITR scans
checklist-flat |  |  | checklist | ITR-E-43A Entec - Small power circuits |  |  |  |  | Yes | ITR-E-43A Entec - Small power circuits | 984a1a10-97f4-4507-bcc9-36b2e39c4794
checkpoint-status |  |  | checkpoint | Power circuit installed, hooked up & identified according to design drawings.
checkpoint-status |  |  | checkpoint | Fixtures properly supported and accessible for maintenance.
checkpoint-status |  |  | checkpoint | Check entire circuit for mechanical damage.
checkpoint-status |  |  | checkpoint | Check correct type of fixture installed (Ex rating & IP rating).
checkpoint-status |  |  | checkpoint | Cable terminations at junction boxes and fixtures.
checkpoint-status |  |  | checkpoint | All spare entries blanked off correctly.
checkpoint-status |  |  | checkpoint | Check Cables For Voltage Segregation Ensure clearance, labelling, colour coding is to standard
checkpoint-status |  |  | checkpoint | Check insulation resistance for phase to earth and neutral.
text | f4a23671-04bb-5893-b493-e95082614ccb |  | textbox | Test with 500 Volt Megger tester. Record current temperature. |  |  | Celsius
text | 2a85bac2-7637-5d63-b3a4-aed426217577 |  | textbox | Phase – Earth |  |  | Megaohm
text | be1263fb-5e45-55d2-9521-fe79b9ad8e1a |  | textbox | Phase – Neutral |  |  | Megaohm
text | 11f316f5-1a62-553a-9da5-7b24e80736c2 |  | textbox | Neutral – Earth |  |  | Megaohm
checkpoint-status |  |  | checkpoint | Check circuit is correctly earthed.
text | 5d3ecb09-2d50-5818-a39a-7f32d55adc68 |  | textbox | Test and confirm the earth resistance for the circuit is less than 1.0 Ohm |  |  | Ohm
checkpoint-status |  |  | checkpoint | Confirm welding outlets cannot be energized whilst plug is removed.
checkpoint-status |  |  | checkpoint | Check correct rating of protection device against design drawings.
checklist-flat |  |  | checklist | Cadwelds |  |  |  |  | Yes | Cadwelds | 9a16e4de-4cb0-4fc2-9f84-e8e08df8830d
checkpoint-status |  |  | checkpoint | Mold type, # and cable size identified
select | 58f6a4e7-1d04-5cde-93ef-7e40e831a9d1 |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horizontal Tee, XA 185mm N/C run to 185mm N/C4 120mm, T.A. 185mm N/C run to 50mm Horizontal Tee, X.A. 185mm N/C run to 185mm N/C Tap, X.A 185mm N/C # 50mm run to 185mm N/C # 50mm Tap, T.A 185mm N/C Run to 120mm N/C Horizontal Tee, T.A. 185mm N/C Horizontal Tee, T.A 50mm conduit run to 50mm flex in B-133.2L.F Sleeve tap, T.A 70mm run to 50mm hoorizontal tee, T.A 70mm conduit run to 50mm flex in B1332LF
select | ed4c3d61-22c0-5062-9fb5-da4c63055431 |  | dropdown | Select mold # | GTC-312C, XBQ-2C2C, TAC-2C2C, ZC-11159Z, TAC-3D2C, XAC-3D3D, ZC-11160Z, TAC-3D2V, TAC-3D3D, ZC-11161Z, TAC.2G2C, ZC-11162Z
select | e5b516be-85a2-5c47-b47f-efa34c9ff8ee |  | dropdown | Select cable size | 50mm to 16mm Earth Rod, 50mm to 50mm Tee, 50mm to 50mm Cross, 185mm to 185mm Tee, 185mm to 120mm Tee, 185mm to 120mm Cross, 185mm to 185mm Cross, 185mm to 50mm to 50mm Cross, 50mm to 70mm, 50mm to 50mm flex Tee Tee, 70mm to 50mm flex tee,185mm to 185mm flex tee
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | cf769ffa-19a3-53d5-b2b0-17f24f167bf3 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | 8f241dee-9f26-5c9b-8c5e-2be746e82030 |  | textbox | Result :
label | d7d48c05-1241-53e6-9f38-33af9b186328 |  | note | Pass if <50 micro ohms
label | 90da1cf9-9cc7-5192-ba3c-dc725a36da23 |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld wrapped in 3M SCOTCH 23 RUBBER, 3M TEMFLEX 1500 GREEN TAPE
label | 9b08347e-eb4b-509b-9f26-aa51bf2a621a |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | GPS coordinates taken
text | cba41b21-17d5-5ebf-b1c3-e6eb079b10cd |  | textbox | Notes:
checklist-flat |  |  | checklist | ITR-I-27A ENTEC- Instrument Panel Junction Box |  |  |  |  | Yes | ITR-I-27A ENTEC- Instrument Panel Junction Box | 9e6b404b-75ae-450d-8568-1b72a9efd034
checkpoint-status |  |  | checkpoint | Check Equipment and Nameplate details are correct in accordance with the instrument index
checkpoint-status |  |  | checkpoint | Check mechanical damage
checkpoint-status |  |  | checkpoint | Earthing correct, as per drawing, and tight
checkpoint-status |  |  | checkpoint | All internal cabling and wiring correct
checkpoint-status |  |  | checkpoint | Check for accessibility & correct mounting/supporting
checkpoint-status |  |  | checkpoint | Spare entries plugged using correct plug for area classification
checkpoint-status |  |  | checkpoint | Check all Cables & Cores are correctly identified
checkpoint-status |  |  | checkpoint | Check internals for cleanliness
checkpoint-status |  |  | checkpoint | Incoming cable condition and glanding correct
checkpoint-status |  |  | checkpoint | Check panel against drawing, area classification and spec's. IP / Ex rating are suitable for installed area
checkpoint-status |  |  | checkpoint | Check I.S / non I.S wiring segregation and identification is correct
checkpoint-status |  |  | checkpoint | Check that different voltage level segregation is correct
checkpoint-status |  |  | checkpoint | Check manual operation of selector switch, MCB, push button, etc
checkpoint-status |  |  | checkpoint | Check MCB/Fuse ratings (If applicable)
checkpoint-status |  |  | checkpoint | Check and record earth bar resistance to general earth.
checklist-flat |  |  | checklist | ITR-E-49A Entec - Electrical Switch Room |  |  |  |  | Yes | ITR-E-49A Entec - Electrical Switch Room | b0640d07-73db-4caa-a278-72eb3805d669
checkpoint-status |  |  | checkpoint | Substation Construction Finished
checkpoint-status |  |  | checkpoint | All Floor, Wall & Ceiling Penetrations Sealed
checkpoint-status |  |  | checkpoint | Danger, Warning & Resuscitation Signs Installed
checkpoint-status |  |  | checkpoint | All Equipment Installed
checkpoint-status |  |  | checkpoint | Lighting & General Power Installation Completed
checkpoint-status |  |  | checkpoint | All Earth Busbars Installed Satisfactorily & Connections Tight
checkpoint-status |  |  | checkpoint | All Telecommunication Equipment Is Installed & Operational
checkpoint-status |  |  | checkpoint | Smoke / Heat Detectors Installed (Including Vesda / Alarm Panel)
checkpoint-status |  |  | checkpoint | Substation Fire Alarm Panel Installed
checkpoint-status |  |  | checkpoint | HVAC Equipment Installed & Operational
checkpoint-status |  |  | checkpoint | Illuminated Exit Signs Installed & Operational
checkpoint-status |  |  | checkpoint | Hand-Held Fire Extinguishers Installed With Correct Type Available
checkpoint-status |  |  | checkpoint | All doors and locks operational (including emergency)
checkpoint-status |  |  | checkpoint | All keys available and handed to Commissioning E&I Superintendent
checkpoint-status |  |  | checkpoint | All safety equipment supplied – rubber mats, voltage sticks etc
checkpoint-status |  |  | checkpoint | Single line diagram detailing main power is fitted to wall
checklist-sectioned |  |  | checklist | ITR-E-12A Entec - Distribution Board Installation |  |  |  |  | Yes | ITR-E-12A Entec - Distribution Board Installation | b71be689-26fe-46a1-94f0-9464900131b3
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | Inspect for mechanical damage from freight and handling
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Electrical Equipment List, Document No. and nameplate details correct.
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, switches and fittings are in good order.
checkpoint-status |  |  | checkpoint | Confirm main isolator operates with associated switches and auxiliaries
checkpoint-status |  |  | checkpoint | Confirm main isolator and sub circuit MCB’s fitted with padlock system.
checkpoint-status |  |  | checkpoint | Check number of sub circuits as per design and specifications.
checkpoint-status |  |  | checkpoint | Check equipment panel external and internal earthing connections are securely fitted and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Check internal cables properly terminated and labelled
checkpoint-status |  |  | checkpoint | DB properly labelled, sub circuit MCB correct rating and application
checkpoint-status |  |  | checkpoint | Check sealing of all cable penetration (where applicable).
checkpoint-status |  |  | checkpoint | Active, Neutral and Earth bar properly identified and labelled, confirm load balance / phase to phase and phase to neutral
checkpoint-status |  |  | checkpoint | DB legend card correct and updated, As-built drawings complete
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-group |  |  | section | Insulation resistance
checkpoint-status |  |  | checkpoint | Equipment details
text | 42578c25-0f99-5172-9702-a85a7e064900 |  | textbox | Test equipment make:
text | 095a4806-5e6f-56eb-a9c7-734ddcea2710 |  | textbox | Calibration date:
text | cc136f12-a56c-56c6-9895-3769776175c1 |  | textbox | Serial no.
checkpoint-status |  |  | checkpoint | RWB / Earth
text | 28c59cd1-2459-570c-986c-126e60dd7c5d |  | textbox | Voltage
text | b9f33c66-457a-5d43-b996-2b84a72f79e6 |  | textbox | Duration
text | 74ef9cc4-24c5-5e5f-921a-b87694a59b79 |  | textbox | Resistance |  |  | Megaohm
checkpoint-status |  |  | checkpoint | R/W
text | 3eb1c1c9-5ec5-5eca-8bff-4d0279171af5 |  | textbox | Voltage
text | 091b96e4-0497-5f7b-9535-b45f216548d6 |  | textbox | Duration
text | 0374e813-261f-5cda-9bb1-87eb812c495f |  | textbox | Resistance |  |  | Megaohm
checkpoint-status |  |  | checkpoint | R/B
text | 497f91b7-b4dc-5caa-892b-058fc8a26335 |  | textbox | Voltage
text | 86d17b3c-d24f-594f-94a6-00eb22f14f97 |  | textbox | Duration
text | f5a233fb-df66-55bc-99ea-9008521b5846 |  | textbox | Resistance |  |  | Megaohm
checkpoint-status |  |  | checkpoint | W/B
text | 30ff5e51-1933-5944-87c6-838e5767efb2 |  | textbox | Voltage
text | 4419f2be-c075-50cf-8344-10c7ceaadadc |  | textbox | Duration
text | 6d6d39cb-e29a-573d-912d-670d89f1acac |  | textbox | Resistance |  |  | Megaohm
checkpoint-status |  |  | checkpoint | RWB / Neutral
text | 91330651-6f4e-5116-917a-b384f5fc1e35 |  | textbox | Voltage
text | eecadff3-0963-5cef-adc9-ebf35966b3f7 |  | textbox | Duration
text | c1824107-2b3a-5faa-8776-c27695c100e5 |  | textbox | Resistance |  |  | Megaohm
checklist-sectioned |  |  | checklist | ITR-E-09A Entec - Earthing and lightning protection |  |  |  |  | Yes | ITR-E-09A Entec - Earthing and lightning protection | b765a18a-ac31-4758-af76-52f2b7e487fc
checkpoint-group |  |  | section | Earthing System Details
checkpoint-status |  |  | checkpoint | Enter details here:
text | 3a6eb32b-1855-557f-835a-28851b546edc |  | textbox | Location of electrodes :
text | c3df4989-fa0e-550e-be21-a199b54e0dce |  | textbox | Electrode Length / Size :
text | 8587f6c2-4e99-517b-91d5-d2cb51daf9d1 |  | textbox | Electrode type :
text | 5ca2787e-209a-5332-bf57-619ab79feeef |  | textbox | Method of Installing electrode :
text | 0bd71a9d-01d2-587b-8a64-9d7981daafbe |  | textbox | No of electrodes :
text | 0a73cc2f-d8af-5d47-b11c-92222afaf829 |  | textbox | Drawing no.
checkpoint-group |  |  | section | Installation
checkpoint-status |  |  | checkpoint | No of electrodes as per drawing, size, length material as per specifications
checkpoint-status |  |  | checkpoint | Earth pits correct as per specifications, covers, no damage
checkpoint-status |  |  | checkpoint | Connections to electrodes secure
checkpoint-status |  |  | checkpoint | Structural and equipment earth connections secure
checkpoint-status |  |  | checkpoint | Earth cable lugs secure, cable passes through concrete in PVC.
checkpoint-status |  |  | checkpoint | Equipment bonding, connection to main earth bar secure
checkpoint-status |  |  | checkpoint | Earth electrode identified, MEN linked installed and labelled
checkpoint-group |  |  | section | Earth electrodes tests and continuity tests
checkpoint-status |  |  | checkpoint | Disconnected electrode (record results)
text | b656ca91-e6bb-502a-8ffc-2825cd25dd48 |  | textbox | Electrode 1 |  |  | Ohm
text | 4c51fbd4-aab3-5903-901b-12b6f7418ff7 |  | textbox | Electrode 2 |  |  | Ohm
text | 2deebd10-5521-5289-92d4-e316984ea282 |  | textbox | Electrode 3 |  |  | Ohm
text | 3c9961cf-a31c-51f9-bf69-829f58e72142 |  | textbox | Electrode 4 |  |  | Ohm
text | 6e0ec24d-6990-5838-98c9-9e250b0c9922 |  | textbox | Electrode 5 |  |  | Ohm
text | b2c25002-9c47-5421-9aa7-49ff01308424 |  | textbox | Electrode 6 |  |  | Ohm
text | 93f1ae46-90f6-5daf-a5e2-b63ad8275e25 |  | textbox | Electrode 7 |  |  | Ohm
text | 76a06b5c-8b5b-5689-b0fe-7a80e5cd45eb |  | textbox | Electrode 8 |  |  | Ohm
checkpoint-status |  |  | checkpoint | Earth grid test results (electrodes connected)
text | 7f615702-a9a7-5bfe-adb8-811aa57b457e |  | textbox | HV earth grid |  |  | Ohm
text | d3b83e1d-3531-5fc8-a2bd-683c0f5ba5ad |  | textbox | LV earth grid |  |  | Ohm
text | d495cf8f-1311-5021-b353-8d950e61a45d |  | textbox | Combine HV and LV earth grid |  |  | Ohm
text | b59b5e7d-334e-51c1-a44c-b090ad846c2b |  | textbox | Instrument Earth |  |  | Ohm
label | 41c9b1ee-a238-55cd-8bf3-76880c4b981b |  | note | Note: Sketch of layout of earth electrodes showing electrode numbers and distances between electrodes.
checklist-sectioned |  |  | checklist | ITR-E-06A Entec - Receptacle for small power GPO's |  |  |  |  | Yes | ITR-E-06A Entec - Receptacle for small power GPO's | c4f0b2e4-27cb-4bf5-9e2c-84d54c1f19f2
checkpoint-group |  |  | section | Equipment check & supports
checkpoint-status |  |  | checkpoint | Check equipment and nameplate details are correct and in accordance with the data sheet and Equipment Schedule.
button | 9a39208f-1632-5f04-8854-1c80ffdd712d |  | button | Receptacle stand is the correct size and type as per the site drawings & specification | YES, NO
button | 938ef2cd-fc85-55a8-aadc-4c830f3c698a |  | button | Fixings are the correct type and are securely fixed. | YES, NO
button | 2be2f1b8-72bf-5e29-82c2-4529fa5090cc |  | button | Location & height is correct as per the site drawings & specifications | YES, NO
checkpoint-group |  |  | section | Outlet & accessories
checkpoint-status |  |  | checkpoint | Receptacle is the correct type as per the site drawings & specifications
checkpoint-status |  |  | checkpoint | Receptacle Details:
text | 2be0ae0c-5bd0-575e-8bcf-094991043a62 |  | textbox | Outlet fitting IP Rating:
text | e8f7f7c3-5c37-5465-ae85-e3a249875f76 |  | textbox | Outlet fitting Ex (if applicable):
text | c4f409a5-8ca4-59df-b1c6-89a457860725 |  | textbox | Outlet rating (Amps): |  |  | Amps
button | 7f0254da-9d0d-5e63-ab64-6ae13e765790 |  | button | Installed undamaged | YES, NO
checkpoint-status |  |  | checkpoint | Junction Box Details (if fitted):
text | 363d3b6c-86b9-5bd4-bfc9-6b7a6899cca7 |  | textbox | Junction fitting IP Rating:
text | afc86c8e-d545-5101-b215-b4c2c0a01a17 |  | textbox | Junction fitting Ex (if applicable):
button | 3020011c-95a9-5850-9f2d-627b625f6dd7 |  | button | Installed undamaged | YES, NO
checkpoint-status |  |  | checkpoint | Equipment has been secured using the correct fixings and IP/ Ex rating has not been compromised.
checkpoint-status |  |  | checkpoint | All spare entries have blanked off with the correctly certified plug (if applicable).
checkpoint-status |  |  | checkpoint | All relevant drawings marked “As-Built”.
checklist-flat |  |  | checklist | ITR-E-11A Entec - Electrical Equipment Switch Room |  |  |  |  | Yes | ITR-E-11A Entec - Electrical Equipment Switch Room | c78a085b-696d-42cf-bda9-abf01b42f4c3
checkpoint-status |  |  | checkpoint | Ensure equipment Panel / DB / MCC / Switchgear is securely mounted within the correct location as shown on general layout drawings: Equipment had been received from the store in good condition as is the correct type as per specifications & data sheets.
checkpoint-status |  |  | checkpoint | Check tag number is in accordance with Electrical Equipment list Document No. etc.
checkpoint-status |  |  | checkpoint | Ensure there is no visible damage to the equipment and all meters, LED indicators, manual switches, PB, MCB, selector switches and fittings are in good order. Hold down mounting arrangement correct.
checkpoint-status |  |  | checkpoint | Confirm equipment panel has adequate air ventilation, as appropriate to its internal heat generation.
checkpoint-status |  |  | checkpoint | Confirm any slide-in cards / modules are firmly fitted to the equipment panel and properly identified.
checkpoint-status |  |  | checkpoint | Check panel air vents are clean and free of dust and dirt.
checkpoint-status |  |  | checkpoint | Check equipment panel external earthing connections are securely fitted to and properly terminated on the cabinet protective earth bar.
checkpoint-status |  |  | checkpoint | Where fitted, check instrument earth connections are securely fitted and properly terminated on the cabinet instrument earth bar.
checkpoint-status |  |  | checkpoint | Ensure any AC power connection(s) is securely fitted / identified different power sources and potentials and cabled to the appropriate Power Distribution Panel circuit breaker(s).
checkpoint-status |  |  | checkpoint | Check sealing of all cable penetration (where applicable).
checkpoint-status |  |  | checkpoint | Ensure all signal cables, including any RF coaxial cables, are correctly identified, and securely fitted to the equipment panel.
checkpoint-status |  |  | checkpoint | Where fitted ensure panel sliding rails are operating smoothly and without risk of damage to external cables and connectors. Check alignment of false floor after panel installation (where applicable).
checkpoint-status |  |  | checkpoint | Confirm panel is readily accessible for inspection and maintenance.
checkpoint-status |  |  | checkpoint | Equipment IP, Ex ratings, check tightness for all circuit connections
checkpoint-status |  |  | checkpoint | All internal cables and wiring is correctly numbered, colour coded and terminated
checkpoint-status |  |  | checkpoint | Check internals for cleanliness
checkpoint-status |  |  | checkpoint | Incoming cable compartment with gland plates provision,
checkpoint-status |  |  | checkpoint | Relays Metering and Protection ratings are correct as per design
checkpoint-status |  |  | checkpoint | As-builts complete
checklist-flat |  |  | checklist | TEST - Earth Pegs Checklist |  |  |  |  | Yes | TEST - Earth Pegs Checklist | e0eec232-4c7b-4565-b8c5-1db15dacdabe
checkpoint-status |  |  | checkpoint | Mold type identified
select | 4ceafb4e-553f-51ec-a3c4-f848ea4a3e12 |  | dropdown | Select mold type: | GT 50mm SQ to 16mm S/S vertical rod, XBQ - 50mm SQ to 50mm SQ crossover, TA 50mm SQ Horrizontal Tee
checkpoint-status |  |  | checkpoint | Cadweld Visual test
label | e38140a9-7132-5df9-9db4-8a34b11ca91d |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Cadweld Ductor test
text | 54664b99-4774-59d4-9ffb-32a0fd7f096d |  | textbox | Result:
label | 5d0968e8-ba81-5a40-ae37-5a829b6824dc |  | note | Please attach photo
checkpoint-status |  |  | checkpoint | Contunity test [Peg to Earth Bar]
text | abfe5148-4cd0-580c-aff8-1f6195ea0076 |  | textbox | Result:
checkpoint-status |  |  | checkpoint | 3 Wire Earth test
text | d3d3da17-903a-527b-81ca-0a4e89c0caf8 |  | textbox | Result:
label | 33c8fff7-bc37-5151-b062-45e042ad12f2 |  | note | Pass if <1 ohm