## Piling Overarching
CFA Piling RHS Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 3 – PRE-CONSTRUCTION (P&G / ESTABLISHMENT)
3.01 | Site Requirements
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.01 | Piling General
7.01.01 | Method Statements | A detailed method statement shall be prepared by the Constructor for the Designer’s review for each piling operation undertaken on the site. | 51/33669 - 3.2, 4 | Method Statement | 3 weeks prior to the commencement of each piling operation | HP | ENG
7.01.02 | Change of piling supervisor, crew of excavation method | When a change is made to the piling crew, excavation method or other change (e.g. variations in ground conditions) that could influence the quality of the works, the Designer may adjust the inspection requirement and frequency to suit the revised risk profile of the works. | 51/33669 - 6.3.2 | Notice | When a change is made | W | ENG
7.01.03 | Non-conformances | Non-conformance "make good" measure agreed with Engineer and subsequently completed. | 3.8.1 | NCR | As required | W | ENG

## Piling Materials
CFA Piling RHS Materials Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 4 – MATERIAL, PERSONNEL & THIRD PARTY APPROVAL | [10 empty] | Comment | EB Comment
4.07 | Piling Materials
4.07.01 | Piling Supervisor | A suitably qualified and experienced person shall be nominated by the Constructor as the ‘Piling Supervisor’. | 51/33669 - 3.9 | Supervisor Approval | Prior to any piling works commencing. | W | ENG
4.07.02 | Pile Mix Design | The Designer shall be provided with the proposed concrete mix design for review, prior to any piling works commencing. | 51/33669 - 5.1 | Mix Design | Prior to any piling works commencing. | HP | ENG
4.07.03 | Reinforcement Cage Fabrication Inspection | Designer inspection of reinforcement cage fabrication process for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure) | 51/33669 - 9.4 | Hold Point Release | First pile at every structure | HP | ENG
4.07.04 | CFA Pile Construction Record Card Template | Supply a template for the CFA pile construction record card a minimum of 3 weeks prior to the commencement of any piling works. | 51/33669 - 9.1 | Construction Record Card Template | 3 weeks prior to the commencement of any piling | HP | ENG

## Trial Pile Hold Points
CFA Piling RHS First Pile Hold Points Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.07 | First Pile at Every Structure
7.07.01 | Inspection of Reinforcement Cages Prior to Installation | Designer inspection of the reinforcement cage for the reinforced trial pile. | 51/33669 - 9.4 | Reinforcement Cage Inspection Record | Once | HP | ENG
7.07.02 | Concreting of Piles | Designer inspection of concreting for the reinforced and unreinforced trial piles. | 51/33669 - 9.4 | Pile Construction Record Card | Once | HP | ENG
7.07.03 | Compression Testing | A set of specimens for concrete tests shall be taken for each trial pile at the following intervals : a. Unreinforced trial pile: 24hrs (3no), 3 days (3no) b. Reinforced trial pile: 3 days (1no), 7 days (2no), 14 days (2no), 21 days (2no) and 28 days (2no). | GHD-Piling Specs 2.1-3.7.1 | Test results | Per pile | HP | ENG
7.07.04 | Pile integrity testing (PIT) | PIT completed on each pile after the concrete has achieved 75% of it's design strength (75% of 25MPa = 18.75MPa). Preliminary PIT results to be submitted to Designer within 24 hrs of testing being done. Final report to be submitted within 10 days of completion of testing for Designer's review. | GHD-Piling Specs 2.1-3.7.2 & 8.1 | Test results | Per pile | HP | ENG
7.07.05 | Pile Excavation | Unreinforced pile only to be to be exhumed to a minimum of 3m after PIT testing. To be photographed over the full length exposed and measurement of pile dimensions to be recorded at max. 500mm intervals. Results to be provided to GHD. | GHD-Piling Specs 2.1-3.7 & 3.7.3 | Photos | Once | HP | ENG

## Piling First Pile Hold Points
CFA Piling RHS First Pile Hold Points Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.07 | First Pile at Every Structure
7.07.01 | Inspection of any Reinforcement Cage Extension | Designer inspection of reinforcement cage extensions for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Reinforcement Cage Inspection Record | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.02 | Inspection of Reinforcement Cages Prior to Installation | Designer inspection of the reinforcement cage for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Photos | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.03 | Concreting of Piles | Designer inspection of concreting for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure). | 51/33669 - 9.4 | Pile Construction Record Card | First pile at every structure with the Opportunity to inspect remainder | HP | ENG
7.07.08 | Pile Head Preparation | Designer inspection of the pile head prior to incorporation into the connecting structure for the first pile at every structure with the Opportunity to inspect (at random for subsequent piles at the same structure) | 51/33669 - 9.4 | Hold Point Release | First pile at every structure | HP | ENG

## Piling Logging Hold Points
CFA Piling RHS Logging Hold Points Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.06 | Class 2 Pile Inspection Requirements
7.06.01 | Logging of Spoil Excavation | Class 2 – 25% of piles, First 2 No. piles constructed and then at random as advised by the Designer, Geological conditions match ground model and design assumptions. Designer to complete material logging for the first pile for all structures with the Opportunity to complete (at random) for subsequent piles. | 51/33669 - 6.3.2 | Pile Construction Record Card | First 2 No. piles constructed and then 25% at random as advised by the Designer | HP | ENG

## Pile Construction Card
CFA Piling RHS Pile Construction Card Inspection and Test Plan
Project: Arnold Dam
Number and Revision: DS2672-ITP-S123 - Rev 1
Item No. | Inspection and Test Point | Acceptance / Conformance Criteria | Standard / Specification | Verifying Document | Frequency | Verification Activity |  | Downer Conformance of Compliance Signoff
[6 empty] | Activity | By | Downer Signature | Date | Comments / Closeout Details
SECTION 7 – CONSTRUCTION ACTIVITY – PILING
7.02 | Setout and Excavation
7.02.01 | Nature of Ground and Subsurface Conditions | The Constructor shall inform the Designer where circumstances indicate that ground and / or groundwater conditions differ from those presented in the reports, indicated on the Drawings or interpreted from proof bores. | 51/33669 - 3.5 | Notice | Ongoing | S | SE
7.02.02 | Pile Logging Inspection | The logging of selected piles shall also be undertaken by the Designer to agree with the Constructor in identifying the founding stratum. | 51/33669 - 6.2.2 | Site Log | Each Pour | W | ENG |  |  | Add First Pile Hold Points Checksheet and / or Selected Logging Hold Points Checksheet as required.
7.02.03 | CFA Column Construction Control | Digital records from the on board Jean Lutz system containing all information specified in 7.1 of the GHD Specification. | 51/33669 - 3.8.1 | Jean-Lutz output | Each Pile | I | SE
7.02.04 | Instrument Calibration | Equipment used for monitoring shall be calibrated at the start of the Works and calibration certificates issued to the Designer prior to commencement. Depth tolerance = +/-50mm; concrete volume = +/-5% | 3.9.2 | Calibration certificates, record of depth measurement and concrete volume | Depth = Prior to commencing Concrete = Varies; see 3.9.2 | I | SE
7.03 | Pile Concreting
7.03.01 | Reinforcement Cage Cover | Pile reinforcement cages shall be located centrally within the pile excavation, such that final concrete cover to the extremities of the reinforcement cages is not less than 75 mm at any location. | 51/33669 - 3.8.2 | Site Record | Each Pile | D | SV / SE
7.04 | Concrete Pour
7.04.01 | Delivery Dockets | The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size. | RSV - CS - 1.9 | Dockets | Each Pour | R | PE
7.04.02 | Compression Testing | A set of specimens for concrete tests shall consist of four specimens from each major pour of concrete, one of which shall be tested at 7 days and the remaining three at 28 days after casting. | RSV - CS - 1.12 | Test Results | Each Pour | R | PE
7.05 | Pile Post Pour
7.05.01 | Pile Head Break Back | Pile heads shall be broken back to achieve A slightly convex profile so that the middle of the pile is nominally 25 mm above the average level at the perimeter of the pile and a Type B construction joint in accordance with standard NZS3109:1997. | 51/33669 - 3.8.3 | Site Record | Each Pile | I | SE
7.05.02 | Pile As-builting | On completion of pile installation and prior to incorporating any piles into the permanent works, the actual pile locations and verticality shall be confirmed by a suitably experienced surveyor. | 51/33669 - 3.7 | Survey Records | 5 working days prior to incorporating any piles into the permanent works. | D | SV
7.05.03 | CFA Pile Construction Record Card | Pile construction records shall be submitted to the Designer within 24 hours of completion of any particular pile. Copies of the records shall be retained on site and made available for inspection by the Designer as required. | 51/33669 - 7 | Pile Construction Record Card | Within 24 hours of completion of any particular pile | W | ENG
7.05.04 | Pile integrity testing (PIT) | PIT completed on each pile after the concrete has achieved 75% of it's design strength (75% of 25MPa = 18.75MPa). Preliminary PIT results to be submitted to Designer within 24 hrs of testing being done. Final report to be submitted within 10 days of completion of testing for Designer's review. | GHD-Piling Specs 2.1-3.7.2 & 8.1 | Test results | First 3 No. piles constructed and then 10 % of piles selected by the Designer, following receipt of the construction record cards. | HP | ENG