## General
SECTION 1 – GENERAL DETAILS
Project Name: | NZTA Weigh Right Programme SP1 Ohakea | [5 empty] | Inspection Key |  | Responsibilities
Project Number: | 558020 | [5 empty] | A | Action | Role Key |  | Name | Signature/ Initial
Customer: | Waka Kotahi | [5 empty] | B | Report by Breach | PM | Project Manager | Kerry Godfrey | KG
Contract Number: | 7456 | [5 empty] | C | Check | PE | Project Engineer | - | -
Area/ Sub-System: | ITS Ducting |  |  | Lot ID Number: |  |  | D | Dimension Inspection | SE | Site Engineer | - | -
[7 empty] | E | Examine | SE | Site Engineer | - | -
ITP Number: | 558020-DOW-ITP-PC-0024 Ducting (Open Trench) |  |  | Version: | 1 |  | H | Hold Point | SV | Surveyor (DNZ) | Stefan Kilian | SK
ITP Description: | Trenching and Installation ducts for power and comms on botht CVSC and Roadside sites | [5 empty] | I | Inspection | QM | QA Manager | - | -
Discipline: | Installation of service ducts (Open Trench) | [5 empty] | M | Monitor on Random Basis | ST | Superintendent | - | -
Specification: | ITS-01-10-202008-STD-DUCT (Waka Kotahi ITS Technical Specifications) | [5 empty] | O | Operation | QE | Quality Engineer | - | -
[7 empty] | R | Review | PS | Supervisor (DNZ) | Gavin Hosnell
Drawings: | 5C4353-WSP-05-DR-E-2001, 5C4353-WSP-05-DR-C-2510,2511,2512,2521,2522,2523 and 8104. | [5 empty] | S | Subcontractor | SCE | ITS Consulting Engineer | - | -
[7 empty] | V | Visual Verification | SCE/SE | DNZ Site Engineer | Ribin Jose | RJ
Prepared By: | Ribin Jose |  |  | Date: | 2024-04-18 |  | W | Witness Point | WS | Welding Supervisor | - | -
Quality Specified:
SECTION 2 – SIGNATURES – CLOSE-OUT & APPROVAL
ITP Close-Out by Downer |  | Name: | Ribin Jose |  |  | Signature: |  | #VALUE! |  |  | Date: | 2024-04-18
Downer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:
Customer Approval |  | Name: |  |  |  | Signature: |  |  |  |  | Date:

## Receiving Inspection
SECTION 3 – RECEIVING INSPECTIONS
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection |  | Inspection Point/Signature & Date
[7 empty] | Key | By | Signature | Date
3.1 | Design | Pre-construction | Ensure that you are working with the latest IFC drawings. | Drawings | Continously | Document review | H | SE
3.2 | Permits | Prior to Construction | Please ensure that the permit to work is the latest and approved, and that Existing Services have been positively identified. | Permit Register | Prior to works. | Document review | H | SE
3.3 | The survey set out of ducting alignment. | Prior to Construction | Consistent with the IFC construction drawings. Note: All positions to be confirmed on site prior to construction If trenching needs to intersect or traverse existing services, appropriate temporary protection must be implemented. | Survey set out records | Continuous | Document review | H | SV
3.4 | Marking out of existing services. Confirm there are no clashes with design and existing services | Prior to Construction | Consistent with the IFC construction drawings. | Photos | Continuous | Document review | R | SV
3.5 | Material Compliance - 50mm or 100mm or 150mm uPVC Ducts | Prior to Construction | Ducts shall comply with AS/NZS 61386:2015 or AS/NZS 2053.2:2001. Orange for Power & Salmon for Fibre, green for telecom. Also required print marking details of the configuration | Product Technical Datasheet, Delivery Dockets | Prior to work starting on site and upond delivery to site. | Visual, Document Review | H | SE
3.6 | Warning Tape | Prior to construction. | Consistent with the ICF drawings | Photos | Prior to work starting on site | Visual, Document Review | V, R | PS
3.7 | Incoming Material Inspection for all products and good delivered onto the project site | Material Delivery | Material inspected apon arrival for defects, material handling and storage is suitable and follows manufactures guidelines. | DN-QUA-QC-10 | Prior to works. | Visual, Document Review | R, V | PS

## In Process Inspections
SECTION 4 – IN-PROCESS INSPECTIONS
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection |  | Inspection Point/Signature & Date
[7 empty] | Key | By | Signature | Date
4.1 | Trench works
4.1.1 | Ensure all sevice in conflict with placement of ducting area exposed | Potholing | All existing services have been identified and confirmed. If trenching needs to intersect or traverse existing services, appropriate temporary protection must be implemented. | Visual inspection and documented. | Prior to the works starting | Visual | V | PS
4.1.2 | Excavations | During construction | Alignment and elevation consistent with the IFC drawings. Where excavation depth exceeds 1.5m the trench shields will be used if the excavations exceed 1.5 meters in depth to Work Safe NZ requirements, All works will be undertaken using hydraulic excavators operated by a competent operator, and all waste material will be removed from the site, and taken to a clean fill site | Photo Records. | Continuous | Visual Inspections, Measure | V, M | SE
5.1 | ITS Ducts Installation
5.1.1 | Placement of Bedding Material | During construction | 100mm thick or as shown in the IFC drawings | Delievry Dockets, Photos | Continuous | Visual Inspections, Measure | V, M | PS
5.1.2 | Laying Ducts for Power and Fibre | During construction | As shown in the IFC drawings. | Photos | Continuous | Visual Inspections, | V | SE
5.1.3 | Clearances | During construction | Check with the as-built data if any services coming close then work to the standard clearance to each services as detailed in project spec | As-built | Continuous | Visual Inspection and verification | V, M | SE
5.1.4 | Placement of Sand Surround Material | During construction | Dimensions as shown in the IFC drawings | Ducting Installation Checksheet, Photos | Continuous | Visual Inspections, Measure | V, M | SE
5.1.5 | As Built Survey of the laid ducts | During construction | Consistent with Issued For Construction drawings | As Built Survey Records | After ducts and chambers are installed | Survey | C | SV
5.1.6 | Backfill ducts with Sand Material or approved material. | During construction | Consistent with Issued For Construction drawings | Photos, Delivery Dockets | After ducts are installed | Visual Inspections, Measure | V, M | SE

## Final Inspection and Handover
SECTION 5 – FINAL INSPECTION AND HANDOVER
Item No. | Activity/ Task Description | Inspection Point: Quality Control Activity | Acceptance Criteria | Verifying Document | Frequency | Inspection Type | Inspection |  | Inspection Point/Signature & Date
[7 empty] | Key | By | Downer Signature | Date | Customer Requirements Verification Records/Location
7.1 | NCR/Defect/RFI Closed out | Upon completion of works | Construction within a tolerance of drawings & specifications | Closed-out NCR/Defects | Review | Review | I/R | SE |  |  | M-DNZ
7.1.1 | As-built Survey | Upon completion of works | Comply with the project specification and drawings | As built survey record completed | Review | Review | R | SE |  |  | M
7.1.2 | Red-line As-built Drawings | Upon completion of works | Consistent with the IFC drawings. | Signed As-built Drawings | Action | Review | R | SE/SV |  |  | ?
7.1.3 | PS3 & Warranties Completed | Upon completion of works | Contractual requirement | PS3 & Warranty | Review | Review | R | PE |  |  | DNZ
7.1.4 | All QA documentation collated & signed-off | Upon completion of works | All signed and closed out | Signed off Documents | Final Internal Review | Review | R | QM |  |  | M-DNZ
SECTION 6 – COMMENTS
|  |  | Customer Release Granted: | ☐ Yes | ☐ No | Date:
Certificate Number: