## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C | itp |  |  |  |  | INF-HSEQ CC0398-ITP-037 Earthing Installation Rev C
section | 1.0 Pre-start activities
checkpoint | 1.1 - Set out
label | Ref docs - Composite Drawings
label | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
label | ○ IFC and latest available revision used?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - W
checkpoint | 1.2 - IFC Submission & Approval
label | Ref docs - Composite Drawings
label | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Permits
label | Ref docs - Symal Safety Procedure
label | Acceptance criteria - Have the below permits been created.
label | – GPP
label | – Working at Heights
label | – Hot Works
label | – Confined Space
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - W
checkpoint | 1.4 - Determine Lot Size
label | Acceptance criteria - What is the lot size?
button | Acceptance | Yes,No,N/A
label | Key - S
label | VIVA - W
checkpoint | 1.5 - Materials
label | Acceptance criteria - Have the provided materials been accepted, and checklist completed?
label | ○ Have the materials and tag numbers/heat numbers been verified?
button | Acceptance | Yes,No,N/A
label | Key - W
label | VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Inspection Checklist
checkpoint | 1.6 - Electrical and Earthing Pre- Qualification
label | Ref docs - Welder Qualifications and tickets. This ITP.
label | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Calibration Certificates
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Bedding and Backfill Materials Approval
label | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Approval
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Excavation and Bedding
checkpoint | 2.1 - Service Location
label | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
label | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - S
checkpoint | 2.2 - Excavation
label | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
label | Acceptance criteria - Trench depth into buried ground 500mm width to provide sufficient width for earthing to reach design depth.
label | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - W
label | VIVA - S
section | 3.0 Laying/Welding/Handover
checkpoint | 3.1 - Earthing Installation
label | Ref docs - Viva Energy Earth Grid Connection Checklist (001) - ITP
label | Acceptance criteria - Have works been undertaken as per the subcontractor’s checklist?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - W
checkpoint | 3.2 - VIVA electrical inspection
label | Ref docs - New Item
label | Acceptance criteria - Has the electrical inspector from VIVA been notified to attend the project site and review the installed earthing?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - W
checkpoint | 3.3 - Earthing Network
label | Ref docs - 239529-CO-FM-00003 – Electrical Earthing by Area
bool | Has earth Grid installed at correct depth of cover?
bool | Have earth rods/connections/ferrules are of the correct type, length and material and located as per the approved drawing?
bool | Has the cleanness and secureness of all earth rods/connections/ferrules been checked?
bool | Are all identification labels being correctly fixed and visible?
bool | Are all cable clamps are secured correctly, coated with anti-corrosive coating?
bool | Are all cables of the correct size and type?
bool | Are all exothermic welds being acceptable?
bool | Has the individual earth path / bar resistance been recorded?
bool | Has the overall grid earth path resistance been recorded?
bool | Has the anti-corrosion material been applied?
bool | Have 3.0m tails been extended as per the project requirements
button | Acceptance | Yes,No,N/A
label | Key - W
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Earth Grid Connection Checklist (Rev 1)
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Electrical Earthing by Area
label | Ref docs - 235929-CO-FC-000034 – Electrical Earthing by Area VIVA Energy Earth Grid Connection Checklist
label | Acceptance criteria - Has the equipment earthing in area earthed via earth bosses or studs been installed as approved installation drawings and specification?
label | ○ Have all earth bosses and studs been tightly fitted with shake proof washers and coated with project specified protection?
label | ○ Are all earthing conductors correct type and size not less than minimum size specified in approved installation drawings?
label | ○ Are all earthing conductors properly installed and protected?
label | ○ Has earth resistivity testing been completed?
label | Structure Steelwork Earthing:
label | ○ Has all structural steelwork that is bolted and provided with equipment earth bonding connected to the main earthing system where required?
label | ○ Have all earth Bosses/Earth Points been cleared paint /rust free prior to connection?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Testing Checklist
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Backfill
label | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
label | Acceptance criteria - Has backfill been completed to provide a compact and even surface?
label | ○ Has testing been completed prior to backfill?
label | ○ Has all third party inspections been completed prior to backfilling?
button | Acceptance | Yes,No,N/A
label | Key - S
label | VIVA - W
checkpoint | 3.6 - Clean-up of site
label | Ref docs - 235929-000-CV-SP-00002 EARTHWORKS
label | Acceptance criteria - Have the areas affected by the works been restored to a condition similar to that which existed prior to the commencement of the work?
button | Acceptance | Yes,No,N/A
label | Key - S
label | VIVA - S
checkpoint | 3.7 - Identification and recording
label | Acceptance criteria - Have the actual installed location and depth of the earthing, and location of pits, been accurately recorded on an as built?
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As built
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - Work is complete and complies with design plans / drawings / specs
label | Acceptance criteria - Redline mark-ups As-Built Survey: Earthing to conform to the required depths and locations.
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | As built
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.9 - Certificate of electrical safety
label | Acceptance criteria - Electrician to supply Certificate of electrical safety for earthing installation
button | Acceptance | Yes,No,N/A
label | Key - H
label | VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) - Certificate of electrical safety
holdpoint | AUTHORITY HOLDPOINT
checklist | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C | itp |  |  |  |  | INF-HSEQ CC0398-ITP-034 Carbon Steel Installation Rev C
section | 1.0 Pre-start activities
checkpoint | 1.1 - Set out
label | Acceptance criteria - Is the position of the pipe in accordance with the drawings?
label | ○ IFC and latest available revision used?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
checkpoint | 1.2 - IFC Submission & Approval
label | Ref docs - Isometric Drawings
label | Acceptance criteria - Is IFC Construction Drawing and Most Current Revision Approved by the client?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Isometric Drawings
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.3 - Permits
label | Ref docs - Symal Safety Procedure
label | Acceptance criteria - Have the below permits been created.
label | – GPP
label | – Working at Heights
label | – Hot Works
label | – Confined Space
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
checkpoint | 1.4 - Determine Lot Size
label | Acceptance criteria - What is the lot size?
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - W
checkpoint | 1.5 - Free Issue Materials
label | Acceptance criteria - Have the free issue materials been accepted and checklist completed?
label | ○ Have the materials and tag numbers/heat numbers been verified?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Inspection Checklist
checkpoint | 1.6 - Pre-Qualifications
label | Ref docs - Welder Qualifications and tickets. This ITP.
label | Acceptance criteria - Welding procedures, equipment to be used, welding qualifications and calibration of welding machines to be submitted and approved by the client, has this been completed?
label | ○ Has the training records for the STOPAQ applicators been provided?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Welding Qualificaitons
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 1.7 - Bedding and Backfill Materials Approval
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
label | Acceptance criteria - Has bedding and backfill materials been approved for use?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Material Approval
holdpoint | AUTHORITY HOLDPOINT
section | 2.0 Excavation and bedding
checkpoint | 2.1 - Service Location
label | Ref docs - DBYD & Services marked on current IFC drawings (if applicable)
label | Acceptance criteria - Current DBYD documents received and works executed by qualified service locator
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - S
checkpoint | 2.2 - Excavation
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.12
label | Acceptance criteria - Excavation shall be to depth adequate to provide full specified bedding depth of 100mm.
label | ○ Minimum trench width as per manufacture specifications pg. 17 is 1.25 x OD + 300mm.
label | ○ Earthworks for trenches shall be done in accordance with standard drawing, has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
checkpoint | 2.3 - Bedding material
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.1.8
label | Acceptance criteria - Has the bedding material been installed as per the manufacturer’s specification?
label | ○ Conforms IFC drawing (if applicable)? Bedding depth minimum 100mm Overlay depth minimum 300mm.
button | Acceptance | Yes,No,N/A
label | Key - S
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Delivery Dockets
section | 3.0 Fabrication
checkpoint | 3.1 - Welding
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P RE-ENG-INT- 0072-PR
label | Acceptance criteria - Have the lengths been welded as per the manufacturers spec and welding duration?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Carbon Steel Subcontractors ITP
bool | Welding Log
checkpoint | 3.2 - Non-Destructive Testing
label | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE-ENG-INT-0003-WIITP – P11P
label | Acceptance criteria - Have the welds been tested as per the ITP’s referenced in the isometric drawings?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Carbon Steel Subcontractors ITP
checkpoint | 3.3 - Coating and wrapping
label | Ref docs - 235929-RE-ENG-INT-0003-WI, 235929-RE-ENG-INT-0003-WIITP – P11U, 235929-RE- ENG-INT-0003-WITP – P11P, Isometric Drawings, RE-ENG-INT-0045-PR
label | Acceptance criteria - Has the application procedure been provided to MDR and approved?
label | ○ Have the welds been wrapped as per the drawings and specification?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Carbon Steel Subcontractors ITP
section | 4.0 Laying
checkpoint | 4.1 - Lifting into trench
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL Section 12.2.1 Item 12.2.7
label | Acceptance criteria - Before lowering in, caps shall be placed on open ends, flanges, etc., which shall remain in place until piping connection can be made. Particular attention shall be given to the need to protect pipes from damage due to loads from heavy plant, has this been completed?
label | ○ Have pipes been laid to true line and level?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - S
checkpoint | 4.2 - Haunching
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
label | Acceptance criteria - Has the backfill material been haunched appropriately around the pipe?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
checkpoint | 4.3 - Pressure Testing
label | Ref docs - 235929-000-CV-SP-00006 Section 13.4
label | Acceptance criteria - Is Air Testing or Hydrostating testing being completed?
bool | Air Testing
bool | Hydrostatic Testing
textbox | What is the test pressure?
label | ○ Has Testing been conducted to all joints and inspected to confirm no leaks?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Testing checklist
checkpoint | 4.4 - Backfill Materials
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
label | Acceptance criteria - Has Sand Back fill been placed to 300mm above Pipe?
label | ○ No compaction equipment to be used until 300mm above pipe.
label | ○ Has select backfill been placed in layers not exceeding 150mm loose thickness?
label | ○ No compaction equipment has been used between 0-300mm above top of pipe, light compaction equipment has only been used from 300-600mm. above pipe.
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
checkpoint | 4.5 - Backfill and Compaction
label | Ref docs - 235929-000-CV-SP-00006 UG PIPE FAB and INSTALL
label | Acceptance criteria - Sand Fill - not less than 90% of maximum density or 70% of relative density, except that under paved areas the entire depth shall be compacted in 150mm layers to not less than 95% of maximum density or 80% relative density.
label | ○ Select Fill - Backfill under pavements shall be compacted to a dry density ratio of no less than 98% modified comp active effort.
label | ○ Backfill to be in 250mm compacted layers.
label | ○ Testing Frequency: Minimum 2 field density tests for each 185 m2 of each compacted fill layer, but no less than 3 tests for total area
label | ○ Has compaction testing been completed as per the project specifications?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - S
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Compaction Testing Results
section | 5.0 Testing and Conformance Check
checkpoint | 5.1 - Test Pack
label | Acceptance criteria - Has a test pack been provided?
label | ○ Test pack to include.
label | – Test Procedure
label | – Test Map
label | – Equipment Calibration
label | – Equipment Details
label | – Exclusion zones if require
label | ○ Provision of testing log template
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Testing Log
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Survey
label | Acceptance criteria - Tolerances in alignments shall be limited to +/- 25 mm vertically or horizontally, unless otherwise specified on engineering drawing, has this been completed?
button | Acceptance | Yes,No,N/A
label | Key - W
label | MDR/VIVA - W
label | Remarks / record (eg. test frequency, reports, certificates, checklist etc) -
bool | Survey as-built
checkpoint | 5.3 - Quality Submission
label | Acceptance criteria - Have all QA documents in-line with the specification been provided to MDR for review?
button | Acceptance | Yes,No,N/A
label | Key - H
label | MDR/VIVA - H
holdpoint | AUTHORITY HOLDPOINT