## F-S Rev02
CIVIL INSPECTION & TEST PLAN
T039 - T04/09 FOAM PROPORTIONER AREA FOAM FOUNDATION BUND |  |  |  |  | Rev: | Originator | Date | Approved | Date
[5 empty] | 0 | Cameron Hinge | 2024-05-15
| H - HOLD |  | CR - Contractor Representative |  | 1
| P - PERFORM |  | CTS - Channel Representative Signoff
| W - WITNESS |  | CTS CI - Channel Civil Inspector
R - REVIEW
ITEM | TASK | SPECIFICATION REFERENCE | ACCEPTANCE CRITERIA | DATE/SIGN |  |  | COMMENTS
1 | Issued For Construction Drawings | IFC Drawings Issued by Client/Engineer | Issued For Construction Drawings Available | Contractor Rep - H
2 | Survey & Setout | IFC Drawings CTS General Civil Construction Spec CTS Excavation Works Spec | Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing. | Contractor Rep - P
3 | Waste Management & Disposal | CTS General Civil Construction Spec CTS Excavation Works Spec CTS Contaminated Environmental Ground Soil Managenet Plan RW-231 | Waste management plan prepared and followed. Supporting documents available on request | Contractor Rep - P CTS Civil Inspector - R
4 | Trim Subgrade | Underground Services Drawings CTS Excavation Permit CTS Excavation Works Spec CTS General Civil Construction Specification | Subgrade to be trimmed within -250mm of the Finished Site Concrete level and to the levels stated on the drawings | Contractor Rep - P CTS Civil Inspector - H
5 | Backfill/Subgrade Compaction | IFC Drawings CTS General Civil Construction Specification Clegg Compaction Inspection Record | Foundation subbase shall consist of 200mm of Gap65 Blue-Brown Rock hardfill material. Subbase compaction shall be tested using a clegg hammer, all readings to exceed a CIV of 24 with 90% of tests to exceed 30. | Contractor Rep - P CTS Civil Inspector - H
6 | Site Concrete | IFC Drawings CTS General Civil Construction Specification Inspection Records Delivery Dockets | Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm | Contractor Rep - P CTS Civil Inspector - R
7 | Reinforcing | IFC Drawings CTS General Civil Construction Specification NZS3109 Manufacturers Documentation Inspection Records | All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing shall be tied and laid out to comply with the IFC drawings | Contractor Rep - P CTS Civil Inspector - H
8 | Cast in Items - Nuts, Bolts and Studs | IFC Drawings CTS General Civil Construction Specification CTS Epoxy Grouting of Anchor Bolts Manufacturers Documentation Inspection Records | Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings Drilled holes for Anchors shall be inspected by Civil Inspector | Contractor Rep - P CTS Civil Inspector - H
9 | Formwork | IFC Drawings CTS General Civil Construction Specification NZS3109 Inspection Records | Fillets to corners above ground as noted on IFC drawings. Tolerances for Insitu formwork shall be +/-20mm dimensionally, and +/-12mm level Minimum cover shall be 50mm unless cast against the ground which shall be 75mm unless noted otherwise. | Contractor Rep - P CTS Civil Inspector - W
10 | Grouting | IFC Drawings CTS General Civil Construction Specification Manufacturers Specification Inspection Records | Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings | Contractor Rep - P CTS Civil Inspector - W
11 | Concrete | IFC Drawings CTS General Civil Construction Specification NZS3112/NZS3109 Inspection Records Delivery Dockets | Concrete shall be 30MPa 28 day compressive strength Slump Tests - one for every pour Crush Tests taken per pour as per NZS3109 & CTS General Civil Specification | Contractor Rep - P CTS Civil Inspector - H
12 | Complete final Civil Inspection and close off ITP | IFC Drawings CTS General Civil Construction Specification Manufacturers Specification | ITP/QC has been completed; all steps & hold points signed byrelevant party. All work completed as per work pack, and any field instructions issued during construction compiled | Contractor Rep - P CTS Civil Inspector - R
13 | Non-Conformance Reporting | UCC Internal NCR and or Lucidity event NCR QC Requirements for Civil Works | All Non-Conformance reports and Investigations are attached and closed out | Contractor Rep - H
14 | As Built & Final Design Documentation |  | Confirmation From Engineer on as built records & redline mark ups | Contractor Rep - P
15 | Reference Info, Specifications |  | Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
16 | Punch Listing | CTS QC Requirments for Civil Work | All punch list items are closed out in the relevant timeframe to the required standard | Contractor Rep - P CTS Civil Inspector - R
17 | Compilation of ITP |  | ITP Completed and Signed off | Contractor Rep - H CTS Civil Inspector - H