## res_ITP_1_Inspection_and_Test_P
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | T039 Foam Proportioner Civil ITP | itp |  |  |  |  | T039 Foam Proportioner Civil ITP
section | Details
checkpoint | 1 - Issued For Construction Drawings
label | SPECIFICATION REFERENCE - IFC Drawings Issued by Client/Engineer
label | ACCEPTANCE CRITERIA - Issued For Construction Drawings Available
label | DATE/SIGN - Contractor Rep - H
holdpoint | HOLD POINT
checkpoint | 2 - Survey & Setout
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Spec, CTS Excavation Works Spec
label | ACCEPTANCE CRITERIA - Foundations and embedded items shall be setout following the tolerances, heights and positions shown in each foundations respective drawing.
label | DATE/SIGN - Contractor Rep - P
checkpoint | 3 - Waste Management & Disposal
label | SPECIFICATION REFERENCE - CTS General Civil Construction Spec, CTS Excavation Works Spec, CTS Contaminated Environmental Ground Soil Managenet Plan RW-231
label | ACCEPTANCE CRITERIA - Waste management plan prepared and followed. Supporting documents available on request.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - R
checkpoint | 4 - Trim Subgrade
label | SPECIFICATION REFERENCE - Underground Services Drawings, CTS Excavation Permit, CTS Excavation Works Spec, CTS General Civil Construction Specification
label | ACCEPTANCE CRITERIA - Subgrade to be trimmed within -250mm of the Finished Site Concrete level and to the levels stated on the drawings
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 5 - Backfill/Subgrade Compaction
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification, Clegg Compaction Inspection Record
label | ACCEPTANCE CRITERIA - Foundation subbase shall consist of 200mm of Gap65 Blue-Brown Rock hardfill material. Subbase compaction shall be tested using a clegg hammer, all readings to exceed a CIV of 24 with 90% of tests to exceed 30.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 6 - Site Concrete
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification, Inspection Records, Delivery Dockets
label | ACCEPTANCE CRITERIA - Site concrete to be placed at the thicknesses shown on the drawings and finished to a height of +/- 10mm
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - R
checkpoint | 7 - Reinforcing
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification NZS3109, Manufacturers Documentation, Inspection Records
label | ACCEPTANCE CRITERIA - All reinforcing bars shall be Micro-Alloy Class E to AS/NZS 4671 as shown in IFC's. All reinforcing bar hooks, laps and bends shall be in accordance with NZS3109 unless otherwise noted. All reinforcing shall be tied and laid out to comply with the IFC drawings.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 8 - Cast in Items - Nuts, Bolts and Studs
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification, CTS Epoxy Grouting of Anchor Bolts, Manufacturers Documentation, Inspection Records
label | ACCEPTANCE CRITERIA - Epoxy Grout Shall be Ramset C8 placed in accordance with manufacturers recommendations to the levels and positions setout in the drawings. Drilled holes for Anchors shall be inspected by Civil Inspector.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 9 - Formwork
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification NZS3109, Inspection Records
label | ACCEPTANCE CRITERIA - Fillets to corners above ground as noted on IFC drawings. Tolerances for Insitu formwork shall be +/-20mm dimensionally, and +/-12mm level. Minimum cover shall be 50mm unless cast against the ground which shall be 75mm unless noted otherwise.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - W
holdpoint | HOLD POINT
checkpoint | 10 - Grouting
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification, Manufacturers Specification, Inspection Records
label | ACCEPTANCE CRITERIA - Grouting shall be Sika 212 or Sika 214 placed in accordance with manufacturers recommendations and the IFC drawings
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - W
holdpoint | HOLD POINT
checkpoint | 11 - Concrete
label | SPECIFICATION REFERENCE - IFC Drawings ,CTS General Civil Construction Specification NZS3112/NZS3109, Inspection Records, Delivery Dockets
label | ACCEPTANCE CRITERIA - Concrete shall be 30MPa 28 day compressive strength, Slump Tests - one for every pour, Crush Tests taken per pour as per NZS3109 & CTS General Civil Specification
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - H
holdpoint | HOLD POINT
checkpoint | 12 - Complete final Civil Inspection and close off ITP
label | SPECIFICATION REFERENCE - IFC Drawings, CTS General Civil Construction Specification, Manufacturers Specification
label | ACCEPTANCE CRITERIA - ITP/QC has been completed; all steps & hold points signed byrelevant party. All work completed as per work pack, and any field instructions issued during construction compiled.
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - R
checkpoint | 13 - Non-Conformance Reporting
label | SPECIFICATION REFERENCE - UCC Internal NCR and or Lucidity event NCR, QC Requirements for Civil Works
label | ACCEPTANCE CRITERIA - All Non-Conformance reports and Investigations are attached and closed out
label | DATE/SIGN - Contractor Rep - H
holdpoint | HOLD POINT
checkpoint | 14 - As Built & Final Design Documentation
label | ACCEPTANCE CRITERIA - Confirmation From Engineer on as built records & redline mark ups
label | DATE/SIGN - Contractor Rep - P
checkpoint | 15 - Reference Info, Specifications
label | ACCEPTANCE CRITERIA - Provided a completed construction defect report that that details any remedial measures taken, & snag lists closed out
checkpoint | 16 - Punch Listing
label | SPECIFICATION REFERENCE - CTS QC Requirments for Civil Work
label | ACCEPTANCE CRITERIA - All punch list items are closed out in the relevant timeframe to the required standard
label | DATE/SIGN - Contractor Rep - P, CTS Civil Inspector - R
checkpoint | 17 - Compilation of ITP
label | ACCEPTANCE CRITERIA - ITP Completed and Signed off
label | DATE/SIGN - Contractor Rep - H, CTS Civil Inspector - H
holdpoint | HOLD POINT