## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned | a906754c-d403-475f-ad3b-c70a140dc0bc |  | checklist | Low Voltage Cables (Mains/Submains) |  |  |  |  | Yes | Testing & Commissioning - Low Voltage Cables (Mains/Submains) | 0d8affbd-99c3-4d6f-94c8-1452c8e6105f
checkpoint-group | b418aaab-9b06-44b0-94e1-3ede97d477ce |  | section | WSA20-MPX-04000-EL-ITC-31052000 Construction Tests (Pre-energisation)
checkpoint-status | d188b021-c32b-41f7-87bb-11f766286f2e |  | checkpoint | Pre-requisite Works
checkpoint-status | 81489160-48f7-46d0-a24e-949ea95b267f |  | checkpoint | Insulation Damage
checkpoint-status | 3b51b38e-15d0-405b-bb07-6d92793c3096 |  | checkpoint | Correct Type of Termination
checkpoint-status | d745f718-f2d9-4418-9af8-482a8be6b609 |  | checkpoint | Correct Cable Size and Labelling
holdpoint | add92717-6d4d-42c9-a6fb-ee5a9a64abac |  | signoff | Checked By (Heyday):
checkpoint-no-status | d76b7d3e-7893-4898-abc4-7856524a63d9 |  | checkpoint | Insulation Resistance
checkpoint-status | 56eb7263-d352-4540-82b1-504626d33d1d |  | checkpoint | R-W
button | ffa14fb8-15fd-51d3-9959-4f7d19cde905 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 242417f9-5a72-5339-bb58-a99423be5f8b |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 5b556e62-d9b7-4870-83b4-50bcbfac5b7b |  | checkpoint | R-B
button | d264b0c7-b7b7-5cf2-b6bb-3b5c00524887 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 0c066d3c-ad99-5a06-acf6-19a238b6f102 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | b894838a-385c-40e9-8bec-73c371bac414 |  | checkpoint | W-B
button | a32e441a-079d-5043-a3bc-415f3864e642 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 40ad8e62-206b-5705-8b53-ce6ece09e0f8 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 0f550083-67ea-4967-83dc-d3339a498887 |  | checkpoint | R-N
button | a39f5898-cb63-5d41-a52f-5373c95efa9d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | da8fc1d5-493b-538b-8d0e-e94a4bdaa36e |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 1ca94486-039c-4892-b3cf-8b780e2b858b |  | checkpoint | W-N
button | b731a9ca-d585-5762-b127-5a2ed792318a |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 76375cf2-58cd-5a2c-a86c-3a8f4bc01d66 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 55fb3f15-268b-4b3d-be21-064d7b8bec24 |  | checkpoint | B-N
button | 1ef2a404-1241-5090-bd5f-a20e3b80ed3d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | b98d8928-132f-5007-acd0-fd77fd7d66e6 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 19d841c7-986a-4238-b259-17523fb3bb5f |  | checkpoint | R-E
button | 24e3b97c-0376-56ee-ab9d-492b702ecd5f |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | cbb384d6-87cc-5bd0-80c9-5cd5ec350f34 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 35f93450-7f45-4b73-9c65-e31af3dbe3de |  | checkpoint | W-E
button | 214f0871-62cd-5860-a5ec-4d96a351d1e7 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 044f765f-8df4-5d3e-9f4c-7e54ac782b40 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 46bac21d-9f13-4a6d-8a04-6d46873a27d0 |  | checkpoint | B-E
button | 5291d96c-05bc-5957-b448-f1e5a03bc9db |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 3062c198-f593-5c2b-843f-b8abef93aced |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 006f4405-0150-4aac-86ae-fa57737e7f32 |  | checkpoint | N-E
button | 0058342c-260a-5ef7-9873-946cd8aa6e80 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
text | 9695a55b-bc10-527e-bfc7-bc4b29254b29 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
holdpoint | 0cbd4359-3351-4abc-abb2-88817f7234e2 |  | signoff | Checked By (Heyday):
checkpoint-no-status | 69e479e3-25e8-4b7d-ae31-c19a2b1f1683 |  | checkpoint | Continuity Testing
checkpoint-status | 14b261e0-1977-4da5-a31a-8f1226ba7306 |  | checkpoint | Red Phase
text | 1daee8fc-c745-5e9f-bab2-360139c10f57 |  | textbox | Resistance (Ω)
text | c761c802-992a-5093-9e69-1a799880a4ef |  | textbox | Target Resistance (Ω)
checkpoint-status | a16308e0-bc73-4098-a838-b7578c171046 |  | checkpoint | White Phase
text | 7ac1f684-4f70-58b9-99b1-4ee70b94823e |  | textbox | Resistance (Ω)
text | 057a6a73-b8d3-575a-8851-bcc2fd7532b1 |  | textbox | Target Resistance (Ω)
checkpoint-status | b31431ac-ddb0-4902-b913-4e5629a26318 |  | checkpoint | Blue Phase
text | f5b1e39e-3fe7-562c-80a6-86c9c4053244 |  | textbox | Resistance (Ω)
text | 08dfa819-d9a2-5b7d-a54d-d64641fe62ca |  | textbox | Target Resistance (Ω)
checkpoint-status | 2626f720-b759-48cc-b13a-655b28d109e3 |  | checkpoint | Neutral
text | 1e3b691f-5fec-538c-9b80-691e6cf151ef |  | textbox | Resistance (Ω)
text | 394687c1-f09d-5872-abcb-eb9386c50309 |  | textbox | Target Resistance (Ω)
checkpoint-status | 48d0ec5e-d841-4f36-8bd6-7ba123ce2bd4 |  | checkpoint | Earth
text | d447ed02-2ed7-577b-a490-c9b653ca4175 |  | textbox | Resistance (Ω)
text | 3e11c70b-d516-52bc-b417-39a4e2b3ca8f |  | textbox | Target Resistance (Ω)
holdpoint | db751fa8-560a-4f0b-ab49-64a991b9aca7 |  | signoff | Checked By (Heyday):
checkpoint-group | 3d441328-ff3d-4850-9693-19a85fa9c3fe |  | section | WSA20-MPX-04000-EL-ITC-31053000 Component (Energised)
checkpoint-no-status | 77fc7e3f-a00d-4e51-856b-ff185d4f06fa |  | checkpoint | Phase Rotation
button | 8ffdb850-aed3-5361-a6a8-5313f2b948ef |  | button | Direction | Clockwise,Anti-Clockwise
holdpoint | e126b328-38f6-42d6-9218-6e1cd2d45b2e |  | signoff | Checked By (Heyday):
checkpoint-no-status | af343016-3efe-4d7a-a4ae-ed3e650a7add |  | checkpoint | Voltage
checkpoint-status | 1ab20a6f-41d1-4fb4-abef-9f9e77bff94a |  | checkpoint | Red - White
text | a3188b29-a1c9-563d-a1c6-40ae982fca5a |  | textbox | Voltage (V)
checkpoint-status | 77c308c5-7443-40cd-b1c3-e691ea6f7e3a |  | checkpoint | Red - Blue
text | 087bfc0f-94ac-52b8-876b-9aedf3296b15 |  | textbox | Voltage (V)
checkpoint-status | 2384e992-b276-4ebb-847a-e56f7367de81 |  | checkpoint | White - Blue
text | 13994845-428f-544a-9577-7317f84f3a4d |  | textbox | Voltage (V)
checkpoint-status | b51e7cb2-4cf8-4edf-831c-d56ca03649dd |  | checkpoint | Red - Neutral
text | 7b8ec0c2-8698-51c4-bad0-630a1daf392e |  | textbox | Voltage (V)
checkpoint-status | 3c14003b-2c46-4bf4-b41c-d33d24eb1f36 |  | checkpoint | White - Neutral
text | 11339380-881a-5e02-a87f-f0749e268f6e |  | textbox | Voltage (V)
checkpoint-status | fa91cc59-fd27-44f4-90a8-d6816bf0b33d |  | checkpoint | Blue - Neutral
text | 9efc517a-8f9e-579a-8113-9446da70c6fb |  | textbox | Voltage (V)
checkpoint-status | 0703d3fd-5af2-4732-b261-3d3ed41c126b |  | checkpoint | Red - Earth
text | 231229c4-d448-5b42-90e9-9c8e3d4274c6 |  | textbox | Voltage (V)
checkpoint-status | b6908b13-b575-47d7-94a0-5f69900ee350 |  | checkpoint | White - Earth
text | 12d987c2-e738-5d10-9e6d-d60a60fc0c2d |  | textbox | Voltage (V)
checkpoint-status | 7755019a-58ab-4d7b-939c-577677253e59 |  | checkpoint | Blue - Earth
text | c30baabc-8880-5c44-8d99-29366cbceaa8 |  | textbox | Voltage (V)
holdpoint | 744591f0-83c0-42bd-8996-f7a302ecc020 |  | signoff | Checked By (Heyday):
checklist-flat | 0768c84e-b3bd-4c6a-aa09-13255ac65d50 |  | checklist | Quality - Busduct |  |  |  |  | Yes | Quality - Busduct | 13283b53-81eb-4481-9b2c-545c88c8c388
checkpoint-status | b5e3fe26-c783-40f9-bcd4-eaf2b88586e1 |  | checkpoint | Receipt of busduct/ busway & take off box's delivery to site
checkpoint-status | a3ff3953-176a-4f1f-aa7e-1986d652eda6 |  | checkpoint | Set out - Ensure correct size, type and spare capacity
checkpoint-status | d6a046bc-7068-4c9b-9b6c-f8328e22b064 |  | checkpoint | Accessories to be factory made items
checkpoint-status | 65db417e-1f27-4f5e-819c-78b92e4a29e3 |  | checkpoint | Hangers installed as per the drawings
checkpoint-status | 299dea92-5f16-4433-a952-cfa942e266da |  | checkpoint | IR Test of Busduct - Separate - Test Result Above 1M Ω
checkpoint-status | 8454a122-48a5-4d58-aebe-c3d8bdefcfe4 |  | checkpoint | Busduct Piece are installed safely
checkpoint-status | c87d056a-92e3-4209-8b5a-28c6bf6d1ea5 |  | checkpoint | Busduct Torqued to 95Nm
checkpoint-status | 29e3b00e-cad7-45d1-917f-5c5cf497b715 |  | checkpoint | IR Test of Busduct - Joined - Test Result Above 1M Ω
checkpoint-status | ac33c530-7829-4181-9de4-04f2f3f3f53c |  | checkpoint | Photos attached of installed piece
checklist-sectioned | ff0e237c-dd3c-4bd6-9493-b3cb341861c7 |  | checklist | Load Bank |  |  |  |  | Yes | Testing & Commissioning - Load Bank | 18ed8d7e-e6cc-4136-906f-92a9054859b7
checkpoint-group | 536dda0e-5101-4baf-9bdf-b0735aff5fb9 |  | section | WSA20-MPX-04000-EL-ITC-31143000 - Component Tests (Pre-commissioning)
checkpoint-status | 7bdbd1de-9025-4189-85e4-2fcb1213e2e6 |  | checkpoint | Sephco Commissioning Checklist
holdpoint | f3d07a75-f318-4c18-bc0e-9b2acceba9c5 |  | signoff | Checked By (Heyday):
checklist-sectioned | d86ba766-a2ac-445a-b7a9-7d0e2f12bb35 |  | checklist | UPS |  |  |  |  | Yes | Testing & Commissioning - UPS | 3b4005fe-9e4d-4e40-a511-ef716e632651
checkpoint-group | d3d6ba6a-6b8c-4492-9690-03c810dfa4b0 |  | section | WSA20-MPX-04000-EL-ITC-31122000 - Construction Tests (Pre-energisation)
checkpoint-status | 42e8ea44-f3cf-4f88-954d-00450a59d395 |  | checkpoint | Commissioning & Installation / Start-up Report - System Room Check – Page 6
checkpoint-status | dde1f0c2-dc76-4937-b9a6-7fb5f2101ebd |  | checkpoint | Commissioning & Installation / Start-up Report - System Check – Page 6.
checkpoint-group | 2c1feebb-a9fc-49b6-91d4-2a605afece55 |  | section | WSA20-MPX-04000-EL-ITC-31123000 - Component Tests (Pre-commissioning)
checkpoint-status | b08d9a29-d782-496e-8c2f-4e2b1b99a2de |  | checkpoint | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
checkpoint-status | 0dc8eb32-4da7-4b1f-b5e3-099a681fb966 |  | checkpoint | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
checkpoint-status | 8ac63ca9-65a0-4386-a608-cb3a7952bc82 |  | checkpoint | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
checkpoint-group | 40d17bd8-4ff6-4810-9439-a5ec90111643 |  | section | WSA20-MPX-04000-EL-ITC-31124000 - System Commissioning
checkpoint-status | 040a6af9-bec2-4cd4-bf7a-deeead920f52 |  | checkpoint | UPS – Functional Performance Test Report
label | cdfe68bd-0803-5136-8892-2e46fd041f09 |  | note | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends): • Load Transfer test • Inverter to bypass transition on NO LOAD • Inverter to bypass transition on FULL LOAD • Load step test (0%-50%-0%) • Load step test (25%-75%-25%) • Load step test (50%-100%-50%) • Load step test (75%-100%-75%) • Load step test (0%-100%-0%) • THDi and THDv measurements (0%, 25%, 50%,75%, 100%) • Expected Results: Total Harmonic Distortion (THD) is to be under 5% • UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%) • UPS battery discharge test (15min EOL)
holdpoint | 9a7ae548-5791-415a-9af5-a28ed0a46ed3 |  | signoff | Checked By (Heyday):
checklist-sectioned | 3d7ba9fd-634e-42ee-ba96-a6a45f561ace |  | checklist | Earthing Systems |  |  |  |  | Yes | Testing & Commissioning - Earthing Systems | 3c5544ac-27fc-4dd8-bd06-3b8b0c07d0b0
checkpoint-group | 9d137dec-f76f-411c-9bdb-8d10cf725ddc |  | section | WSA20-MPX-04000-EL-ITC-31092000a - Construction Tests (Main Earth System)
checkpoint-status | e7aacbe3-eba3-4257-8091-3b0048fd8e71 |  | checkpoint | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
checkpoint-status | 8b11df9f-d8ce-43c3-9555-9082e3d1271e |  | checkpoint | RWV Industries – Earthing Test Report. Footing Earthing
checkpoint-group | 212013d4-08f9-4781-93a9-9b5499d61ba4 |  | section | WSA20-MPX-04000-EL-ITC-31092000b – Construction Test (Earth System Reticulation)
checkpoint-status | af04e8f3-e900-48a0-aa5d-104d325a64ba |  | checkpoint | Correct Cable Size and Labelling
checkpoint-status | 55b2e75a-7919-4a28-a697-f8d82da92b53 |  | checkpoint | Earth Continuity
text | cf58112c-1ecb-534b-bdc3-173b7a2d78e8 |  | textbox | Resistance (Ω)
text | e93a1bb8-5dcc-5756-b8b1-381a9987ec9d |  | textbox | Target Resistance (Ω)
holdpoint | a1101b52-19ab-4df7-a50d-b33f10af9ba3 |  | signoff | Checked By (Heyday):
checklist-flat | c4fab001-6d7f-4e61-9514-e45467024253 |  | checklist | Communications Cabling |  |  |  |  | Yes | Testing & Commissioning - Communications Cabling | 49d31490-7e0b-4329-bd56-0e4e047099b0
checkpoint-status | 55d94b5c-3689-4cb2-8f73-9160690a51be |  | checkpoint | Cable installed to Manufacturers requirements
checkpoint-status | f4a63d89-7085-4de9-a646-9ff3b5e2c2b7 |  | checkpoint | Cable Labelled
checkpoint-status | 57b1b891-a26a-4284-b199-006ddec485d7 |  | checkpoint | Cable Terminated
checkpoint-status | 0b118d6f-2240-4905-9767-72c4a3c64569 |  | checkpoint | Cable Tested
checkpoint-status | 61d91b88-697a-4bdc-a7a3-1d7e495d395f |  | checkpoint | As-Builts reflects installed Cable Number and Location
holdpoint | 86dbe344-1f18-4c57-9799-284e4f4985ac |  | signoff | Checked By (Heyday):
checklist-flat | 942ddc73-90e7-4113-b188-d0d2bd40f2b6 |  | checklist | Quality - Earthing & Lightning protection |  |  |  |  | Yes | Quality - Earthing & Lightning protection | 571d8303-108f-4b8e-8d23-7d9bf309ab8f
checkpoint-status | 1479e842-cca4-487c-ab4e-fbc4bbd640de |  | checkpoint | Receipt of Cable & test point delivery to site
checkpoint-status | 39de632f-40ed-467a-b184-4cb1d361cc72 |  | checkpoint | Correct cable size and Cable type installed per the shop drawing
checkpoint-status | 949d0a9c-6e76-4913-a8b1-243717cdd555 |  | checkpoint | Installed and Terminated to final locations
holdpoint | 6d5b64a1-3d75-444a-b7b6-bd7a5fc618ad |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 232b8310-ad90-42ac-8360-ffb23fe6a001 |  | checkpoint | Photos of test piont and bonds attached
checklist-flat | 8d60bbbe-1ea3-4ffc-acc6-cc9659a95a68 |  | checklist | Emergency Lighting |  |  |  |  | Yes | Testing & Commissioning - Emergency Lighting | 5c2c4495-272d-45c0-8bcb-22b0848868b5
checkpoint-status | c2dfcdbf-2955-419d-b108-ffede429bf4f |  | checkpoint | Pre-requisite Works
checkpoint-status | 22880dd4-2579-4d39-b8c9-957b8934c66f |  | checkpoint | Correct Location & Labelling
checkpoint-status | 919b553b-f5f3-4c09-8f17-9d5c2b61169a |  | checkpoint | Correct Software Mapping
checkpoint-status | bc6f4cea-40bb-4efd-b470-b4392c182cc9 |  | checkpoint | Discharge Autonomy Test
holdpoint | e7af81ef-61e0-4cde-9f0b-c1aae177aa04 |  | signoff | Checked By (Heyday):
checklist-flat | befeb558-5dff-408c-be76-d2ce72f1844a |  | checklist | Quality - In Ground conduit install. |  |  |  |  | Yes | Quality - In Ground conduit install - HV ONLY | 5f3c24cc-25d8-463d-9e04-a304ce091c0b
checkpoint-status | 73a71ac9-bed4-4633-9d29-21efd7bbd825 |  | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
checkpoint-status | 2622f687-370d-4ad8-902e-5f73f0b589b6 |  | checkpoint | Set out. (ITP Reference Item 2)
checkpoint-status | 6259a244-bbfe-42b5-b5fd-9ed8c0ad949c |  | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3)
holdpoint | 90fc07f1-12f8-4be1-896f-b45f3eac4701 |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | dd02b98f-0593-48ef-95db-8b6cc4b7ab98 |  | checkpoint | Conduit Installation. (ITP Reference Item 4)
checkpoint-status | c0e3dd45-3837-42c7-bee2-80fed1e7f336 |  | checkpoint | Spacer Frame Installation. (ITP Reference Item 5)
checkpoint-status | 5761ad7f-9073-4e10-8201-47d52ca32c93 |  | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
checkpoint-status | d08685d6-ed34-483b-89b9-269076cad5c8 |  | checkpoint | Bellmouths installed within Insitu Pits. (ITP Reference Item 7)
checkpoint-status | b3c19a1d-81eb-4263-999c-3a3a7b5c1c09 |  | checkpoint | Glue Conduits together. (ITP Reference Item 8)
checkpoint-status | 67b70002-92b4-4565-bbe6-d9c23f5fe188 |  | checkpoint | TSB Installation around & above conduits. (ITP Reference Item 9)
holdpoint | 367f0d61-a448-4b6f-9362-f1c6a51d7b09 |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 5aba8eea-2b46-4f4a-96b5-2272371c28af |  | checkpoint | 150mm cover of backfill above TSB. (ITP Reference Item 10)
checkpoint-status | cd6b3534-56e2-435e-b73b-aa9fcc6bee01 |  | checkpoint | Warning tape installation above 150mm cover. (ITP Reference Item 11)
checkpoint-status | f70d4a64-90e6-489b-9c09-8c9e5f9b1ce5 |  | checkpoint | Back fill & compact. (ITP Reference Item 12)
checkpoint-status | 8162eec1-3d56-4a82-bde2-8d1f7d768500 |  | checkpoint | Rope & pathway test. (ITP Reference Item 13)
checkpoint-status | 54eb1e84-db3e-4c93-95e4-fbc4fb10d586 |  | checkpoint | Sealing of conduits. (ITP Reference Item 14) HOLD POINT
holdpoint | 53bfa6af-a21d-4791-91fd-86ad581731fa |  | signoff | Signoff Required from Heyday & Multiplex
checklist-sectioned | 4fa4fbf4-42a3-4393-b3f3-b3449cbe025c |  | checklist | Main Switchboards (Energised) |  |  |  |  | Yes | Testing & Commissioning - Main Switchboards (Energised) | 64d6e037-8712-458e-a7e1-f150bd367c0a
checkpoint-group | ac0e86aa-8433-435d-99f0-ee31dee7d83a |  | section | Phase Voltage Reading
checkpoint-status | 24106199-b416-4225-9d08-100917b946cd |  | checkpoint | Red - Earth
text | c443a7c0-6aba-543f-82e5-1170cbc71f4a |  | textbox | Voltage (V)
checkpoint-status | e3980818-60e0-4b1b-ab2c-81724d8f83d1 |  | checkpoint | White - Earth
text | eef0209b-e0b9-523b-8d28-9f9340dc3729 |  | textbox | Voltage (V)
checkpoint-status | 18896dac-fc9f-46de-b007-79aeef2b0f90 |  | checkpoint | Blue - Earth
text | 2f39fda3-89eb-5730-adaf-57ef629f4a16 |  | textbox | Voltage (V)
checkpoint-status | 37cecaf8-dd25-4fa0-88b0-67aeb76f8251 |  | checkpoint | Neutral - Earth
text | d9ab42fc-3e57-59f4-9227-22a83acd2a34 |  | textbox | Voltage (V)
checkpoint-status | 1ab16c1a-4ccb-4083-9814-f592ea23ebf5 |  | checkpoint | Red - White
text | faf84b07-2bca-5974-ac1b-59db0a83d6d7 |  | textbox | Voltage (V)
checkpoint-status | 83ba6965-4ced-4f86-967f-af18081b752d |  | checkpoint | Red - Blue
text | c9bf26ff-c861-5cc4-ba8e-e92005fbe46e |  | textbox | Voltage (V)
checkpoint-status | 101036c5-4d49-417e-9273-22589dd9d669 |  | checkpoint | Red - Neutral
text | 130a2510-3cbd-5ac6-b383-6f1ce4e81e05 |  | textbox | Voltage (V)
checkpoint-status | 7bdcb278-4f06-4a4d-b354-23a8b3a31689 |  | checkpoint | White - Blue
text | 62ab94a7-c532-5e3f-b61c-750942b36bf9 |  | textbox | Voltage (V)
checkpoint-status | 83173e6a-8ca4-46ac-a28a-57ac2ba143c5 |  | checkpoint | White - Neutral
text | 06feaf21-f1e7-5548-8341-e2b5fcfc3809 |  | textbox | Voltage (V)
checkpoint-status | a8540f30-6054-4949-875f-3153f51ab8d9 |  | checkpoint | Blue - Neutral
text | d7baeed0-5f98-54f2-a730-e0d7b4d47bba |  | textbox | Voltage (V)
checkpoint-group | d602f38d-cb2d-47df-af96-38ea7789a0dc |  | section | Phase Rotation
checkpoint-no-status | cc20153b-ce79-445c-86cd-57ab49ea7a6a |  | checkpoint | Direction
button | 12292019-ba2f-5220-a323-2186e95666e1 |  | button | Direction: | Clockwise,Anti-Clockwise
holdpoint | 3da7e379-2ead-4d3d-8087-3dda4c33f598 |  | signoff | Checked By (Heyday):
checklist-flat | f8f7170d-7d95-45ff-a33e-8660a43544f1 |  | checklist | HV/LV Transformers |  |  |  |  | Yes | Testing & Commissioning - HV/LV Transformers | 682ebdb8-8578-489d-a9e5-3800d82eef20
checkpoint-status | 0969b89b-13b4-4408-9f80-44764c16f940 |  | checkpoint | Schneider Electric Transformer QA/QC Test Report – Installation Configuration Page 3.
checkpoint-status | 71e45806-0bf8-420a-9058-dc8022588864 |  | checkpoint | Schneider Electric Transformer QA/QC Test Report – Pre-Testing inspection Page 4.
checkpoint-status | 3db19474-7cc3-4bc9-96d7-b8a25713e7af |  | checkpoint | Schneider Electric Transformer QA/QC Test Report – Transformer Test - Page 4:
label | f8c6c0e2-0485-509a-931b-46c872a5edc9 |  | note | Continuity test on HV and LV Windings
label | 3faf0bd7-0a5a-5492-be65-9c05fe1f5766 |  | note | ○ Insulation Resistance Test LV Winding to Earth
label | a9a2e7ec-06f4-5b0c-89c3-d73ab8bec5d5 |  | note | ○ Winding Resistance
label | d5f48f7a-6630-5728-8eb8-e0783cbc2636 |  | note | ○ Winding Ration verification (taps: +2.5%, +1.25%, 0, -1.25%, -2.5% )
label | 07063b97-3ec1-52e0-b91d-4ecb899353d4 |  | note | ○ Vector Groups
label | b63500bd-c421-55e0-9a61-593f3e871930 |  | note | ○ Check bushings
label | bb642782-7878-5cb6-a87d-4afc54389d15 |  | note | ○ Control cubicle visual inspection
label | 8d2f3627-9622-502b-9733-5ad37a7f6000 |  | note | ○ Control Cabling within the control cubicle visual inspection and connection verification against approved schematics
label | c61de0f1-9a75-591c-8fd3-a5716389ee98 |  | note | ○ Confirm opening of LV door operates “normally open contact when doors are closed”
holdpoint | 5c13a156-5bca-4154-a40f-5738c1d988f4 |  | signoff | Checked By (Heyday):
checklist-flat | bc06466f-09e0-4844-adac-aec4b5269f76 |  | checklist | LV and Communication - Pit and Pipe Inspection |  |  |  |  | Yes | LV and Communication - Pit and Pipe Inspection | 6854771f-97b8-4a9d-8480-fd8c04d63c53
checkpoint-status | 8014076b-6fd0-4f39-92bc-06436c30abbd |  | checkpoint | Cover Slab and correct Pit installed per shop drawing.
checkpoint-status | 7f8c709e-47a2-46a9-97f3-9530310e73c8 |  | checkpoint | Pit Lid installed to correct FSL
checkpoint-status | 7392339a-0e99-4210-9eee-1c4acde014c7 |  | checkpoint | Conduits from pit out have been mandueled using correct size.
checkpoint-status | 2762682b-f76d-4347-b346-e128b9f353ef |  | checkpoint | Ropes installed in conduits
holdpoint | 4a19f46c-9fca-48f7-87c8-9ef56fa500f7 |  | signoff | Signoff Required from Heyday
checkpoint-status | e9793bd1-f449-4e14-bf49-ad1a79f8ff50 |  | checkpoint | Photo of pits installed.
checklist-flat | 6074ec10-56f3-4474-abae-aef805bb6293 |  | checklist | ITP |  |  |  |  | Yes | ITP | 877d5dc6-9a9a-42f4-9a24-13da1d037be9
checkpoint-status | 652e967d-7a17-434c-bf03-94f23854ac39 |  | checkpoint | Please attach copy of ITP
checklist-sectioned | f2ae26d0-732b-4c22-8a57-76221fbdbf34 |  | checklist | Low Voltage Busduct |  |  |  |  | Yes | Testing & Commissioning - Low Voltage Busduct | 8c12e5dc-b514-4ea9-a397-7add5c0a0739
checkpoint-group | 456b08ca-e207-4909-837c-9051d924cc65 |  | section | WSA20-MPX-04000-EL-ITC-31062000 - Construction Tests (Pre-energisation)
checkpoint-status | 88e083bb-65b3-4821-b713-25f807690161 |  | checkpoint | Pre-requisite Works
checkpoint-status | 33ff30d1-4b38-40a4-96a5-49373509e033 |  | checkpoint | Insulation Damage
checkpoint-status | 2e18a745-a672-4ea7-abde-38f5520a15b4 |  | checkpoint | Correct Type of Termination
checkpoint-status | 5868bfdf-2ba2-472a-96c7-b86573eac01d |  | checkpoint | Correct Colour Code
checkpoint-status | 777333ec-6526-40c3-93df-7866d419e0c5 |  | checkpoint | Correct Size and Labelling
checkpoint-status | d6fde58c-c327-4e00-b1b5-e06e20de61eb |  | checkpoint | Correct Routing
holdpoint | 52f30371-e3a7-46db-bcf3-738a1ecac67d |  | signoff | Checked By (Heyday):
checkpoint-no-status | 70be4b91-9326-41a3-8fa4-5846f1d6d28f |  | checkpoint | Continuity Testing
checkpoint-status | 8c208c2a-fda5-47d6-b289-65039016f967 |  | checkpoint | Red Phase
text | d760a07c-a0ab-5aea-8c85-e42a1b632a1b |  | textbox | Resistance (Ω)
text | 6388ecc3-dcbd-502c-ab3f-ea14405c4e8c |  | textbox | Target Resistance (Ω)
checkpoint-status | 3243a251-c227-4160-a312-a15171a5d0b3 |  | checkpoint | White Phase
text | 3302b7af-e714-5e74-a84f-e7fb93b90fa1 |  | textbox | Resistance (Ω)
text | 3b1aa585-d7f8-546c-b026-3c366b538946 |  | textbox | Target Resistance (Ω)
checkpoint-status | 3ad209b8-32e1-4793-9255-4611a4e16bf4 |  | checkpoint | Blue Phase
text | 59858db9-1356-5905-a89b-3fa1e81dc68e |  | textbox | Resistance (Ω)
text | e1abd291-b3ac-58e8-ba45-aa102f29d32c |  | textbox | Target Resistance (Ω)
checkpoint-status | 70ec6558-c48b-4ebe-b82d-06552c99f54b |  | checkpoint | Neutral
text | 8a9533d3-81f3-5462-a08f-ec5ff1eb073e |  | textbox | Resistance (Ω)
text | df35f72b-4921-5154-8a47-1113899f141c |  | textbox | Target Resistance (Ω)
checkpoint-status | f693b3a0-e418-4add-b8a2-9a71d2e49959 |  | checkpoint | Earth
text | e453448b-4dfa-5011-8935-2835892adffb |  | textbox | Resistance (Ω)
text | 5fe3340c-208d-566a-822e-ce7e6814bd47 |  | textbox | Target Resistance (Ω)
holdpoint | dbfa72ad-0f65-4b1a-8042-908f34a93fd8 |  | signoff | Checked By (Heyday):
checkpoint-no-status | a84923ae-54df-4440-8393-69b1740cd3a0 |  | checkpoint | Insulation Resistance
checkpoint-status | 1504c22d-c196-4b6a-a463-c82116a04a73 |  | checkpoint | R-W
button | 51128386-c24a-5588-bc0d-1859742fc9d4 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 8ab39c68-798e-50b3-bd8b-801f2be936cf |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 145effaa-c7ec-45c9-b0a8-668ffaf8f79b |  | checkpoint | R-B
button | d7b22b03-2fbd-5240-975b-f70b8bcfa28c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 17f55901-d760-55b8-adcc-eba36a9db950 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 2fd690f8-d16f-4162-93a0-cb824003ad7d |  | checkpoint | W-B
button | f15b6bc1-8404-551f-86df-c7f474a4fd3f |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | b8159012-21a9-5470-8f70-581503f99bd2 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 57ff2447-f45f-49f9-beca-57b4e4a2d8f6 |  | checkpoint | R-N
button | f033eda8-1460-5ead-b701-fc4ca3f111f1 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 88711205-0ac2-5f87-90b8-7e757ea5263f |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 7aba0c7e-1193-42bc-93f6-ee7313cb8b75 |  | checkpoint | W-N
button | a7c38ef3-e591-5de0-8f55-cbfafbb3f1e7 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 2eeb434d-4c7c-546a-9138-fabfa54850a6 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 98e7b3fe-61ea-41cc-adac-03baa5737c7c |  | checkpoint | B-N
button | 7c7c6c91-ec42-5c27-9342-2e1b53adf62d |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 5deb0752-ced7-5191-8005-a4a588f5ab19 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | c9358eb9-e82d-4cd4-bbf5-b5358d44d6f9 |  | checkpoint | R-E
button | 025fcaf7-a6b1-5b6b-afad-bf16eda78d5a |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 8fc9e7a2-08d6-58b2-a3ef-cb88ca761850 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 43c694d9-e5e7-4f0c-9eeb-f42b9c017003 |  | checkpoint | W-E
button | 2e88d830-4e53-5c93-b095-726cf4a277f1 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | e1d11c32-79ff-5d66-9922-2a4c32ab3ae4 |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | b0fcabbb-dfce-4f0e-a4cf-ea8dd8cac405 |  | checkpoint | B-E
button | 26666fa4-20be-53e6-99f5-8aa42cfdc78e |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | db1bdf79-6e41-5f02-a4b2-fcee282b2a5a |  | textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint-status | 4e3f03ee-ca63-411c-9fcd-00aa0065f5a3 |  | checkpoint | N-E
button | f3fb91b6-2604-50a5-98e6-5c1a2b1c4b17 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
text | 212c3234-fdd2-5bdf-8440-991c7d7d21fb |  | textbox | Actual Reading if <500MΩ/<1000MΩ
holdpoint | 3691258b-414d-430a-94d8-1cad21fea521 |  | signoff | Checked By (Heyday):
checkpoint-group | 44ee039e-db5a-4a1d-aeff-c0aa90df277c |  | section | WSA20-MPX-04000-EL-ITC-31063000 - Component (Energised)
checkpoint-no-status | e622dae7-fba7-4a8e-8804-f60bcef86ff7 |  | checkpoint | Phase Rotation
button | 3738276c-4df9-5e9d-b093-a7e863411365 |  | button | Direction | Clockwise,Anti-Clockwise
holdpoint | 5cc1309c-fd6c-472b-ae61-f18a2f5c90e9 |  | signoff | Checked By (Heyday):
checkpoint-no-status | ca68aa3c-494f-442f-b0c7-320f5b0db7a7 |  | checkpoint | Voltage
checkpoint-status | 6687dd39-41ee-4a27-bf2c-3119c60f0d42 |  | checkpoint | Red - White
text | 3e33d243-0b5d-560f-b40e-60b73467af2a |  | textbox | Voltage (V)
checkpoint-status | 4402a99d-a46b-476c-a608-9ac6c31746c3 |  | checkpoint | Red - Blue
text | 7a9f82cc-1075-5e64-9d44-26cee9c9802e |  | textbox | Voltage (V)
checkpoint-status | 39517011-7ef0-4299-823c-2fac5555af3f |  | checkpoint | White - Blue
text | 862b5091-e827-5b2b-9f7f-d8080f3a4bdf |  | textbox | Voltage (V)
checkpoint-status | 578353b6-66da-4c69-84d3-d25f100978c9 |  | checkpoint | Red - Neutral
text | c0e92404-a128-5877-9ad5-032dace55b21 |  | textbox | Voltage (V)
checkpoint-status | 6abdb4d8-f523-4e7f-abe2-6a090076b202 |  | checkpoint | White - Neutral
text | 79988495-81f3-50a7-ae62-30b076236ede |  | textbox | Voltage (V)
checkpoint-status | 901b9d68-9d8d-46b0-9d37-8b85a94af21d |  | checkpoint | Blue - Neutral
text | cabefad3-fc34-5b90-8882-64679f9b8a2e |  | textbox | Voltage (V)
checkpoint-status | db9abba3-c3e4-43f6-974c-e92f58d4da54 |  | checkpoint | Red - Earth
text | af52eb64-1869-5022-9292-3b93bb4f7313 |  | textbox | Voltage (V)
checkpoint-status | d299dd35-6908-46bd-98a8-923e9a1479fb |  | checkpoint | White - Earth
text | 75009560-ea82-5284-af34-edeca9f3da79 |  | textbox | Voltage (V)
checkpoint-status | 87e2b594-16a1-4960-83a8-ce438350ef12 |  | checkpoint | Blue - Earth
text | 2abf185b-4fea-5b46-ba0b-c14224f28689 |  | textbox | Voltage (V)
holdpoint | 755c4764-8331-4a13-a39e-3936836cbc34 |  | signoff | Checked By (Heyday):
checklist-sectioned | 55687e49-7ac5-41c7-95bb-08c0e7c58654 |  | checklist | PMCS |  |  |  |  | Yes | Testing & Commissioning - PMCS | 8fd5c6d4-3d8b-41d3-bd55-357253f55fcc
checkpoint-group | 6d39116f-93ac-4c31-b733-b41891044e4a |  | section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests (Pre-commissioning)
checkpoint-status | 0f3e7711-e0b9-4442-9cde-9544fac38446 |  | checkpoint | Schneider Point to Point Validation ITP - RIOM
checkpoint-status | 363f12e9-42ca-4ebd-9f72-465cb421c246 |  | checkpoint | Schneider Point to Point Validation ITP - PAC
checkpoint-status | 909ed226-bacd-4172-948f-6bb3a9774ffe |  | checkpoint | Schneider Point to Point Validation ITP - EPS
checkpoint-status | 4170b671-0120-496a-950c-fc6c643c72a1 |  | checkpoint | Schneider Point to Point Validation ITP - PFC
checkpoint-status | 4bce19cd-c9e5-44b5-8633-e57edd635592 |  | checkpoint | Schneider Point to Point Validation ITP - UPS
checkpoint-status | 512c4451-1ea2-4d4c-92e5-aa9bedb5a86f |  | checkpoint | Schneider Point to Point Validation ITP - EV
checkpoint-status | fb8cc9f5-9762-4676-8db2-7fb9a4072ff9 |  | checkpoint | Schneider Point to Point Validation ITP - IEM
checkpoint-status | fef1adbb-cd17-4792-83f6-ddad180e93d7 |  | checkpoint | Schneider Point to Point Validation ITP - eGSE
checkpoint-status | e0760722-56ae-4c39-9758-f4ad831a7800 |  | checkpoint | Schneider Point to Point Validation ITP - GEN
checkpoint-status | 0d4a2136-bbf3-4120-9af8-aa4ee417b934 |  | checkpoint | Schneider Point to Point Validation ITP - LCS
checkpoint-status | f2e4baf3-db16-42c1-856b-c5d1ea2af0dc |  | checkpoint | Schneider Point to Point Validation ITP - EML
checkpoint-status | 32ac393c-b449-49c8-8c01-4537449c011d |  | checkpoint | Schneider Point to Point Validation ITP - PV
holdpoint | 2aaa59e8-f9a9-40e8-95e6-eb37298f6b25 |  | signoff | Checked By (Heyday):
checkpoint-group | ff22da6d-3cf0-4ac7-84a6-1401d58129f9 |  | section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests (Commissioning)
checkpoint-status | 42e63be9-0b4d-45fa-a96c-67f05aaa6664 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
checkpoint-status | b1cacbf7-ed0f-4b96-9a82-abceea0421a7 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
checkpoint-status | 8c03faf9-2e4c-4ef7-9741-bad9b0bbc42d |  | checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
checkpoint-status | d1aca762-82b0-4fa7-9cd5-d65258b3be37 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
checkpoint-status | d5f5901f-5e6f-4899-b397-55aa27f163eb |  | checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
checkpoint-status | c0daf05b-b0eb-4b4e-8f71-b97e9dc4a6e4 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - EV
checkpoint-status | 8ace8b4e-3b9a-43be-9525-4151be7b76cc |  | checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
checkpoint-status | 559e5a9a-153d-4f70-9936-accb5ef23056 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
checkpoint-status | e76c6a77-eb82-4ce1-b0ab-43b760b35fd1 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
checkpoint-status | d50a52b4-a611-4608-996c-f6ed4059e72b |  | checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
checkpoint-status | 04659ead-350e-4522-adac-90c797c5c308 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - EML
checkpoint-status | f983179a-9ad1-4eb9-a581-a3b64af3d443 |  | checkpoint | Schneider WSA LV PMCS Cx ITP - PV
holdpoint | 5575884b-b5f1-4f3a-bcf7-d8139b45eee7 |  | signoff | Checked By (Heyday):
checklist-flat | 2a7a5575-2a12-47c2-a292-10a24024510d |  | checklist | Quality - Power and Lighting Subcircuits |  |  |  |  | Yes | Quality - Power and Lighting Subcircuits | ad30fce7-fc69-4556-b72d-785e683cb1ef
checkpoint-status | 70aa64d9-0d08-47a5-8647-185834a86644 |  | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
checkpoint-status | 84059ae9-7244-4dd8-9a39-ebc63fff828d |  | checkpoint | Correct size & cable type. (ITP Reference Item 2)
holdpoint | 4a470d59-f780-42db-bffe-6da8cc16b798 |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | db00ad9e-a369-4a3c-bd2f-9ccd89e5e646 |  | checkpoint | Installed to correct cable routing arrangements & circuit number. (ITP Reference Item 3)
checkpoint-status | 4219368a-1076-4619-8929-abca8707cfec |  | checkpoint | Installed to final location. (ITP Reference Item 4)
checkpoint-status | 20a0c556-952f-4aa0-bd5d-f94f701bcb09 |  | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 5)
holdpoint | 1edfb0b5-9856-4905-aedf-671e3f5cee52 |  | signoff | Signoff Required from Heyday & Multiplex
checklist-flat | 86aa87a6-b5d4-4b51-9765-f9fe0fc446b6 |  | checklist | Pole Light Footings Installation ITC |  |  |  |  | Yes | Quality - Pole Light Footings Installation ITC | b3653cae-4453-4750-8932-3242343a6308
checkpoint-status | 93472ed9-c576-4bed-b079-e12233246175 |  | checkpoint | Receipt of foundation cages delivery to site & storage. (ITP Reference Item 1)
checkpoint-status | 791b4fb7-fecc-41d7-ba76-cc69cb27162e |  | checkpoint | Set out (Correct pier locations as per approved shop drawings). (ITP Reference Item 2)
checkpoint-status | 19e95f7b-a15c-46ca-a66e-1812cf73670b |  | checkpoint | Correct trenching alignment & depth with excavator and auger. (ITP Reference Item 3)
checkpoint-status | 22f2ae71-60be-47d2-a9f0-112b19deee8c |  | checkpoint | Install cage and rag bolts to correct finish level. (ITP Reference Item 4)
checkpoint-status | 13281cde-694f-4b1e-9787-09b3d6d65227 |  | checkpoint | Install conduits and formatube. (ITP Reference Item 5)
holdpoint | 23fa6f29-6099-4518-9c9d-54ac3c86a3d9 |  | signoff | HOLD POINT inspection prior to concrete
checkpoint-status | cd81f109-9a77-4b22-a318-90a67a3acbd7 |  | checkpoint | Concrete installation with tremie pipe. (ITP Reference Item 6)
checkpoint-status | 17ea0ec2-33b1-4fee-be15-8539fba8033e |  | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 7)
holdpoint | 1d223f93-c353-40b4-95bf-e85ae1de063a |  | signoff | Signoff Required from Heyday & Multiplex
checklist-flat | 1d378708-99dd-41cd-983b-c8c2d8a87dfb |  | checklist | Quality - Cable tray/Ladder |  |  |  |  | Yes | Quality - Cable tray/Ladder | b99e1bbf-8088-4867-80a2-3e90377a8162
checkpoint-status | f7304667-4e24-48f5-86d3-64ffdb1e21d2 |  | checkpoint | Receipt of Cable Tray delivery to site & storage
checkpoint-status | 2bd9f9cf-263c-476d-95d4-0a08b088bef3 |  | checkpoint | Set out to be confirmed with latest AFC Drawings
checkpoint-status | e64772dd-b6dd-4bf5-8a12-dc36b7263180 |  | checkpoint | Accessories to be factory made items
checkpoint-status | fc0f799c-8b1b-4379-bc47-2f292f97907c |  | checkpoint | Correct Levelling & Alignment
checkpoint-status | b080b835-d7b7-432f-a0c0-8ab4fe9b2f95 |  | checkpoint | correct bracket and safe fixing
checkpoint-status | 4a33f2d3-208c-4b01-be48-6274464e9497 |  | checkpoint | Correct Bends used (Cable Ladder)
checkpoint-status | 3928498c-2649-4de9-8894-ce6451f89040 |  | checkpoint | Cable Tray Checked For Sharp Edges
checkpoint-status | 818b9572-aaf8-4143-80ad-91e2dbb47f32 |  | checkpoint | Containment Earthing - As Per the Standards
holdpoint | ec96a558-76fa-48dd-91b2-bf90d58d063c |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 2d94ecbf-4577-48d4-8ae1-f2e0f5ca54ef |  | checkpoint | Photos attached.
checklist-flat | df71fccc-889f-4250-bc86-4df129d6a8ae |  | checklist | LOT BREAK UP |  |  |  |  | Yes | LOT BREAK UP | bf79bc91-8ad4-4f46-930b-65b5c78a92e6
checkpoint-status | dcdf5328-e886-4cde-95f0-59dde8dc5444 |  | checkpoint | Attached Mark up of Lot Breakup
checklist-flat | f5d4527b-a4f5-4f85-a73d-8bb4269b0fe5 |  | checklist | Quality - Distribution boards |  |  |  |  | Yes | Quality - Distribution boards | c02f82a4-8acb-45f1-b205-c2803f466e5d
checkpoint-status | d6119b14-f47e-46ad-9c3d-1dfc2d7431d3 |  | checkpoint | Receipt of switchboard delivery to site
checkpoint-status | bce8f233-f43b-4bb6-a305-e9445debc197 |  | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
checkpoint-status | 3fed3a41-f5ad-4054-adc2-0c781a13ca4d |  | checkpoint | Correct alignment to set out drawings
holdpoint | d3ccabc7-63ba-425b-ba90-8961928abe68 |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 0b755a50-7baf-4f0c-8830-94a475ae7592 |  | checkpoint | Correct bracket and safe fixing
checkpoint-status | aa1624e4-fda7-4b38-9962-42d72de05b34 |  | checkpoint | Photos of boards attached
checklist-flat | acb2f3e9-3777-4399-b35b-cd82a51e0bc9 |  | checklist | Quality - Inground LV & Communication Conduits |  |  |  |  | Yes | Quality - Inground LV & Communication Conduits | c522e169-e86f-4012-8c80-3cd661ff986d
checkpoint-status | 9b2fffc9-270e-40a7-8705-dc47b2e2fc93 |  | checkpoint | Receipt of conduit delivery to site & storage. (ITP Reference Item 1)
checkpoint-status | 70b2b64d-0827-4bee-80ee-6c7a6b30714b |  | checkpoint | Set out. (ITP Reference Item 2)
checkpoint-status | 0a679e76-8055-432b-9110-4815fb67c9bc |  | checkpoint | Excavation - Correct trenching alignment & depth. (ITP Reference Item 3) HOLD POINT
holdpoint | 59074d54-8fd4-43b0-a5b8-4cdfea916d9c |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 357831f8-c75f-46be-9596-87d215933f06 |  | checkpoint | Conduit Installation. (ITP Reference Item 4)
checkpoint-status | 9e6699ed-e0b0-4dd0-b3a0-700451229f5f |  | checkpoint | Spacer Frame Installation if required. (ITP Reference Item 5)
checkpoint-status | a87979ac-06d4-4e99-82f7-e6aaefb00a8f |  | checkpoint | Change of direction/bend Installation, correct bending radius used as per drawing. (ITP Reference Item 6)
checkpoint-status | 333936bd-24ef-4be2-9e99-69381801f33f |  | checkpoint | Glue Conduits together. (ITP Reference Item 7)
checkpoint-status | 6987a898-3ce5-4f8a-a5de-6ab949600aeb |  | checkpoint | 300mm cover of backfill above conduits. (ITP Reference Item 9)
checkpoint-status | 8f0fea9b-58bd-4345-9e8a-4aa51bceb2c8 |  | checkpoint | Warning tape installation above 300mm cover. (ITP Reference Item 10)
checkpoint-status | dec68183-4c9b-4ee1-9342-effcea72e79a |  | checkpoint | Back fill & compact. (ITP Reference Item 11)
holdpoint | 96c28ed0-6797-4ae4-b00d-b769a9c6d3bb |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 3d9dc89b-30c6-419b-a47d-9320633a0ebf |  | checkpoint | Record photo evidence. (ITP Reference Item 14)
checklist-sectioned | 2c616a08-4007-4620-addb-f581fcab06d0 |  | checklist | Solar Photovoltaic System |  |  |  |  | Yes | Testing & Commissioning - Solar Photovoltaic System | c579d32d-d874-44f7-8140-62cb4e952edc
checkpoint-group | 89d1f6d2-1963-4133-a7de-b92c3d8e7f56 |  | section | WSA20-MPX-04000-EL-ITC-31152000 - Construction Tests (Pre-energisation)
checkpoint-status | bd544349-4a6f-4b8a-a4dd-081a8fdb5feb |  | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)
checkpoint-group | 0be74ac1-e8e6-4c39-99d5-17f70815606b |  | section | WSA20-MPX-04000-EL-ITC-31153000 - Component Tests (Pre-commissioning)
checkpoint-status | d61768d8-9093-468d-9ae4-f38258a54d34 |  | checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
holdpoint | 40175248-b572-4786-a7f0-7f2770546d75 |  | signoff | Checked By (Heyday):
checklist-flat | 4f516721-9264-4603-a113-5d0c70e71377 |  | checklist | Lighting Control |  |  |  |  | Yes | Testing & Commissioning - Lighting Control | c6d05d6c-6653-4af0-b947-9251f094b48f
checkpoint-status | 8c82fdbe-8112-4b24-8d84-0462942894a2 |  | checkpoint | Pre-requisite Works
checkpoint-status | f6adb625-199d-424f-91ee-be65f1df8ba3 |  | checkpoint | Correct Location & Labelling
checkpoint-status | 857c855a-81e6-4de5-a16a-74858e79f3c5 |  | checkpoint | Manual Control
checkpoint-status | e0ecd3a3-ac7c-4d58-81db-b765f2d3fefa |  | checkpoint | Occupancy Sensor or PE Cell Control
holdpoint | 420e3ac5-6120-45c2-9561-ce56de03204b |  | signoff | Checked By (Heyday):
checklist-sectioned | aa74fcea-9fd7-4272-85da-3062e6d82c72 |  | checklist | Subcircuits |  |  |  |  | Yes | Testing & Commissioning - Subcircuits | d18be06a-d775-4cb0-9fe5-4490e6ded185
checkpoint-group | ce80f4f8-359e-45ba-82f4-beff319bdb56 |  | section | WSA20-MPX-04000-EL-ITC-31072000 - Construction Tests (Pre-energisation)
checkpoint-status | 9d1d725f-e75f-4651-899d-ba169217ea78 |  | checkpoint | Pre-requisite Works
checkpoint-status | ca8f262f-5379-4ace-a0eb-0dfc56b3ea73 |  | checkpoint | Insulation Damage
checkpoint-status | 1222671d-68ee-410e-bcf3-47d40e26c4e0 |  | checkpoint | Correct Type of Termination
checkpoint-status | c6b43b7a-37ad-4a04-a944-8ce9c6b9df72 |  | checkpoint | Correct Colour Code
checkpoint-status | 56b8074e-3f10-43a0-b58f-0782e3a08141 |  | checkpoint | Correct Outlet Rating and Size
holdpoint | 0d74cdb5-6cef-4b2b-b5fc-ce05cd0e1663 |  | signoff | Checked By (Heyday):
checkpoint-status | 72109a08-e8d6-4cad-9b3f-4460f2ceb457 |  | checkpoint | Earth Continuity
text | de1a5eba-25ac-5bf6-bb10-03bca0555d70 |  | textbox | Resistance (Ω)
text | 39a5c5a4-291a-5980-9ad4-d1fc8bfc1c5d |  | textbox | Target Resistance (Ω)
holdpoint | 5164c35e-42c7-4f64-a57b-2d830c04c8e6 |  | signoff | Checked By (Heyday):
checkpoint-status | ed5dd999-579f-4ac5-afc5-12a8a7770c67 |  | checkpoint | Polarity Check
button | df6af67d-2fd0-5063-bec8-31c1107d65e4 |  | button | No Transposition | YES,NO
button | fc3d0071-01ec-5171-879c-04bfe86e2fc8 |  | button | Switch in Active | YES,NO
holdpoint | a398744d-c9db-47f1-848e-0c3d24393a20 |  | signoff | Checked By (Heyday):
checkpoint-no-status | d16b7916-d583-4860-aa5d-8104fa2d9cbf |  | checkpoint | Insulation Resistance
checkpoint-status | 002ce7da-be2e-408b-9719-f255d6ed9874 |  | checkpoint | R-W
button | c074a980-6c99-55a2-aeed-a5ebee961fdc |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 96b4099e-4f75-52a1-811e-2c87becd0144 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | b076e3cf-5ab6-4578-b487-baddcc70a05f |  | checkpoint | R-B
button | 21693f30-d3cd-59d7-bff7-f881e177d99f |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | d31cb9e6-20de-5b7a-9340-5cfbc1e83e9a |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | af1e8ec5-0584-4d82-afe8-5494e33f2b64 |  | checkpoint | W-B
button | 76ad528c-7cb4-5581-bf3c-44f168daf6b2 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 5f7d3f5e-1c91-5d1e-9113-cb3eacd09e06 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | c6a942e1-a481-4b2b-8ac8-f4af0bccb645 |  | checkpoint | R-N
button | 81cd113b-d80f-5d68-86b6-d47d311c959f |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | c171a1f5-ea56-51d7-a50f-2a7e07107e62 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 75fcf534-58f4-4cca-b1a6-6aea9a25b6be |  | checkpoint | W-N
button | 40ed3da2-01c9-598d-b5b4-06dc6d8acde9 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 781e4aa2-521d-5f38-8efd-ffe05f5f62bd |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 7771afbb-88cc-4091-b498-3d9df7f44e21 |  | checkpoint | B-N
button | 81711b4e-f1c7-5257-b978-fbf0b4fb0679 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | c32633c6-9ccf-5d3b-85a1-7ddc379371e9 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3399558b-fe36-46cc-9a7a-7ab871eda1d6 |  | checkpoint | R-E
button | 2fc92432-118d-5228-8a7b-6fd1f750cd94 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | da535eb8-c4c9-5496-96ed-da1d83bc7c0e |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | dd4330fd-ab08-473c-ace6-4cba61f8b3dc |  | checkpoint | W-E
button | 446500c6-98b6-5ab1-9e11-67e0ea488f5c |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 9b0438c7-e9b8-5085-b97b-2da64fbf6cc6 |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 8dee7980-1d7b-4864-be15-b0b0114f6466 |  | checkpoint | B-E
button | 6914f480-b52c-51b2-bf42-ed95e0395890 |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 4dec0f28-07a7-5440-b3ab-2dcaaf80318e |  | textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint-status | 3bc4c2fa-6b14-497f-bbba-2c26290b4da8 |  | checkpoint | N-E
button | 96d1dc4f-c848-55c9-bc9e-d039426e369b |  | button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
text | 8a51a274-a03a-5be1-928c-de42db9f1b8f |  | textbox | Actual Reading if <200MΩ/<500MΩ
holdpoint | 39c2a196-cfe9-457e-acfb-00bfb45aaacc |  | signoff | Checked By (Heyday):
checkpoint-group | e90b5211-44af-491a-99ad-c67560a2ae43 |  | section | WSA20-MPX-04000-EL-ITC-31073000 - Component (Energised)
checkpoint-no-status | be4c3d3e-066f-4495-bc9f-cc14026ba636 |  | checkpoint | Voltage
checkpoint-status | a3c3ff91-c597-4a30-98f2-a23d70da4600 |  | checkpoint | Red - White
text | fa35a161-1cb0-5934-91a0-36b921249c9d |  | textbox | Voltage (V)
checkpoint-status | d12560ff-0b47-48f4-9fa1-4c7071f4ef7b |  | checkpoint | Red - Blue
text | 490c400e-5a07-53eb-b032-f1c14eb14369 |  | textbox | Voltage (V)
checkpoint-status | 550ad47e-b49c-4319-9724-2cb00a19d06e |  | checkpoint | White - Blue
text | 852028f4-a693-53ba-bc17-90b93817959b |  | textbox | Voltage (V)
checkpoint-status | 8f76cb4d-b653-4c9a-975d-81ea1ed77bd5 |  | checkpoint | Red - Neutral
text | 7f6796e0-21a7-5efc-811b-abcc6be2a643 |  | textbox | Voltage (V)
checkpoint-status | ff89a1e5-81ef-4902-89d8-d10461435870 |  | checkpoint | White - Neutral
text | 890d3091-a296-53bf-8218-818c1bac95d8 |  | textbox | Voltage (V)
checkpoint-status | 1d0aed37-8c51-4936-a4ad-351aa70e6c6b |  | checkpoint | Blue - Neutral
text | 17b0609e-05c2-5828-b731-6f2a7dbd5e0b |  | textbox | Voltage (V)
checkpoint-status | 179355a9-a625-4727-a277-889f26566fb1 |  | checkpoint | Red - Earth
text | d7cfc087-6bde-5bba-912b-f941d80963b6 |  | textbox | Voltage (V)
checkpoint-status | c3595eac-0ee2-4011-8eb9-f0b70da112e7 |  | checkpoint | White - Earth
text | fd6a712b-4c3d-5160-846b-2c6d1c388530 |  | textbox | Voltage (V)
checkpoint-status | 3e6d322b-b737-4244-a7ee-3762587e78f3 |  | checkpoint | Blue - Earth
text | 4dda6179-996a-5e30-8d80-0f634bc801aa |  | textbox | Voltage (V)
holdpoint | 49dc874e-24aa-4d1a-bb8f-9091130f03b6 |  | signoff | Checked By (Heyday):
checkpoint-status | a8b50e2c-71fb-4144-af69-9dae25366f7b |  | checkpoint | Earth Fault Loop Impedance Test - (N/A if the circuit is RCD Protected)
text | 2d020140-c388-50e2-80d6-7716adecc947 |  | textbox | Impedance (Ω)
text | 80ee3bd8-09e6-5ca2-94a6-d61e9ede1bd9 |  | textbox | Target Impedance (Ω)
checkpoint-status | e9ac923d-d16c-4a2d-b951-0fe526ee02f2 |  | checkpoint | RCD/RCBO Tripping Test
text | 034f732f-e6f8-5d9d-ad1e-d40373576b83 |  | textbox | Trip Current (mA)
text | fd409c9e-0861-55a7-bc35-f2c74a19552b |  | textbox | Trip Time (ms)
holdpoint | 0041b9db-30c0-4e21-956d-c1447d070b4d |  | signoff | Checked By (Heyday):
checklist-sectioned | 8a12bc81-852a-42fa-919d-77c59291ec49 |  | checklist | Distribution Boards |  |  |  |  | Yes | Testing & Commissioning - Distribution Boards | da3d6cb0-a1af-44eb-b1f6-ac5f355cee21
checkpoint-group | befff1b7-cdc5-48ea-a061-d23e489f4a54 |  | section | WSA20-MPX-04000-EL-ITC-31042000 - Construction Tests (Pre-energisation)
checkpoint-no-status | 8aef7084-c54d-490f-94b0-f6c82345b0e4 |  | checkpoint | Physical Checks
checkpoint-status | 072462a1-79cb-4d12-ae2e-4806c776acc3 |  | checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | b9e204ed-e733-40ee-b963-a527532331c0 |  | checkpoint | Confirm correct circuit identification and labelling
checkpoint-status | d5b14b6d-0bb8-4fa5-9a7d-ac1aa4dfb9f5 |  | checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint-status | b5aa7b16-ca58-4132-bd75-df4f38a92c48 |  | checkpoint | Confirm correct phase identification of busbars and cables inside the board
checkpoint-status | 960814b1-d4f1-4eb8-afd6-9dd4fe2a4e8d |  | checkpoint | Confirm correct size of earthing conductors
checkpoint-status | ecc2d984-30b7-4816-be06-eaa075472837 |  | checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
checkpoint-no-status | 374c4c6c-7d97-402d-b9b2-df2750f2e197 |  | checkpoint | Mechanical Checks
checkpoint-status | 9adb9b5c-f2aa-403c-a906-dafac33518bd |  | checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint-status | 3d4c00e6-103e-4b45-b777-807d0bf49eca |  | checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint-status | a03b8395-b346-4154-bfb9-b39012ac6ec1 |  | checkpoint | Repeat mounting and dismounting of power fuses for 1 time
checkpoint-status | 43f3a65b-0bfd-4bed-b296-c13c8fcb731e |  | checkpoint | Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | b2ba8713-1fcc-4a08-aaed-6f3437572b50 |  | checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint-status | 7eb74bea-7458-464e-8320-a6171450ac7a |  | checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
checkpoint-no-status | 75558229-01ad-49c2-8a72-d0087e6382c6 |  | checkpoint | Preliminary Checks
checkpoint-status | 1b9649bb-34c9-41f0-88db-887257b20716 |  | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint-status | 6562a44e-93c6-45f3-8609-f2035daa6fc8 |  | checkpoint | 2. Confirm Main Breaker Closed
checkpoint-status | 8869132b-6f36-49f4-9f9c-39e148ef7dda |  | checkpoint | 3. Confirm Outgoing Breakers Closed
checkpoint-no-status | 8b53b68c-cbbd-417e-ab01-4b587ccc9cce |  | checkpoint | Insulation Resistance (500V)
checkpoint-status | 2adf828e-5eab-417e-9417-3225e0b451f5 |  | checkpoint | 1. Between L1 Phase and Neutral
button | 252995c4-3058-5922-a590-3f4b901feaef |  | button | >10MΩ | YES,NO
text | 4dbb3afd-b81a-5e23-ac52-7cc41e9f6021 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 4437b518-52e7-40cd-ad19-cabd978af9e3 |  | checkpoint | 2. Between L2 Phase and Neutral
button | 480e065c-db22-5f9f-8e8f-c3e212f65e55 |  | button | >10MΩ | YES,NO
text | 4409fbb1-de4f-57a1-ae07-42d1209fd8cf |  | textbox | Actual Reading if <10MΩ
checkpoint-status | af96019b-0aa8-4ae0-9727-4770bef5fbfa |  | checkpoint | 3. Between L3 Phase and Neutral
button | 6af31d2a-1187-5fb5-8cd5-188648ae34f2 |  | button | >10MΩ | YES,NO
text | 5beadad3-245d-5f34-8c06-c6b4f3f77dd3 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | a4739208-5f93-485e-98c1-eae8fbc39f1c |  | checkpoint | 4. Between Neutral and Earth
button | 24b51fe3-e3fb-571c-bc7f-f01ce11f3fa5 |  | button | >10MΩ | YES,NO
text | a9752b8c-002f-5c9b-8b93-7804d1e9ca4e |  | textbox | Actual Reading if <10MΩ
checkpoint-status | b69b2eba-14a2-460a-96dd-c0bd6e2c0703 |  | checkpoint | 5. Between L1 Phase and Earth
button | 92108cb4-fd9d-58e0-8408-a5bdba99614f |  | button | >10MΩ | YES,NO
text | 282e675c-e94f-5301-ab4c-c4f88b6ba74d |  | textbox | Actual Reading if <10MΩ
checkpoint-status | a1aada8f-7ef3-4f0b-8881-bafff775e948 |  | checkpoint | 6. Between L2 Phase and Earth
button | ab812b25-1864-5914-b7a4-bccfbc0281a2 |  | button | >10MΩ | YES,NO
text | dcd85f6d-abf7-5960-9bba-94351f6977fc |  | textbox | Actual Reading if <10MΩ
checkpoint-status | baeee464-7a53-4cb9-b98d-de0d3d08b37b |  | checkpoint | 7. Between L3 Phase and Earth
button | d593c4ed-c29d-5080-95ef-1d02134bc06c |  | button | >10MΩ | YES,NO
text | cdb39ec0-d324-5528-a29f-162edddda46c |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 3dcd5104-a300-474f-b39f-322838a7e336 |  | checkpoint | 8. Between L1 Phase and L2 Phase
button | 03cb3c11-8203-5438-bc6c-8afa28b8c8e0 |  | button | >10MΩ | YES,NO
text | 661bbaa2-4eac-5c30-b253-b7204dccea05 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 19021149-7849-4fef-a610-d9bc8a5c6369 |  | checkpoint | 9. Between L1 Phase and L3 Phase
button | 2a294e6f-8529-5b72-acd2-34fa2e75bfd6 |  | button | >10MΩ | YES,NO
text | fc5794e5-0c81-50f8-b3e4-7b6c8294ac7d |  | textbox | Actual Reading if <10MΩ
checkpoint-status | a8269f11-ac62-4c74-94e7-48599ffa610a |  | checkpoint | 10. Between L2 Phase and L3 Phase
button | e7be9898-6b92-57bd-8e79-6f186b8011d7 |  | button | >10MΩ | YES,NO
text | eac45ed8-3dab-55c3-a8c3-62117aad5561 |  | textbox | Actual Reading if <10MΩ
holdpoint | 264bb266-777b-41db-babe-9d856501af0d |  | signoff | Checked By (Heyday):
checkpoint-status | c51d6c5a-4c34-4fd6-9f69-4dd6685aa92f |  | checkpoint | Earth Continuity Test
text | 43e3ca24-26ca-5bae-b4cd-846a5902f0ef |  | textbox | Incoming Earth Size (mm²)
text | f375eb93-4844-58fd-a0c0-b6d15e09dd30 |  | textbox | From (MSB/DB)
text | e178bfbd-0a59-5558-acd5-10b70c3c3eca |  | textbox | Resistance (Ω)
holdpoint | fc6523f2-5b0f-4a72-8fc0-722726b09ac7 |  | signoff | Checked By (Heyday):
checkpoint-group | af84f614-889a-4fc0-b51a-9761b23502cd |  | section | WSA20-MPX-04000-EL-ITC-31043000 - Component (Energised)
checkpoint-no-status | 046e7bec-7262-4a87-a45e-0befc79d0779 |  | checkpoint | Phase Voltage Reading
checkpoint-status | 2ed8b086-f527-4d3a-906d-580a04bcaf16 |  | checkpoint | Red- Earth
text | 6879d49d-05ab-5a2e-8537-54c84bb5ae90 |  | textbox | Voltage (V)
checkpoint-status | 10a35a7c-bbcd-4651-9411-0ff435579b6a |  | checkpoint | White - Earth
text | 8fa2a7c7-a441-5dc1-b27e-d0e19acaa129 |  | textbox | Voltage (V)
checkpoint-status | bd4579f9-5ede-4029-b670-d1c6e71bad69 |  | checkpoint | Blue - Earth
text | 9a98399d-8c33-52eb-a56c-fcda7285c85b |  | textbox | Voltage (V)
checkpoint-status | 4ccde900-8c93-4ad6-a919-cc826d7d3e2b |  | checkpoint | Neutral - Earth
text | c83a65a0-1e36-54f9-98dc-93ac5eeb9567 |  | textbox | Voltage (V)
checkpoint-status | d506e7d1-18b8-430a-b5f1-b06b17d580da |  | checkpoint | Red- White
text | 5ab20a3d-34ae-541c-aaed-dc79c259c08e |  | textbox | Voltage (V)
checkpoint-status | 3e9feb99-d15b-4460-986d-6ffa2c39141d |  | checkpoint | Red - Blue
text | 41bd1bf7-a66c-53ca-9cb9-1cc912c581e3 |  | textbox | Voltage (V)
checkpoint-status | 451b83f5-61ba-441f-ad8f-2275ba50ed49 |  | checkpoint | Red - Neutral
text | 9c9bfbec-3187-56e6-92d6-ed7fb858af08 |  | textbox | Voltage (V)
checkpoint-status | 6cb39429-0426-442b-8cde-74f6fda4c058 |  | checkpoint | White - Blue
text | 0d0ab664-371a-53b5-b99e-9b61aeafb9c6 |  | textbox | Voltage (V)
checkpoint-status | bc6b1ec6-7af5-46fd-999d-a18b8162918b |  | checkpoint | White - Neutral
text | 74fae398-d9b7-5755-b6a7-a4456e8039ce |  | textbox | Voltage (V)
checkpoint-status | 4c776b83-3e40-4ed1-81ff-899481e99196 |  | checkpoint | Blue - Neutral
text | acd7ac2e-f037-5060-8ce0-a37fb947c6b1 |  | textbox | Voltage (V)
checkpoint-no-status | f21d3dc2-9344-4fee-8c58-ac76db31cc6c |  | checkpoint | Phase Rotation
button | 1c9ff4c4-9684-5348-85a7-cd12c3c9a381 |  | button | Direction | Clockwise,Anti-Clockwise
holdpoint | eb0701b5-d2f3-471f-a88c-f8209dbd620d |  | signoff | Checked By (Heyday):
checklist-flat | 1692c674-264d-43a8-895e-89d4489657b9 |  | checklist | PFC |  |  |  |  | Yes | Testing & Commissioning - PFC | dab4326f-13e5-489f-9245-3a69c35d77a0
checkpoint-status | b9e5f50a-5821-4da8-8e5f-7ed2189325d8 |  | checkpoint | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
checkpoint-status | 9ca0f94b-ac56-403c-b7ca-19d64ec7c5f3 |  | checkpoint | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
checkpoint-status | 62bf39a1-b81f-432f-ac16-19e111f34dbe |  | checkpoint | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
checkpoint-status | 243a503a-d40b-4a84-b625-6cf5070751e9 |  | checkpoint | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
checklist-sectioned | 9fab4365-0c7c-4272-bb80-5b9faa529583 |  | checklist | Main Switchboards (Pre-Energisation) |  |  |  |  | Yes | Testing & Commissioning - Main Switchboards (Pre-Energisation) | dbc977a7-0dc7-45e4-a7db-3390fdef7ef5
checkpoint-group | 22eb7f7e-8c59-4487-a47e-66dfb2a8e4d9 |  | section | Physical Checks
checkpoint-status | 5c2ce6ee-2a07-4eb2-9732-1425352814d4 |  | checkpoint | 1. Confirm boards dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | 5be2bd0b-1025-4ae4-ab50-3f0c711f4972 |  | checkpoint | 2. Confirm correct MSB Form of Separation, Provide actual Form of Separation in Comments section
checkpoint-status | 996b0331-5238-44f9-8e27-1af654b0136a |  | checkpoint | 3. Confirm the Layout of fitted components (ACBs, MCCBs, MEN, ATS) is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | d34f0ac7-b294-4054-a440-b05145502ed7 |  | checkpoint | 4. Confirm that Brand of fitted components is in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint-status | d13c1f9f-6f12-45a5-abe1-069a42001d25 |  | checkpoint | 5. Confirm meters location, types and labels are in accordance with approved shop drawings
checkpoint-status | fed66c04-a281-4226-85d2-cc1308b854d6 |  | checkpoint | 6. Confirm the circuit breakers rating is in accordance with discrimination study (provide discrimination study reference in the Comments section)
checkpoint-status | 166bb322-d628-43ec-9bf8-041b5379fdf0 |  | checkpoint | 7. Confirm Trip units and protection relay settings are set in accordance with discrimination study
checkpoint-status | 93ac2995-c7cb-4cc3-a23d-7aeb233d2f0d |  | checkpoint | 8. Confirm correct circuit identification and labelling
checkpoint-status | 33c244aa-637a-4c9c-a3bd-f3f0a27832bc |  | checkpoint | 9. Confirm easy access to controls termination
checkpoint-status | d5c43a96-4cd9-4b7e-b730-d86ffd31a364 |  | checkpoint | 10. Confirm correct location, access and sufficient support for incoming cables
checkpoint-status | f6c1526b-8bd8-47df-910e-4c30ff239067 |  | checkpoint | 11. Confirm correct location, access and sufficient support for outgoing cables
checkpoint-status | efb34131-9aba-4536-afc2-5a1ba1c41ba4 |  | checkpoint | 12. Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in a Comment section
checkpoint-status | c7e0b75b-2b88-486c-8aea-193fa85a6473 |  | checkpoint | 13. Confirm correct phase identification of busbars and cables inside the board
checkpoint-status | b6b186e7-a394-432b-b4c3-1c546efb7c33 |  | checkpoint | 14. Confirm correct size of incoming power cables as per approved cable schedule
checkpoint-status | 25682894-a13e-4c7e-b5d2-1ed03bbe5ca8 |  | checkpoint | 15. Confirm correct size of earthing conductors
checkpoint-status | a63f9ab9-3c0d-4360-a0b2-a829b7bfa713 |  | checkpoint | 16. Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
holdpoint | 529e41ad-b85c-4e77-a03f-21cbf978f9af |  | signoff | Checked By (Heyday):
checkpoint-group | 6ce9011f-c18e-49cb-8b51-cbc6ca09e827 |  | section | Mechanical Checks
checkpoint-status | d3d3fa2f-dbd4-48a9-a297-191ccc66a30a |  | checkpoint | 1. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint-status | cd7f5d77-c10b-4355-bdc9-48df1eeb1747 |  | checkpoint | 2. Repeat racking of air circuit breaker in and out of chassis for 2 times to verify correct functionality of sliding mechanism
checkpoint-status | a02c43de-d823-4815-9245-9b73bf7a7185 |  | checkpoint | 3. Repeat closing and opening of air circuit breakers for 3 times using the front panel operating buttons and charging handle
checkpoint-status | 293c2a5e-d8a8-44c8-9185-207501f06af8 |  | checkpoint | 4. Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint-status | 2afb0689-63c5-4f33-af11-123463e55789 |  | checkpoint | 5. Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint-status | e16b21ae-358f-422a-839c-288ffec3b935 |  | checkpoint | 6. Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | a8b903c9-d1e9-473c-b6c1-f629e9a99da3 |  | checkpoint | 7. Repeat mounting and dismounting of control fuses 1 time
checkpoint-status | 288f2a71-998d-4c75-beb6-0deb9499782e |  | checkpoint | 8. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 1 Breaker and confirm that Source 2 Breaker is mechanically interlocked
checkpoint-status | 8c1eaf4e-3fa3-4791-be7e-e1e6ef8c795c |  | checkpoint | 9. Verify integrity of mechanical interlocking system between ASBs (MCCBs) by closing Source 2 Breaker and confirm that Source 1 Breaker is mechanically interlocked
checkpoint-status | 0d8aaa41-c502-4bba-a980-96764f1df1d1 |  | checkpoint | 10. Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards
holdpoint | c87d02e9-828c-4db6-9932-1072e3b506bc |  | signoff | Checked By (Heyday):
checkpoint-group | 1f491dfa-7337-4563-bc46-34746bb3c48c |  | section | Switch Gear Busbar - Preliminary Checks
checkpoint-status | c5631ed0-e566-4ae8-a020-7b6d4211b82e |  | checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint-status | 4eb807d2-5bca-4540-a6de-0dfec00a7205 |  | checkpoint | 2. Confirm Main Incomers ACBs/MCCBs are Closed
checkpoint-status | b5b90f91-02f1-494a-91fd-5e26a35e8f42 |  | checkpoint | 3. Confirm Bus-coupler is Closed (if exist)
checkpoint-status | ca1b94e1-2e86-4ed2-b45f-3aa6b6454048 |  | checkpoint | 4. Confirm Outgoing Feeders is Closed
checkpoint-status | 2cb37458-00bc-44c1-8295-797f0992e483 |  | checkpoint | 5. Confirm Main Panel Neutral to Earth Link(s) was Removed
checkpoint-status | 8b6c5b34-5b0a-4375-a758-2d56372f3092 |  | checkpoint | 6. Confirm Neutral link on Transient Voltage Surge Suppressor is Opened
checkpoint-status | 297782fc-ca5d-450f-a8d4-348b269dd1bf |  | checkpoint | 7. Confirm All Long Time rating Plugs From ACB's are Removed (if applicable)
checkpoint-group | 0e3b566a-5543-4de4-95da-6e4ccb73147b |  | section | Switch Gear Busbar - Insulation Resistance (1000V)
checkpoint-status | e79c8a67-e5e7-4a7e-a99b-af1abab22fb3 |  | checkpoint | 1. Between L1 Phase and Neutral
button | da47e5a7-0c2b-5bec-a1d1-4cb02286f697 |  | button | >10MΩ | YES,NO
text | db7be619-6a72-502a-a4ad-711cf96f67d4 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 71a0f318-66af-4cc8-b487-4df4c9dc029a |  | checkpoint | 2. Between L2 Phase and Neutral
button | 59432468-bda3-564d-92dc-f4e2bee5c3db |  | button | >10MΩ | YES,NO
text | aba78d31-3e23-55a6-9766-d251b6434bdb |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 673eae18-143e-4e9a-8ae1-0a45252a041c |  | checkpoint | 3. Between L3 Phase and Neutral
button | 0f2b13e8-1769-58bf-8094-2321c28b4b65 |  | button | >10MΩ | YES,NO
text | e07c2df7-beb2-56f8-871c-1eef6ab7088f |  | textbox | Actual Reading if <10MΩ
checkpoint-status | ce6fad98-6bb5-4fb7-9f88-ee00befb1116 |  | checkpoint | 4. Between Neutral and Earth
button | 9fdcde1a-167f-5d39-a0e5-1cb4f6b03e16 |  | button | >10MΩ | YES,NO
text | 0aae33fc-1f86-56cf-bcaa-7c9683e5ced3 |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 596b3c56-7ea2-4ff0-8354-eacef1be0c8f |  | checkpoint | 5. Between L1 Phase and Earth
button | 0e5eadb1-159e-5316-8ed3-ba7569aa068a |  | button | >10MΩ | YES,NO
text | 3af4c9b7-17ee-509a-a86a-e44dbb922e4f |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 75ea76a2-5def-436e-9cf8-f0c5b020c21e |  | checkpoint | 6. Between L2 Phase and Earth
button | ff324f1f-1245-5080-b81b-6adf91084997 |  | button | >10MΩ | YES,NO
text | 5a4fc6a7-81e0-5134-99ea-ee44034c6aea |  | textbox | Actual Reading if <10MΩ
checkpoint-status | f37dec3d-c4f3-4751-a50c-2eb1a3b0b25f |  | checkpoint | 7. Between L3 Phase and Earth
button | 57077747-e456-51dc-95f8-16862262daf8 |  | button | >10MΩ | YES,NO
text | e07fb00e-674c-51f5-870d-14d2e9b4849f |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 5cc50f0b-a7f2-4c30-bb36-d5194b192585 |  | checkpoint | 8. Between L1 Phase and L2 Phase
button | 401458f6-879f-53f3-8d18-10efab680a77 |  | button | >10MΩ | YES,NO
text | 705676ed-5793-5579-9cde-bc18e438a4ab |  | textbox | Actual Reading if <10MΩ
checkpoint-status | 349c44dd-d60c-47bb-8322-bf4b839fe071 |  | checkpoint | 9. Between L1 Phase and L3 Phase
button | 99997557-a1cf-561c-9d88-77517f0475ee |  | button | >10MΩ | YES,NO
text | c6dabda2-3ff5-580c-98b5-aa61ee7a6bbe |  | textbox | Actual Reading if <10MΩ
checkpoint-status | cd0086bf-ad8b-4954-92a3-fa574f86657a |  | checkpoint | 10. Between L2 Phase and L3 Phase
button | a9563b29-b822-560b-894a-19a8b0711f65 |  | button | >10MΩ | YES,NO
text | 357f59da-ed5f-59e7-b57e-96b1702845dd |  | textbox | Actual Reading if <10MΩ
holdpoint | 67310bca-10fe-4882-a17f-e4b101ed6794 |  | signoff | Checked By (Heyday):
checkpoint-group | 617ac783-deeb-4d2c-a6fc-cf19e94add7c |  | section | Circuit Breaker Settings Check
checkpoint-status | 19a2969e-dbcc-41c8-a3f0-9159857e3e9b |  | checkpoint | Circuit Breaker Settings Check
text | 835eb5c1-5f2d-5710-aadb-36394bf4654d |  | textbox | Cubicle ID
text | 91a2b2b3-4cfa-5af5-9722-386cba31835c |  | textbox | Feeder Name
button | 55199d04-18f2-511c-9854-a369d11a7e1c |  | button | Setup as per Discrimiation settings (YES/NO) | YES,NO
holdpoint | caf1447e-4504-4012-b446-7880ab6823df |  | signoff | Checked By (Heyday):
checkpoint-group | 4a519bd4-1653-4c30-85a8-b02ff8273204 |  | section | Current Transformer Checks
checkpoint-status | 2f8f8b1b-7c5b-4126-93f6-d396977b82ad |  | checkpoint | Current Transformer Checks
text | 30d835de-637a-5822-afca-b2eec318553c |  | textbox | CT ID | YES,NO
button | 8f0d1368-938d-5dac-9eea-61880c8a1aa7 |  | button | CT Polarity is Correct | YES,NO
button | bbfc2853-d078-5953-9199-36455cb8f00f |  | button | No crossed phase CT connections | YES,NO
button | 3ba6c161-79a1-5a17-b798-3ff025d6af66 |  | button | No phase sequence CT connection errors | YES,NO
holdpoint | cd34c750-45f8-4686-ad16-80ed235bc4fa |  | signoff | Checked By (Heyday):
checklist-flat | 14710401-9c29-4f39-b42b-46d1e98b2241 |  | checklist | Quality - Precast Pit Install |  |  |  |  | Yes | Quality - Precast Pit Install | dd337cec-0d60-4231-99e6-5240a6b65a55
checkpoint-status | 086a6b84-79c1-498b-8fd5-7a0d0772c2d7 |  | checkpoint | Receipt of Precast pit delivery to site & storage
checkpoint-status | b14f26fa-c956-42c1-b0eb-9aff33b5c57e |  | checkpoint | Pit is built to approved shop drawings (photos attached)
checkpoint-status | 130f2cdf-1e80-4855-95c0-2cd47b51596c |  | checkpoint | correct trenching and alignment & depth
checkpoint-status | 9aded11b-2e7c-4a43-8a19-631766a35474 |  | checkpoint | installed to correct finish level
checkpoint-status | c15d1211-1381-4840-9688-999120feaeba |  | checkpoint | correct back fill installed around pit
holdpoint | 81f8fe16-d331-4056-87d5-6661de7afbed |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | cb7ac338-822e-4947-bc3d-0bac0e0bc5a9 |  | checkpoint | Install correct pit lid
checkpoint-status | 8de1c1e5-d080-4a8f-9755-8cb1dff3eead |  | checkpoint | Photo of pit installed attached.
checklist-flat | 98f3e20c-7459-44a1-acf3-d606bbabcc8c |  | checklist | Heyday On-site Penetration Register |  |  |  |  | Yes | Add Heyday On-site Penetration Register | de50cf9e-922c-47de-9430-19964bd75fb3
checkpoint-no-status | 59c53197-7f17-4c08-bf34-cbdecd6a2185 |  | checkpoint | Fire Stopping System No.
select | 672e6ca0-d27f-5ade-be47-cadc764e3fd6 |  | dropdown | Select System No. | FAS190329 - Conduits within concrete,27912900 - Conduit through FRL
checkpoint-no-status | e82129a9-505d-4e71-b755-ee0177a1c10c |  | checkpoint | Penetration Type
select | cc41d543-a0b2-5338-bccb-350edabe3c42 |  | dropdown | Select Type | Floor,Wall,Ceiling
checkpoint-no-status | 131473b5-4685-4902-9704-23cc5b0c0dad |  | checkpoint | Location
text | faf0f92a-b611-5142-9cc5-1997de933838 |  | textbox | Location:
checkpoint-no-status | 0c4e0a22-6611-460c-a28a-e063b47bc23b |  | checkpoint | FRL
select | ff51926a-ed3a-538f-be24-62136736cc0a |  | dropdown | Select FRL | ~ / 120 / 120
checkpoint-no-status | 9f625aa4-64a1-4726-aa04-9e338bb01d63 |  | checkpoint | Service Description
select | 964bec46-4098-5d46-8d97-65a3ffddbac9 |  | dropdown | Select Description | Conduits within concrete,Concrete through FR compartment
checkpoint-status | 3ce1e2b8-4527-4c0f-8dfd-51303366e887 |  | checkpoint | Photo of Fire Sealing & Label
checklist-flat | a51aecd7-4888-4ee4-90eb-9c6e39fa4e6f |  | checklist | Quality Mains and Sub Mains |  |  |  |  | Yes | Quality Mains and Sub Mains | f67d079f-ce9d-4a67-a5f1-6beeb86a97c3
checkpoint-status | 481c366a-fe5f-4bf9-b08e-3fe618e39573 |  | checkpoint | Receipt of cable containment delivery to site & storage. (ITP Reference Item 1)
checkpoint-status | c1f2e221-dde5-4dad-9b44-c6afb6999b40 |  | checkpoint | Cable storage & handling. (ITP Reference Item 2)
checkpoint-status | a952b6d5-c1b0-4efa-bc98-18fecdf45664 |  | checkpoint | Correct cable size & type. (ITP Reference Item 3)
holdpoint | 2e077f6e-060a-4e49-a276-969004145f0b |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | dd8f2a5e-5bac-4622-9945-985f7020ddc9 |  | checkpoint | Cable pulling tension to not exceed manufacturer's recommendations. (ITP Reference Item 4)
checkpoint-status | 7199c90a-99f7-4c2e-ad30-b8eb856528f1 |  | checkpoint | Cable lubrication if required. (ITP Reference Item 5)
checkpoint-status | cc57e662-d195-4557-b8fc-88991a964bdd |  | checkpoint | Installed to latest drawings – schematics/single line diagram & cable containment drawings. (ITP Reference Item 6)
checkpoint-status | 3700b49e-c745-4dde-9bf2-634c32593cff |  | checkpoint | Correct cable tag installed. (ITP Reference Item 7)
checkpoint-status | 89bedb52-fb10-432d-9c5e-92594ea32e40 |  | checkpoint | Photo evidence captured for cable containment install. (ITP Reference Item 8)
holdpoint | 2007734c-08ee-4ea7-bd50-d84c77daae1f |  | signoff | Signoff Required from Heyday & Multiplex
checklist-flat | ba235e82-281b-4be6-86a7-99b15884cf5b |  | checklist | Quality - Main switchboard Install |  |  |  |  | Yes | Quality - Main switchboard Install | f6caa16d-431c-4ec8-9a0f-72c5b120b20f
checkpoint-status | 4e2cdcce-3851-423a-a541-3b034abfec6f |  | checkpoint | Receipt of switchboard delivery to site
checkpoint-status | af37baef-ea2c-4d09-9044-e0784b0f5248 |  | checkpoint | set out to be confirmed with latest Switchboards Shop drawings
checkpoint-status | 716a9f94-20d4-4671-948f-dc7edc48366e |  | checkpoint | Correct alignment to set out drawings
holdpoint | b2e7b34e-3d88-4de2-b56b-a13cac0dbf56 |  | signoff | Signoff Required from Heyday & Multiplex
checkpoint-status | 4592a97d-1ffe-468f-9314-db6d31bb43bc |  | checkpoint | Correct bracket and safe fixing
checkpoint-status | e1732cfa-bc3c-438f-99ff-b6c05049e4c7 |  | checkpoint | Photos of boards attached